## Main
Input | BOILER CALCULATIONS |  | STEAM MAINS CALCULATIONS |  | VENT CALCULATIONS
Output | Manufacturer Selection | Weil-Mclain | Riser Size(Schd40) | 6 | Main Vol(ft3) | 19.6354
| Boiler Selection | LGB-12 | Riser Count | 1 | Radiator Vol(ft3) | 74.25
| Gross BTU/HR | 1144000 | Main Diameter(Schd40) | 6 | Upfeed Vol(ft3) | 10.8052
| Water@Waterline(gal) | 69.1 | Main Length(ft) | 100 | Total Vol(ft3) | 104.6906
| Operating Pressure(PSIG) | 0.1 | Riser Velocity(fps) | 43.5938 | Total Rad Vent(cfm) | 85.14
| Section Weight(lbs) | 3365 | Main Velocity | 43.5938 | Main Vent | Gorton #2
| Enthalpy(BTU/LB) | 968.7975 | Main end pressure(psig) | 0.073808 | Main Vent Count | 5
| Steam Density(lb/ft3) | 0.037504 |  |  | Main Vent Cap(cfm) | 11
| Steam Rate(Lb/HR) | 1180.8454 |  |  | Time to Vent(min) | 9.5173
| Time to Steam(min) | 8.1352
| Boiler Duty Cycle | 96.38%
RADIATION CALCULATIONS
| Radiators(BTU/HR) | 804418.56
| Radiator Condensate(lbs/hr) | 806.8391
| Upfeed(BTU/HR) | 243540
| Upfeed Condensate(lb/hr) | 829.2975
| Main Radiation(BTU/HR) | 54600
| Main Condensate(lb/hr) | 56.3585
| Total Radiation(BTU/HR) | 1102558.56
| Total condensate(lb/hr) | 1692.4951
| Min Radiator Pressure(psig) | 0.069325
| Init BTU to Heat Pipes(BTU) | 59121.4853
| Init BTU to Heat Radiators(BTU) | 556174.08
| Init Time to heat Metal(min) | 32.2707
| Time to Steady State(min) | 49.9233

## TimeAnalysis
| Main | Supplies | Radiators | Timestep(min) | Time(min) | BTU Output | ft3/hr gen | Main Venting(%) | Supply Venting(%) | Radiator Venting(%) | Total Venting | Main Heating | Supply Heating | Radiator Heating | Total Radiation(BTU/hr) | Condensate Gen(lb/hr) | Energy(BTUs) | Time | % Load
Volf(ft3) | 19.6354 | 10.8052 | 91.08 | 0.02 | 0 | 1144000 | 660 | 0 |  |  | 0 | 0 |  |  |  | 0 |  | 0 | 0%
BTU Heat | 0 | 0 | 0 |  | 0.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0%
Radiation(btu/hr) | 54600 | 243540 | 804418.56 |  | 0.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0%
TTH(min) | 0 | 0 | 0 |  | 0.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0%
TTV(min) | 1.785 | 0.98229 | 8.28 |  | 0.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0%
[5 empty] | 0.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0%
[5 empty] | 0.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0%
[5 empty] | 0.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0%
Start Temp(f) |  |  |  |  | 0.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0%
212 |  |  |  |  | 0.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0%
[5 empty] | 0.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0%
Time to Hourly Output |  |  |  |  | 0.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0%
19.2 |  |  |  |  | 0.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0%
[5 empty] | 0.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0%
[5 empty] | 0.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0%
[5 empty] | 0.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0%
[5 empty] | 0.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0%
[5 empty] | 0.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0%
[5 empty] | 0.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 0%
[5 empty] | 0.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0%
[5 empty] | 0.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0%
[5 empty] | 0.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 0%
[5 empty] | 0.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0%
[5 empty] | 0.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 0%
[5 empty] | 0.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0%
[5 empty] | 0.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0%
[5 empty] | 0.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0%
[5 empty] | 0.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0%
[5 empty] | 0.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 0%
[5 empty] | 0.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0%
[5 empty] | 0.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0%
[5 empty] | 0.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0%
[5 empty] | 0.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0%
[5 empty] | 0.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 0%
[5 empty] | 0.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0%
[5 empty] | 0.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0%
[5 empty] | 0.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0%
[5 empty] | 0.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 0%
[5 empty] | 0.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 0%
[5 empty] | 0.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0%
[5 empty] | 0.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0%
[5 empty] | 0.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 0%
[5 empty] | 0.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0%
[5 empty] | 0.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0%
[5 empty] | 0.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0%
[5 empty] | 0.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0%
[5 empty] | 0.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 0%
[5 empty] | 0.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 0%
[5 empty] | 0.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0%
[5 empty] | 0.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0%
[5 empty] | 1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0%
[5 empty] | 1.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0%
[5 empty] | 1.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0%
[5 empty] | 1.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 0%
[5 empty] | 1.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0%
[5 empty] | 1.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0%
[5 empty] | 1.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0%
[5 empty] | 1.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0%
[5 empty] | 1.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16 | 0%
[5 empty] | 1.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 0%
[5 empty] | 1.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0%
[5 empty] | 1.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0%
[5 empty] | 1.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.24 | 0%
[5 empty] | 1.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0%
[5 empty] | 1.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 0%
[5 empty] | 1.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0%
[5 empty] | 1.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.32 | 0%
[5 empty] | 1.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 0%
[5 empty] | 1.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36 | 0%
[5 empty] | 1.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 0%
[5 empty] | 1.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0%
[5 empty] | 1.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0%
[5 empty] | 1.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 0%
[5 empty] | 1.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.46 | 0%
[5 empty] | 1.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 0%
[5 empty] | 1.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0%
[5 empty] | 1.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.52 | 0%
[5 empty] | 1.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.54 | 0%
[5 empty] | 1.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0%
[5 empty] | 1.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0%
[5 empty] | 1.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0%
[5 empty] | 1.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 0%
[5 empty] | 1.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.64 | 0%
[5 empty] | 1.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0%
[5 empty] | 1.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 0%
[5 empty] | 1.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0%
[5 empty] | 1.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 0%
[5 empty] | 1.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 0%
[5 empty] | 1.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.76 | 0%
[5 empty] | 1.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0%
[5 empty] | 1.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0%
[5 empty] | 1.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 0%
[5 empty] | 1.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 0%
[5 empty] | 1.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.86 | 0%
[5 empty] | 1.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 0%
[5 empty] | 1.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0%
[5 empty] | 1.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 0%
[5 empty] | 1.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 0%
[5 empty] | 1.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 0%
[5 empty] | 1.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 0%
[5 empty] | 2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0%
[5 empty] | 2.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 0%
[5 empty] | 2.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 0%
[5 empty] | 2.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 0%
[5 empty] | 2.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0%
[5 empty] | 2.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0%
[5 empty] | 2.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0%
[5 empty] | 2.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.14 | 0%
[5 empty] | 2.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0%
[5 empty] | 2.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.18 | 0%
[5 empty] | 2.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0%
[5 empty] | 2.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 0%
[5 empty] | 2.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 0%
[5 empty] | 2.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | 0%
[5 empty] | 2.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.28 | 0%
[5 empty] | 2.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0%
[5 empty] | 2.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 0%
[5 empty] | 2.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.34 | 0%
[5 empty] | 2.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.36 | 0%
[5 empty] | 2.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0%
[5 empty] | 2.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0%
[5 empty] | 2.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 0%
[5 empty] | 2.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.44 | 0%
[5 empty] | 2.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.46 | 0%
[5 empty] | 2.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.48 | 0%
[5 empty] | 2.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0%
[5 empty] | 2.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.52 | 0%
[5 empty] | 2.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 0%
[5 empty] | 2.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 0%
[5 empty] | 2.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58 | 0%
[5 empty] | 2.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0%
[5 empty] | 2.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 0%
[5 empty] | 2.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.64 | 0%
[5 empty] | 2.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.66 | 0%
[5 empty] | 2.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.68 | 0%
[5 empty] | 2.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0%
[5 empty] | 2.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 0%
[5 empty] | 2.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 0%
[5 empty] | 2.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.76 | 0%
[5 empty] | 2.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.78 | 0%
[5 empty] | 2.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0%
[5 empty] | 2.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.82 | 0%
[5 empty] | 2.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.84 | 0%
[5 empty] | 2.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 0%
[5 empty] | 2.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 0%
[5 empty] | 2.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0%
[5 empty] | 2.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.92 | 0%
[5 empty] | 2.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 0%
[5 empty] | 2.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.96 | 0%
[5 empty] | 2.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.98 | 0%
[5 empty] | 3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0%
[5 empty] | 3.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 0%
[5 empty] | 3.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.04 | 0%
[5 empty] | 3.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.06 | 0%
[5 empty] | 3.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 0%
[5 empty] | 3.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0%
[5 empty] | 3.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0%
[5 empty] | 3.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 0%
[5 empty] | 3.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 0%
[5 empty] | 3.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.18 | 0%
[5 empty] | 3.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0%
[5 empty] | 3.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 0%
[5 empty] | 3.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.24 | 0%
[5 empty] | 3.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.26 | 0%
[5 empty] | 3.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 0%
[5 empty] | 3.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0%
[5 empty] | 3.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.32 | 0%
[5 empty] | 3.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.34 | 0%
[5 empty] | 3.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.36 | 0%
[5 empty] | 3.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.38 | 0%
[5 empty] | 3.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0%
[5 empty] | 3.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.42 | 0%
[5 empty] | 3.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.44 | 0%
[5 empty] | 3.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.46 | 0%
[5 empty] | 3.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.48 | 0%
[5 empty] | 3.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0%
[5 empty] | 3.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.52 | 0%
[5 empty] | 3.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.54 | 0%
[5 empty] | 3.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56 | 0%
[5 empty] | 3.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 0%
[5 empty] | 3.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0%
[5 empty] | 3.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.62 | 0%
[5 empty] | 3.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.64 | 0%
[5 empty] | 3.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.66 | 0%
[5 empty] | 3.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.68 | 0%
[5 empty] | 3.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0%
[5 empty] | 3.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0%
[5 empty] | 3.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.74 | 0%
[5 empty] | 3.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.76 | 0%
[5 empty] | 3.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.78 | 0%
[5 empty] | 3.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0%
[5 empty] | 3.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.82 | 0%
[5 empty] | 3.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.84 | 0%
[5 empty] | 3.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 0%
[5 empty] | 3.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.88 | 0%
[5 empty] | 3.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0%
[5 empty] | 3.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 0%
[5 empty] | 3.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.94 | 0%
[5 empty] | 3.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.96 | 0%
[5 empty] | 3.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.98 | 0%
[5 empty] | 4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0%
[5 empty] | 4.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.02 | 0%
[5 empty] | 4.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 0%
[5 empty] | 4.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0%
[5 empty] | 4.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.08 | 0%
[5 empty] | 4.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0%
[5 empty] | 4.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.12 | 0%
[5 empty] | 4.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.14 | 0%
[5 empty] | 4.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.16 | 0%
[5 empty] | 4.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.18 | 0%
[5 empty] | 4.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0%
[5 empty] | 4.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.22 | 0%
[5 empty] | 4.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.24 | 0%
[5 empty] | 4.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.26 | 0%
[5 empty] | 4.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.28 | 0%
[5 empty] | 4.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0%
[5 empty] | 4.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.32 | 0%
[5 empty] | 4.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.34 | 0%
[5 empty] | 4.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.36 | 0%
[5 empty] | 4.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.38 | 0%
[5 empty] | 4.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0%
[5 empty] | 4.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.42 | 0%
[5 empty] | 4.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.44 | 0%
[5 empty] | 4.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.46 | 0%
[5 empty] | 4.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.48 | 0%
[5 empty] | 4.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0%
[5 empty] | 4.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.52 | 0%
[5 empty] | 4.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.54 | 0%
[5 empty] | 4.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0%
[5 empty] | 4.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.58 | 0%
[5 empty] | 4.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0%
[5 empty] | 4.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.62 | 0%
[5 empty] | 4.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 0%
[5 empty] | 4.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.66 | 0%
[5 empty] | 4.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.68 | 0%
[5 empty] | 4.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0%
[5 empty] | 4.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.72 | 0%
[5 empty] | 4.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.74 | 0%
[5 empty] | 4.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.76 | 0%
[5 empty] | 4.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.78 | 0%
[5 empty] | 4.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0%
[5 empty] | 4.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.82 | 0%
[5 empty] | 4.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.84 | 0%
[5 empty] | 4.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.86 | 0%
[5 empty] | 4.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.88 | 0%
[5 empty] | 4.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0%
[5 empty] | 4.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.92 | 0%
[5 empty] | 4.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.94 | 0%
[5 empty] | 4.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | 0%
[5 empty] | 4.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.98 | 0%
[5 empty] | 5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0%
[5 empty] | 5.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.02 | 0%
[5 empty] | 5.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.04 | 0%
[5 empty] | 5.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.06 | 0%
[5 empty] | 5.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.08 | 0%
[5 empty] | 5.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0%
[5 empty] | 5.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.12 | 0%
[5 empty] | 5.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.14 | 0%
[5 empty] | 5.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.16 | 0%
[5 empty] | 5.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.18 | 0%
[5 empty] | 5.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0%
[5 empty] | 5.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.22 | 0%
[5 empty] | 5.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.24 | 0%
[5 empty] | 5.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.26 | 0%
[5 empty] | 5.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.28 | 0%
[5 empty] | 5.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0%
[5 empty] | 5.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.32 | 0%
[5 empty] | 5.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.34 | 0%
[5 empty] | 5.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.36 | 0%
[5 empty] | 5.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.38 | 0%
[5 empty] | 5.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0%
[5 empty] | 5.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.42 | 0%
[5 empty] | 5.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.44 | 0%
[5 empty] | 5.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.46 | 0%
[5 empty] | 5.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.48 | 0%
[5 empty] | 5.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0%
[5 empty] | 5.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.52 | 0%
[5 empty] | 5.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.54 | 0%
[5 empty] | 5.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.56 | 0%
[5 empty] | 5.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.58 | 0%
[5 empty] | 5.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0%
[5 empty] | 5.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.62 | 0%
[5 empty] | 5.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.64 | 0%
[5 empty] | 5.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.66 | 0%
[5 empty] | 5.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.68 | 0%
[5 empty] | 5.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 0%
[5 empty] | 5.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.72 | 0%
[5 empty] | 5.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.74 | 0%
[5 empty] | 5.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.76 | 0%
[5 empty] | 5.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.78 | 0%
[5 empty] | 5.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0%
[5 empty] | 5.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.82 | 0%
[5 empty] | 5.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.84 | 0%
[5 empty] | 5.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 0%
[5 empty] | 5.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.88 | 0%
[5 empty] | 5.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0%
[5 empty] | 5.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.92 | 0%
[5 empty] | 5.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 0%
[5 empty] | 5.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.96 | 0%
[5 empty] | 5.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.98 | 0%
[5 empty] | 6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0%
[5 empty] | 6.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.02 | 0%
[5 empty] | 6.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.04 | 0%
[5 empty] | 6.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.06 | 0%
[5 empty] | 6.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.08 | 0%
[5 empty] | 6.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 0%
[5 empty] | 6.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.12 | 0%
[5 empty] | 6.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.14 | 0%
[5 empty] | 6.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.16 | 0%
[5 empty] | 6.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18 | 0%
[5 empty] | 6.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 0%
[5 empty] | 6.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.22 | 0%
[5 empty] | 6.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 0%
[5 empty] | 6.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.26 | 0%
[5 empty] | 6.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.28 | 0%
[5 empty] | 6.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 0%
[5 empty] | 6.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0%
[5 empty] | 6.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0%
[5 empty] | 6.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.36 | 0%
[5 empty] | 6.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.38 | 0%
[5 empty] | 6.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0%
[5 empty] | 6.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.42 | 0%
[5 empty] | 6.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.44 | 0%
[5 empty] | 6.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.46 | 0%
[5 empty] | 6.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.48 | 0%
[5 empty] | 6.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 0%
[5 empty] | 6.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.52 | 0%
[5 empty] | 6.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.54 | 0%
[5 empty] | 6.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.56 | 0%
[5 empty] | 6.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.58 | 0%
[5 empty] | 6.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0%
[5 empty] | 6.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.62 | 0%
[5 empty] | 6.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.64 | 0%
[5 empty] | 6.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.66 | 0%
[5 empty] | 6.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.68 | 0%
[5 empty] | 6.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0%
[5 empty] | 6.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 0%
[5 empty] | 6.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.74 | 0%
[5 empty] | 6.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.76 | 0%
[5 empty] | 6.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.78 | 0%
[5 empty] | 6.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0%
[5 empty] | 6.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.82 | 0%
[5 empty] | 6.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 0%
[5 empty] | 6.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.86 | 0%
[5 empty] | 6.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.88 | 0%
[5 empty] | 6.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0%
[5 empty] | 6.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.92 | 0%
[5 empty] | 6.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.94 | 0%
[5 empty] | 6.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.96 | 0%
[5 empty] | 6.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.98 | 0%
[5 empty] | 7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0%
[5 empty] | 7.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.02 | 0%
[5 empty] | 7.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.04 | 0%
[5 empty] | 7.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.06 | 0%
[5 empty] | 7.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.08 | 0%
[5 empty] | 7.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0%
[5 empty] | 7.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.12 | 0%
[5 empty] | 7.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.14 | 0%
[5 empty] | 7.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.16 | 0%
[5 empty] | 7.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.18 | 0%
[5 empty] | 7.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 0%
[5 empty] | 7.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.22 | 0%
[5 empty] | 7.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0%
[5 empty] | 7.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.26 | 0%
[5 empty] | 7.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.28 | 0%
[5 empty] | 7.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 0%
[5 empty] | 7.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.32 | 0%
[5 empty] | 7.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.34 | 0%
[5 empty] | 7.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.36 | 0%
[5 empty] | 7.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.38 | 0%
[5 empty] | 7.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0%
[5 empty] | 7.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.42 | 0%
[5 empty] | 7.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.44 | 0%
[5 empty] | 7.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.46 | 0%
[5 empty] | 7.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.48 | 0%
[5 empty] | 7.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0%
[5 empty] | 7.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 0%
[5 empty] | 7.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.54 | 0%
[5 empty] | 7.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.56 | 0%
[5 empty] | 7.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.58 | 0%
[5 empty] | 7.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6 | 0%
[5 empty] | 7.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.62 | 0%
[5 empty] | 7.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.64 | 0%
[5 empty] | 7.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.66 | 0%
[5 empty] | 7.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.68 | 0%
[5 empty] | 7.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7 | 0%
[5 empty] | 7.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.72 | 0%
[5 empty] | 7.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.74 | 0%
[5 empty] | 7.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.76 | 0%
[5 empty] | 7.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.78 | 0%
[5 empty] | 7.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 0%
[5 empty] | 7.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.82 | 0%
[5 empty] | 7.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.84 | 0%
[5 empty] | 7.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.86 | 0%
[5 empty] | 7.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.88 | 0%
[5 empty] | 7.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 0%
[5 empty] | 7.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.92 | 0%
[5 empty] | 7.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.94 | 0%
[5 empty] | 7.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.96 | 0%
[5 empty] | 7.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.98 | 0%
[5 empty] | 8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0%
[5 empty] | 8.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.02 | 0%
[5 empty] | 8.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0%
[5 empty] | 8.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.06 | 0%
[5 empty] | 8.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0%
[5 empty] | 8.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 0%
[5 empty] | 8.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12 | 0%
[5 empty] | 8.14 | 1144000 | 660 | 0.2663% | 0% | 0% | 0.00043022 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 0%
[5 empty] | 8.16 | 1144000 | 660 | 1.387% | 0% | 0% | 0.0022406 | 757.1262 | 0 | 0 | 757.1262 | 0.01563 | 0.25238 | 8.16 | 0.06867%
[5 empty] | 8.18 | 1144000 | 660 | 2.507% | 0% | 0% | 0.004051 | 1368.8779 | 0 | 0 | 1368.8779 | 0.04389 | 0.70867 | 8.18 | 0.1242%
[5 empty] | 8.2 | 1144000 | 660 | 3.628% | 0% | 0% | 0.0058614 | 1980.6296 | 0 | 0 | 1980.6296 | 0.084778 | 1.3689 | 8.2 | 0.1796%
[5 empty] | 8.22 | 1144000 | 660 | 4.748% | 0% | 0% | 0.0076718 | 2592.3814 | 0 | 0 | 2592.3814 | 0.1383 | 2.233 | 8.22 | 0.2351%
[5 empty] | 8.24 | 1144000 | 660 | 5.868% | 0% | 0% | 0.0094822 | 3204.1331 | 0 | 0 | 3204.1331 | 0.20444 | 3.301 | 8.24 | 0.2906%
[5 empty] | 8.26 | 1144000 | 660 | 6.989% | 0% | 0% | 0.011293 | 3815.8848 | 0 | 0 | 3815.8848 | 0.28322 | 4.573 | 8.26 | 0.3461%
[5 empty] | 8.28 | 1144000 | 660 | 8.109% | 0% | 0% | 0.013103 | 4427.6365 | 0 | 0 | 4427.6365 | 0.37462 | 6.0489 | 8.28 | 0.4016%
[5 empty] | 8.3 | 1144000 | 660 | 9.23% | 0% | 0% | 0.014913 | 5039.3882 | 0 | 0 | 5039.3882 | 0.47866 | 7.7287 | 8.3 | 0.4571%
[5 empty] | 8.32 | 1144000 | 660 | 10.35% | 0% | 0% | 0.016724 | 5651.14 | 0 | 0 | 5651.14 | 0.59532 | 9.6124 | 8.32 | 0.5125%
[5 empty] | 8.34 | 1144000 | 660 | 11.47% | 0% | 0% | 0.018534 | 6262.8917 | 0 | 0 | 6262.8917 | 0.72461 | 11.7 | 8.34 | 0.568%
[5 empty] | 8.36 | 1144000 | 660 | 12.59% | 0% | 0% | 0.020345 | 6874.6434 | 0 | 0 | 6874.6434 | 0.86653 | 13.9916 | 8.36 | 0.6235%
[5 empty] | 8.38 | 1144000 | 660 | 13.71% | 0% | 0% | 0.022155 | 7486.3951 | 0 | 0 | 7486.3951 | 1.0211 | 16.487 | 8.38 | 0.679%
[5 empty] | 8.4 | 1144000 | 660 | 14.83% | 0% | 0% | 0.023965 | 8098.1469 | 0 | 0 | 8098.1469 | 1.1883 | 19.1864 | 8.4 | 0.7345%
[5 empty] | 8.42 | 1144000 | 660 | 15.95% | 0% | 0% | 0.025776 | 8709.8986 | 0 | 0 | 8709.8986 | 1.3681 | 22.0897 | 8.42 | 0.79%
[5 empty] | 8.44 | 1144000 | 660 | 17.07% | 0% | 0% | 0.027586 | 9321.6503 | 0 | 0 | 9321.6503 | 1.5605 | 25.1969 | 8.44 | 0.8455%
[5 empty] | 8.46 | 1144000 | 660 | 18.19% | 0% | 0% | 0.029396 | 9933.402 | 0 | 0 | 9933.402 | 1.7656 | 28.5081 | 8.46 | 0.9009%
[5 empty] | 8.48 | 1144000 | 660 | 19.31% | 0% | 0% | 0.031207 | 10545.1538 | 0 | 0 | 10545.1538 | 1.9833 | 32.0231 | 8.48 | 0.9564%
[5 empty] | 8.5 | 1144000 | 660 | 20.43% | 0% | 0% | 0.033017 | 11156.9055 | 0 | 0 | 11156.9055 | 2.2136 | 35.7421 | 8.5 | 1.012%
[5 empty] | 8.52 | 1144000 | 660 | 21.55% | 0% | 0% | 0.034828 | 11768.6572 | 0 | 0 | 11768.6572 | 2.4565 | 39.665 | 8.52 | 1.067%
[5 empty] | 8.54 | 1144000 | 660 | 22.67% | 0% | 0% | 0.036638 | 12380.4089 | 0 | 0 | 12380.4089 | 2.7121 | 43.7918 | 8.54 | 1.123%
[5 empty] | 8.56 | 1144000 | 660 | 23.8% | 0% | 0% | 0.038448 | 12992.1607 | 0 | 0 | 12992.1607 | 2.9803 | 48.1225 | 8.56 | 1.178%
[5 empty] | 8.58 | 1144000 | 660 | 24.92% | 0% | 0% | 0.040259 | 13603.9124 | 0 | 0 | 13603.9124 | 3.2612 | 52.6571 | 8.58 | 1.234%
[5 empty] | 8.6 | 1144000 | 660 | 26.04% | 0% | 0% | 0.042069 | 14215.6641 | 0 | 0 | 14215.6641 | 3.5547 | 57.3957 | 8.6 | 1.289%
[5 empty] | 8.62 | 1144000 | 660 | 27.16% | 0% | 0% | 0.04388 | 14827.4158 | 0 | 0 | 14827.4158 | 3.8608 | 62.3382 | 8.62 | 1.345%
[5 empty] | 8.64 | 1144000 | 660 | 28.28% | 0% | 0% | 0.04569 | 15439.1676 | 0 | 0 | 15439.1676 | 4.1795 | 67.4846 | 8.64 | 1.4%
[5 empty] | 8.66 | 1144000 | 660 | 29.4% | 0% | 0% | 0.0475 | 16050.9193 | 0 | 0 | 16050.9193 | 4.5108 | 72.8349 | 8.66 | 1.456%
[5 empty] | 8.68 | 1144000 | 660 | 30.52% | 0% | 0% | 0.049311 | 16662.671 | 0 | 0 | 16662.671 | 4.8548 | 78.3891 | 8.68 | 1.511%
[5 empty] | 8.7 | 1144000 | 660 | 31.64% | 0% | 0% | 0.051121 | 17274.4227 | 0 | 0 | 17274.4227 | 5.2114 | 84.1472 | 8.7 | 1.567%
[5 empty] | 8.72 | 1144000 | 660 | 32.76% | 0% | 0% | 0.052932 | 17886.1745 | 0 | 0 | 17886.1745 | 5.5807 | 90.1093 | 8.72 | 1.622%
[5 empty] | 8.74 | 1144000 | 660 | 33.88% | 0% | 0% | 0.054742 | 18497.9262 | 0 | 0 | 18497.9262 | 5.9626 | 96.2753 | 8.74 | 1.678%
[5 empty] | 8.76 | 1144000 | 660 | 35% | 0% | 0% | 0.056552 | 19109.6779 | 0 | 0 | 19109.6779 | 6.3571 | 102.6452 | 8.76 | 1.733%
[5 empty] | 8.78 | 1144000 | 660 | 36.12% | 0% | 0% | 0.058363 | 19721.4296 | 0 | 0 | 19721.4296 | 6.7642 | 109.219 | 8.78 | 1.789%
[5 empty] | 8.8 | 1144000 | 660 | 37.24% | 0% | 0% | 0.060173 | 20333.1814 | 0 | 0 | 20333.1814 | 7.184 | 115.9967 | 8.8 | 1.844%
[5 empty] | 8.82 | 1144000 | 660 | 38.36% | 0% | 0% | 0.061984 | 20944.9331 | 0 | 0 | 20944.9331 | 7.6163 | 122.9783 | 8.82 | 1.9%
[5 empty] | 8.84 | 1144000 | 660 | 39.48% | 0% | 0% | 0.063794 | 21556.6848 | 0 | 0 | 21556.6848 | 8.0614 | 130.1639 | 8.84 | 1.955%
[5 empty] | 8.86 | 1144000 | 660 | 40.6% | 0% | 0% | 0.065604 | 22168.4365 | 0 | 0 | 22168.4365 | 8.519 | 137.5534 | 8.86 | 2.011%
[5 empty] | 8.88 | 1144000 | 660 | 41.72% | 0% | 0% | 0.067415 | 22780.1882 | 0 | 0 | 22780.1882 | 8.9893 | 145.1468 | 8.88 | 2.066%
[5 empty] | 8.9 | 1144000 | 660 | 42.84% | 0% | 0% | 0.069225 | 23391.94 | 0 | 0 | 23391.94 | 9.4722 | 152.9441 | 8.9 | 2.122%
[5 empty] | 8.92 | 1144000 | 660 | 43.96% | 0% | 0% | 0.071036 | 24003.6917 | 0 | 0 | 24003.6917 | 9.9677 | 160.9453 | 8.92 | 2.177%
[5 empty] | 8.94 | 1144000 | 660 | 45.08% | 0% | 0% | 0.072846 | 24615.4434 | 0 | 0 | 24615.4434 | 10.4759 | 169.1505 | 8.94 | 2.233%
[5 empty] | 8.96 | 1144000 | 660 | 46.2% | 0% | 0% | 0.074656 | 25227.1951 | 0 | 0 | 25227.1951 | 10.9967 | 177.5595 | 8.96 | 2.288%
[5 empty] | 8.98 | 1144000 | 660 | 47.32% | 0% | 0% | 0.076467 | 25838.9469 | 0 | 0 | 25838.9469 | 11.5301 | 186.1725 | 8.98 | 2.344%
[5 empty] | 9 | 1144000 | 660 | 48.44% | 0% | 0% | 0.078277 | 26450.6986 | 0 | 0 | 26450.6986 | 12.0762 | 194.9894 | 9 | 2.399%
[5 empty] | 9.02 | 1144000 | 660 | 49.56% | 0% | 0% | 0.080087 | 27062.4503 | 0 | 0 | 27062.4503 | 12.6349 | 204.0102 | 9.02 | 2.455%
[5 empty] | 9.04 | 1144000 | 660 | 50.69% | 0% | 0% | 0.081898 | 27674.202 | 0 | 0 | 27674.202 | 13.2062 | 213.235 | 9.04 | 2.51%
[5 empty] | 9.06 | 1144000 | 660 | 51.81% | 0% | 0% | 0.083708 | 28285.9538 | 0 | 0 | 28285.9538 | 13.7901 | 222.6636 | 9.06 | 2.565%
[5 empty] | 9.08 | 1144000 | 660 | 52.93% | 0% | 0% | 0.085519 | 28897.7055 | 0 | 0 | 28897.7055 | 14.3867 | 232.2962 | 9.08 | 2.621%
[5 empty] | 9.1 | 1144000 | 660 | 54.05% | 0% | 0% | 0.087329 | 29509.4572 | 0 | 0 | 29509.4572 | 14.9959 | 242.1327 | 9.1 | 2.676%
[5 empty] | 9.12 | 1144000 | 660 | 55.17% | 0% | 0% | 0.089139 | 30121.2089 | 0 | 0 | 30121.2089 | 15.6177 | 252.1731 | 9.12 | 2.732%
[5 empty] | 9.14 | 1144000 | 660 | 56.29% | 0% | 0% | 0.09095 | 30732.9607 | 0 | 0 | 30732.9607 | 16.2522 | 262.4174 | 9.14 | 2.787%
[5 empty] | 9.16 | 1144000 | 660 | 57.41% | 0% | 0% | 0.09276 | 31344.7124 | 0 | 0 | 31344.7124 | 16.8992 | 272.8656 | 9.16 | 2.843%
[5 empty] | 9.18 | 1144000 | 660 | 58.53% | 0% | 0% | 0.094571 | 31956.4641 | 0 | 0 | 31956.4641 | 17.559 | 283.5178 | 9.18 | 2.898%
[5 empty] | 9.2 | 1144000 | 660 | 59.65% | 0% | 0% | 0.096381 | 32568.2158 | 0 | 0 | 32568.2158 | 18.2313 | 294.3739 | 9.2 | 2.954%
[5 empty] | 9.22 | 1144000 | 660 | 60.77% | 0% | 0% | 0.098191 | 33179.9676 | 0 | 0 | 33179.9676 | 18.9163 | 305.4338 | 9.22 | 3.009%
[5 empty] | 9.24 | 1144000 | 660 | 61.89% | 0% | 0% | 0.1 | 33791.7193 | 0 | 0 | 33791.7193 | 19.6139 | 316.6978 | 9.24 | 3.065%
[5 empty] | 9.26 | 1144000 | 660 | 63.01% | 0% | 0% | 0.10181 | 34403.471 | 0 | 0 | 34403.471 | 20.3241 | 328.1656 | 9.26 | 3.12%
[5 empty] | 9.28 | 1144000 | 660 | 64.13% | 0% | 0% | 0.10362 | 35015.2227 | 0 | 0 | 35015.2227 | 21.047 | 339.8373 | 9.28 | 3.176%
[5 empty] | 9.3 | 1144000 | 660 | 65.25% | 0% | 0% | 0.10543 | 35626.9745 | 0 | 0 | 35626.9745 | 21.7824 | 351.713 | 9.3 | 3.231%
[5 empty] | 9.32 | 1144000 | 660 | 66.37% | 0% | 0% | 0.10724 | 36238.7262 | 0 | 0 | 36238.7262 | 22.5306 | 363.7925 | 9.32 | 3.287%
[5 empty] | 9.34 | 1144000 | 660 | 67.49% | 0% | 0% | 0.10905 | 36850.4779 | 0 | 0 | 36850.4779 | 23.2913 | 376.076 | 9.34 | 3.342%
[5 empty] | 9.36 | 1144000 | 660 | 68.61% | 0% | 0% | 0.11086 | 37462.2296 | 0 | 0 | 37462.2296 | 24.0647 | 388.5635 | 9.36 | 3.398%
[5 empty] | 9.38 | 1144000 | 660 | 69.73% | 0% | 0% | 0.11267 | 38073.9814 | 0 | 0 | 38073.9814 | 24.8507 | 401.2548 | 9.38 | 3.453%
[5 empty] | 9.4 | 1144000 | 660 | 70.85% | 0% | 0% | 0.11448 | 38685.7331 | 0 | 0 | 38685.7331 | 25.6493 | 414.15 | 9.4 | 3.509%
[5 empty] | 9.42 | 1144000 | 660 | 71.97% | 0% | 0% | 0.1163 | 39297.4848 | 0 | 0 | 39297.4848 | 26.4606 | 427.2492 | 9.42 | 3.564%
[5 empty] | 9.44 | 1144000 | 660 | 73.09% | 0% | 0% | 0.11811 | 39909.2365 | 0 | 0 | 39909.2365 | 27.2845 | 440.5523 | 9.44 | 3.62%
[5 empty] | 9.46 | 1144000 | 660 | 74.21% | 0% | 0% | 0.11992 | 40520.9882 | 0 | 0 | 40520.9882 | 28.121 | 454.0593 | 9.46 | 3.675%
[5 empty] | 9.48 | 1144000 | 660 | 75.33% | 0% | 0% | 0.12173 | 41132.74 | 0 | 0 | 41132.74 | 28.9702 | 467.7702 | 9.48 | 3.731%
[5 empty] | 9.5 | 1144000 | 660 | 76.46% | 0% | 0% | 0.12354 | 41744.4917 | 0 | 0 | 41744.4917 | 29.8319 | 481.685 | 9.5 | 3.786%
[5 empty] | 9.52 | 1144000 | 660 | 77.58% | 0% | 0% | 0.12535 | 42356.2434 | 0 | 0 | 42356.2434 | 30.7063 | 495.8038 | 9.52 | 3.842%
[5 empty] | 9.54 | 1144000 | 660 | 78.7% | 0% | 0% | 0.12716 | 42967.9951 | 0 | 0 | 42967.9951 | 31.5934 | 510.1264 | 9.54 | 3.897%
[5 empty] | 9.56 | 1144000 | 660 | 79.82% | 0% | 0% | 0.12897 | 43579.7469 | 0 | 0 | 43579.7469 | 32.493 | 524.653 | 9.56 | 3.953%
[5 empty] | 9.58 | 1144000 | 660 | 80.94% | 0% | 0% | 0.13078 | 44191.4986 | 0 | 0 | 44191.4986 | 33.4053 | 539.3835 | 9.58 | 4.008%
[5 empty] | 9.6 | 1144000 | 660 | 82.06% | 0% | 0% | 0.13259 | 44803.2503 | 0 | 0 | 44803.2503 | 34.3303 | 554.3179 | 9.6 | 4.064%
[5 empty] | 9.62 | 1144000 | 660 | 83.18% | 0% | 0% | 0.1344 | 45415.002 | 0 | 0 | 45415.002 | 35.2678 | 569.4562 | 9.62 | 4.119%
[5 empty] | 9.64 | 1144000 | 660 | 84.3% | 0% | 0% | 0.13621 | 46026.7538 | 0 | 0 | 46026.7538 | 36.218 | 584.7985 | 9.64 | 4.175%
[5 empty] | 9.66 | 1144000 | 660 | 85.42% | 0% | 0% | 0.13802 | 46638.5055 | 0 | 0 | 46638.5055 | 37.1808 | 600.3447 | 9.66 | 4.23%
[5 empty] | 9.68 | 1144000 | 660 | 86.54% | 0% | 0% | 0.13983 | 47250.2572 | 0 | 0 | 47250.2572 | 38.1563 | 616.0948 | 9.68 | 4.286%
[5 empty] | 9.7 | 1144000 | 660 | 87.66% | 0% | 0% | 0.14164 | 47862.0089 | 0 | 0 | 47862.0089 | 39.1443 | 632.0488 | 9.7 | 4.341%
[5 empty] | 9.72 | 1144000 | 660 | 88.78% | 0% | 0% | 0.14345 | 48473.7607 | 0 | 0 | 48473.7607 | 40.145 | 648.2067 | 9.72 | 4.396%
[5 empty] | 9.74 | 1144000 | 660 | 89.9% | 0% | 0% | 0.14526 | 49085.5124 | 0 | 0 | 49085.5124 | 41.1584 | 664.5685 | 9.74 | 4.452%
[5 empty] | 9.76 | 1144000 | 660 | 91.02% | 0% | 0% | 0.14707 | 49697.2641 | 0 | 0 | 49697.2641 | 42.1843 | 681.1343 | 9.76 | 4.507%
[5 empty] | 9.78 | 1144000 | 660 | 92.14% | 0% | 0% | 0.14888 | 50309.0158 | 0 | 0 | 50309.0158 | 43.2229 | 697.9039 | 9.78 | 4.563%
[5 empty] | 9.8 | 1144000 | 660 | 93.26% | 0% | 0% | 0.15069 | 50920.7676 | 0 | 0 | 50920.7676 | 44.2741 | 714.8775 | 9.8 | 4.618%
[5 empty] | 9.82 | 1144000 | 660 | 94.38% | 0% | 0% | 0.1525 | 51532.5193 | 0 | 0 | 51532.5193 | 45.338 | 732.055 | 9.82 | 4.674%
[5 empty] | 9.84 | 1144000 | 660 | 95.5% | 0% | 0% | 0.15431 | 52144.271 | 0 | 0 | 52144.271 | 46.4144 | 749.4365 | 9.84 | 4.729%
[5 empty] | 9.86 | 1144000 | 660 | 96.62% | 0% | 0% | 0.15612 | 52756.0227 | 0 | 0 | 52756.0227 | 47.5035 | 767.0218 | 9.86 | 4.785%
[5 empty] | 9.88 | 1144000 | 660 | 97.74% | 0% | 0% | 0.15793 | 53367.7745 | 0 | 0 | 53367.7745 | 48.6053 | 784.8111 | 9.88 | 4.84%
[5 empty] | 9.9 | 1144000 | 660 | 98.86% | 0% | 0% | 0.15974 | 53979.5262 | 0 | 0 | 53979.5262 | 49.7196 | 802.8042 | 9.9 | 4.896%
[5 empty] | 9.92 | 1144000 | 660 | 99.98% | 0% | 0% | 0.16156 | 54591.2779 | 0 | 0 | 54591.2779 | 50.8466 | 821.0013 | 9.92 | 4.951%
[5 empty] | 9.94 | 1144000 | 660 | 100% | 2.007% | 0% | 0.16337 | 54600 | 4887.911 | 0 | 59487.911 | 52.0747 | 840.8306 | 9.94 | 5.395%
[5 empty] | 9.96 | 1144000 | 660 | 100% | 4.043% | 0% | 0.16518 | 54600 | 9846.5197 | 0 | 64446.5197 | 53.4051 | 862.3128 | 9.96 | 5.845%
[5 empty] | 9.98 | 1144000 | 660 | 100% | 6.079% | 0% | 0.16699 | 54600 | 14805.1283 | 0 | 69405.1283 | 54.838 | 885.4478 | 9.98 | 6.295%
[5 empty] | 10 | 1144000 | 660 | 100% | 8.115% | 0% | 0.1688 | 54600 | 19763.737 | 0 | 74363.737 | 56.3731 | 910.2358 | 10 | 6.745%
[5 empty] | 10.02 | 1144000 | 660 | 100% | 10.15% | 0% | 0.17061 | 54600 | 24722.3457 | 0 | 79322.3457 | 58.0107 | 936.6765 | 10.02 | 7.194%
[5 empty] | 10.04 | 1144000 | 660 | 100% | 12.19% | 0% | 0.17242 | 54600 | 29680.9544 | 0 | 84280.9544 | 59.7506 | 964.7702 | 10.04 | 7.644%
[5 empty] | 10.06 | 1144000 | 660 | 100% | 14.22% | 0% | 0.17423 | 54600 | 34639.5631 | 0 | 89239.5631 | 61.5929 | 994.5167 | 10.06 | 8.094%
[5 empty] | 10.08 | 1144000 | 660 | 100% | 16.26% | 0% | 0.17604 | 54600 | 39598.1718 | 0 | 94198.1718 | 63.5375 | 1025.9161 | 10.08 | 8.544%
[5 empty] | 10.1 | 1144000 | 660 | 100% | 18.3% | 0% | 0.17785 | 54600 | 44556.7805 | 0 | 99156.7805 | 65.5845 | 1058.9684 | 10.1 | 8.993%
[5 empty] | 10.12 | 1144000 | 660 | 100% | 20.33% | 0% | 0.17966 | 54600 | 49515.3892 | 0 | 104115.3892 | 67.7339 | 1093.6735 | 10.12 | 9.443%
[5 empty] | 10.14 | 1144000 | 660 | 100% | 22.37% | 0% | 0.18147 | 54600 | 54473.9979 | 0 | 109073.9979 | 69.9856 | 1130.0315 | 10.14 | 9.893%
[5 empty] | 10.16 | 1144000 | 660 | 100% | 24.4% | 0% | 0.18328 | 54600 | 59432.6066 | 0 | 114032.6066 | 72.3397 | 1168.0424 | 10.16 | 10.34%
[5 empty] | 10.18 | 1144000 | 660 | 100% | 26.44% | 0% | 0.18509 | 54600 | 64391.2153 | 0 | 118991.2153 | 74.7962 | 1207.7061 | 10.18 | 10.79%
[5 empty] | 10.2 | 1144000 | 660 | 100% | 28.48% | 0% | 0.1869 | 54600 | 69349.824 | 0 | 123949.824 | 77.355 | 1249.0227 | 10.2 | 11.24%
[5 empty] | 10.22 | 1144000 | 660 | 100% | 30.51% | 0% | 0.18871 | 54600 | 74308.4327 | 0 | 128908.4327 | 80.0162 | 1291.9922 | 10.22 | 11.69%
[5 empty] | 10.24 | 1144000 | 660 | 100% | 32.55% | 0% | 0.19052 | 54600 | 79267.0414 | 0 | 133867.0414 | 82.7798 | 1336.6145 | 10.24 | 12.14%
[5 empty] | 10.26 | 1144000 | 660 | 100% | 34.58% | 0% | 0.19233 | 54600 | 84225.6501 | 0 | 138825.6501 | 85.6458 | 1382.8898 | 10.26 | 12.59%
[5 empty] | 10.28 | 1144000 | 660 | 100% | 36.62% | 0% | 0.19414 | 54600 | 89184.2588 | 0 | 143784.2588 | 88.6141 | 1430.8178 | 10.28 | 13.04%
[5 empty] | 10.3 | 1144000 | 660 | 100% | 38.66% | 0% | 0.19595 | 54600 | 94142.8675 | 0 | 148742.8675 | 91.6847 | 1480.3988 | 10.3 | 13.49%
[5 empty] | 10.32 | 1144000 | 660 | 100% | 40.69% | 0% | 0.19776 | 54600 | 99101.4762 | 0 | 153701.4762 | 94.8578 | 1531.6326 | 10.32 | 13.94%
[5 empty] | 10.34 | 1144000 | 660 | 100% | 42.73% | 0% | 0.19957 | 54600 | 104060.0849 | 0 | 158660.0849 | 98.1332 | 1584.5193 | 10.34 | 14.39%
[5 empty] | 10.36 | 1144000 | 660 | 100% | 44.76% | 0% | 0.20138 | 54600 | 109018.6936 | 0 | 163618.6936 | 101.5109 | 1639.0589 | 10.36 | 14.84%
[5 empty] | 10.38 | 1144000 | 660 | 100% | 46.8% | 0% | 0.20319 | 54600 | 113977.3023 | 0 | 168577.3023 | 104.9911 | 1695.2513 | 10.38 | 15.29%
[5 empty] | 10.4 | 1144000 | 660 | 100% | 48.84% | 0% | 0.205 | 54600 | 118935.911 | 0 | 173535.911 | 108.5736 | 1753.0966 | 10.4 | 15.74%
[5 empty] | 10.42 | 1144000 | 660 | 100% | 50.87% | 0% | 0.20681 | 54600 | 123894.5197 | 0 | 178494.5197 | 112.2584 | 1812.5948 | 10.42 | 16.19%
[5 empty] | 10.44 | 1144000 | 660 | 100% | 52.91% | 0% | 0.20863 | 54600 | 128853.1283 | 0 | 183453.1283 | 116.0457 | 1873.7458 | 10.44 | 16.64%
[5 empty] | 10.46 | 1144000 | 660 | 100% | 54.94% | 0% | 0.21044 | 54600 | 133811.737 | 0 | 188411.737 | 119.9353 | 1936.5497 | 10.46 | 17.09%
[5 empty] | 10.48 | 1144000 | 660 | 100% | 56.98% | 0% | 0.21225 | 54600 | 138770.3457 | 0 | 193370.3457 | 123.9272 | 2001.0065 | 10.48 | 17.54%
[5 empty] | 10.5 | 1144000 | 660 | 100% | 59.02% | 0% | 0.21406 | 54600 | 143728.9544 | 0 | 198328.9544 | 128.0216 | 2067.1162 | 10.5 | 17.99%
[5 empty] | 10.52 | 1144000 | 660 | 100% | 61.05% | 0% | 0.21587 | 54600 | 148687.5631 | 0 | 203287.5631 | 132.2183 | 2134.8787 | 10.52 | 18.44%
[5 empty] | 10.54 | 1144000 | 660 | 100% | 63.09% | 0% | 0.21768 | 54600 | 153646.1718 | 0 | 208246.1718 | 136.5173 | 2204.2941 | 10.54 | 18.89%
[5 empty] | 10.56 | 1144000 | 660 | 100% | 65.12% | 0% | 0.21949 | 54600 | 158604.7805 | 0 | 213204.7805 | 140.9188 | 2275.3623 | 10.56 | 19.34%
[5 empty] | 10.58 | 1144000 | 660 | 100% | 67.16% | 0% | 0.2213 | 54600 | 163563.3892 | 0 | 218163.3892 | 145.4226 | 2348.0835 | 10.58 | 19.79%
[5 empty] | 10.6 | 1144000 | 660 | 100% | 69.2% | 0% | 0.22311 | 54600 | 168521.9979 | 0 | 223121.9979 | 150.0287 | 2422.4575 | 10.6 | 20.24%
[5 empty] | 10.62 | 1144000 | 660 | 100% | 71.23% | 0% | 0.22492 | 54600 | 173480.6066 | 0 | 228080.6066 | 154.7373 | 2498.4843 | 10.62 | 20.69%
[5 empty] | 10.64 | 1144000 | 660 | 100% | 73.27% | 0% | 0.22673 | 54600 | 178439.2153 | 0 | 233039.2153 | 159.5482 | 2576.1641 | 10.64 | 21.14%
[5 empty] | 10.66 | 1144000 | 660 | 100% | 75.31% | 0% | 0.22854 | 54600 | 183397.824 | 0 | 237997.824 | 164.4614 | 2655.4967 | 10.66 | 21.59%
[5 empty] | 10.68 | 1144000 | 660 | 100% | 77.34% | 0% | 0.23035 | 54600 | 188356.4327 | 0 | 242956.4327 | 169.477 | 2736.4822 | 10.68 | 22.04%
[5 empty] | 10.7 | 1144000 | 660 | 100% | 79.38% | 0% | 0.23216 | 54600 | 193315.0414 | 0 | 247915.0414 | 174.595 | 2819.1205 | 10.7 | 22.49%
[5 empty] | 10.72 | 1144000 | 660 | 100% | 81.41% | 0% | 0.23397 | 54600 | 198273.6501 | 0 | 252873.6501 | 179.8154 | 2903.4117 | 10.72 | 22.94%
[5 empty] | 10.74 | 1144000 | 660 | 100% | 83.45% | 0% | 0.23578 | 54600 | 203232.2588 | 0 | 257832.2588 | 185.1381 | 2989.3558 | 10.74 | 23.38%
[5 empty] | 10.76 | 1144000 | 660 | 100% | 85.49% | 0% | 0.23759 | 54600 | 208190.8675 | 0 | 262790.8675 | 190.5632 | 3076.9528 | 10.76 | 23.83%
[5 empty] | 10.78 | 1144000 | 660 | 100% | 87.52% | 0% | 0.2394 | 54600 | 213149.4762 | 0 | 267749.4762 | 196.0907 | 3166.2026 | 10.78 | 24.28%
[5 empty] | 10.8 | 1144000 | 660 | 100% | 89.56% | 0% | 0.24121 | 54600 | 218108.0849 | 0 | 272708.0849 | 201.7205 | 3257.1053 | 10.8 | 24.73%
[5 empty] | 10.82 | 1144000 | 660 | 100% | 91.59% | 0% | 0.24302 | 54600 | 223066.6936 | 0 | 277666.6936 | 207.4527 | 3349.6609 | 10.82 | 25.18%
[5 empty] | 10.84 | 1144000 | 660 | 100% | 93.63% | 0% | 0.24483 | 54600 | 228025.3023 | 0 | 282625.3023 | 213.2873 | 3443.8693 | 10.84 | 25.63%
[5 empty] | 10.86 | 1144000 | 660 | 100% | 95.67% | 0% | 0.24664 | 54600 | 232983.911 | 0 | 287583.911 | 219.2242 | 3539.7306 | 10.86 | 26.08%
[5 empty] | 10.88 | 1144000 | 660 | 100% | 97.7% | 0% | 0.24845 | 54600 | 237942.5197 | 0 | 292542.5197 | 225.2635 | 3637.2448 | 10.88 | 26.53%
[5 empty] | 10.9 | 1144000 | 660 | 100% | 99.74% | 0% | 0.25026 | 54600 | 242901.1283 | 0 | 297501.1283 | 231.4051 | 3736.4118 | 10.9 | 26.98%
[5 empty] | 10.92 | 1144000 | 660 | 100% | 101.8% | 0.2104% | 0.25365 | 54600 | 247859.737 | 1692.697 | 304152.434 | 237.6841 | 3837.796 | 10.92 | 27.59%
[5 empty] | 10.94 | 1144000 | 660 | 100% | 100% | 0.452% | 0.25389 | 54600 | 243540 | 3635.737 | 301775.737 | 243.914 | 3938.3879 | 10.94 | 27.37%
[5 empty] | 10.96 | 1144000 | 660 | 100% | 100% | 0.6935% | 0.2557 | 54600 | 243540 | 5578.777 | 303718.777 | 250.184 | 4039.6275 | 10.96 | 27.55%
[5 empty] | 10.98 | 1144000 | 660 | 100% | 100% | 0.9351% | 0.25751 | 54600 | 243540 | 7521.817 | 305661.817 | 256.4942 | 4141.5147 | 10.98 | 27.72%
[5 empty] | 11 | 1144000 | 660 | 100% | 100% | 1.177% | 0.25932 | 54600 | 243540 | 9464.857 | 307604.857 | 262.8444 | 4244.0497 | 11 | 27.9%
[5 empty] | 11.02 | 1144000 | 660 | 100% | 100% | 1.418% | 0.26113 | 54600 | 243540 | 11407.897 | 309547.897 | 269.2347 | 4347.2323 | 11.02 | 28.08%
[5 empty] | 11.04 | 1144000 | 660 | 100% | 100% | 1.66% | 0.26294 | 54600 | 243540 | 13350.937 | 311490.937 | 275.6652 | 4451.0626 | 11.04 | 28.25%
[5 empty] | 11.06 | 1144000 | 660 | 100% | 100% | 1.901% | 0.26475 | 54600 | 243540 | 15293.977 | 313433.977 | 282.1358 | 4555.5406 | 11.06 | 28.43%
[5 empty] | 11.08 | 1144000 | 660 | 100% | 100% | 2.143% | 0.26656 | 54600 | 243540 | 17237.017 | 315377.017 | 288.6465 | 4660.6663 | 11.08 | 28.6%
[5 empty] | 11.1 | 1144000 | 660 | 100% | 100% | 2.384% | 0.26837 | 54600 | 243540 | 19180.057 | 317320.057 | 295.1973 | 4766.4397 | 11.1 | 28.78%
[5 empty] | 11.12 | 1144000 | 660 | 100% | 100% | 2.626% | 0.27018 | 54600 | 243540 | 21123.097 | 319263.097 | 301.7882 | 4872.8607 | 11.12 | 28.96%
[5 empty] | 11.14 | 1144000 | 660 | 100% | 100% | 2.867% | 0.27199 | 54600 | 243540 | 23066.137 | 321206.137 | 308.4192 | 4979.9294 | 11.14 | 29.13%
[5 empty] | 11.16 | 1144000 | 660 | 100% | 100% | 3.109% | 0.2738 | 54600 | 243540 | 25009.177 | 323149.177 | 315.0904 | 5087.6458 | 11.16 | 29.31%
[5 empty] | 11.18 | 1144000 | 660 | 100% | 100% | 3.351% | 0.27561 | 54600 | 243540 | 26952.217 | 325092.217 | 321.8016 | 5196.0099 | 11.18 | 29.49%
[5 empty] | 11.2 | 1144000 | 660 | 100% | 100% | 3.592% | 0.27742 | 54600 | 243540 | 28895.257 | 327035.257 | 328.553 | 5305.0216 | 11.2 | 29.66%
[5 empty] | 11.22 | 1144000 | 660 | 100% | 100% | 3.834% | 0.27923 | 54600 | 243540 | 30838.297 | 328978.297 | 335.3445 | 5414.681 | 11.22 | 29.84%
[5 empty] | 11.24 | 1144000 | 660 | 100% | 100% | 4.075% | 0.28104 | 54600 | 243540 | 32781.337 | 330921.337 | 342.1761 | 5524.9882 | 11.24 | 30.01%
[5 empty] | 11.26 | 1144000 | 660 | 100% | 100% | 4.317% | 0.28285 | 54600 | 243540 | 34724.377 | 332864.377 | 349.0478 | 5635.9429 | 11.26 | 30.19%
[5 empty] | 11.28 | 1144000 | 660 | 100% | 100% | 4.558% | 0.28466 | 54600 | 243540 | 36667.417 | 334807.417 | 355.9596 | 5747.5454 | 11.28 | 30.37%
[5 empty] | 11.3 | 1144000 | 660 | 100% | 100% | 4.8% | 0.28647 | 54600 | 243540 | 38610.457 | 336750.457 | 362.9115 | 5859.7956 | 11.3 | 30.54%
[5 empty] | 11.32 | 1144000 | 660 | 100% | 100% | 5.041% | 0.28828 | 54600 | 243540 | 40553.497 | 338693.497 | 369.9035 | 5972.6934 | 11.32 | 30.72%
[5 empty] | 11.34 | 1144000 | 660 | 100% | 100% | 5.283% | 0.29009 | 54600 | 243540 | 42496.537 | 340636.537 | 376.9357 | 6086.2389 | 11.34 | 30.9%
[5 empty] | 11.36 | 1144000 | 660 | 100% | 100% | 5.524% | 0.2919 | 54600 | 243540 | 44439.577 | 342579.577 | 384.008 | 6200.4321 | 11.36 | 31.07%
[5 empty] | 11.38 | 1144000 | 660 | 100% | 100% | 5.766% | 0.29371 | 54600 | 243540 | 46382.617 | 344522.617 | 391.1203 | 6315.273 | 11.38 | 31.25%
[5 empty] | 11.4 | 1144000 | 660 | 100% | 100% | 6.008% | 0.29552 | 54600 | 243540 | 48325.657 | 346465.657 | 398.2728 | 6430.7615 | 11.4 | 31.42%
[5 empty] | 11.42 | 1144000 | 660 | 100% | 100% | 6.249% | 0.29733 | 54600 | 243540 | 50268.697 | 348408.697 | 405.4654 | 6546.8978 | 11.42 | 31.6%
[5 empty] | 11.44 | 1144000 | 660 | 100% | 100% | 6.491% | 0.29914 | 54600 | 243540 | 52211.737 | 350351.737 | 412.6981 | 6663.6817 | 11.44 | 31.78%
[5 empty] | 11.46 | 1144000 | 660 | 100% | 100% | 6.732% | 0.30096 | 54600 | 243540 | 54154.777 | 352294.777 | 419.971 | 6781.1133 | 11.46 | 31.95%
[5 empty] | 11.48 | 1144000 | 660 | 100% | 100% | 6.974% | 0.30277 | 54600 | 243540 | 56097.817 | 354237.817 | 427.2839 | 6899.1925 | 11.48 | 32.13%
[5 empty] | 11.5 | 1144000 | 660 | 100% | 100% | 7.215% | 0.30458 | 54600 | 243540 | 58040.857 | 356180.857 | 434.6369 | 7017.9195 | 11.5 | 32.3%
[5 empty] | 11.52 | 1144000 | 660 | 100% | 100% | 7.457% | 0.30639 | 54600 | 243540 | 59983.897 | 358123.897 | 442.0301 | 7137.2941 | 11.52 | 32.48%
[5 empty] | 11.54 | 1144000 | 660 | 100% | 100% | 7.698% | 0.3082 | 54600 | 243540 | 61926.937 | 360066.937 | 449.4634 | 7257.3164 | 11.54 | 32.66%
[5 empty] | 11.56 | 1144000 | 660 | 100% | 100% | 7.94% | 0.31001 | 54600 | 243540 | 63869.977 | 362009.977 | 456.9368 | 7377.9864 | 11.56 | 32.83%
[5 empty] | 11.58 | 1144000 | 660 | 100% | 100% | 8.181% | 0.31182 | 54600 | 243540 | 65813.017 | 363953.017 | 464.4503 | 7499.3041 | 11.58 | 33.01%
[5 empty] | 11.6 | 1144000 | 660 | 100% | 100% | 8.423% | 0.31363 | 54600 | 243540 | 67756.057 | 365896.057 | 472.0039 | 7621.2695 | 11.6 | 33.19%
[5 empty] | 11.62 | 1144000 | 660 | 100% | 100% | 8.665% | 0.31544 | 54600 | 243540 | 69699.097 | 367839.097 | 479.5976 | 7743.8825 | 11.62 | 33.36%
[5 empty] | 11.64 | 1144000 | 660 | 100% | 100% | 8.906% | 0.31725 | 54600 | 243540 | 71642.137 | 369782.137 | 487.2315 | 7867.1432 | 11.64 | 33.54%
[5 empty] | 11.66 | 1144000 | 660 | 100% | 100% | 9.148% | 0.31906 | 54600 | 243540 | 73585.177 | 371725.177 | 494.9054 | 7991.0516 | 11.66 | 33.71%
[5 empty] | 11.68 | 1144000 | 660 | 100% | 100% | 9.389% | 0.32087 | 54600 | 243540 | 75528.217 | 373668.217 | 502.6195 | 8115.6077 | 11.68 | 33.89%
[5 empty] | 11.7 | 1144000 | 660 | 100% | 100% | 9.631% | 0.32268 | 54600 | 243540 | 77471.257 | 375611.257 | 510.3736 | 8240.8114 | 11.7 | 34.07%
[5 empty] | 11.72 | 1144000 | 660 | 100% | 100% | 9.872% | 0.32449 | 54600 | 243540 | 79414.297 | 377554.297 | 518.1679 | 8366.6629 | 11.72 | 34.24%
[5 empty] | 11.74 | 1144000 | 660 | 100% | 100% | 10.11% | 0.3263 | 54600 | 243540 | 81357.337 | 379497.337 | 526.0023 | 8493.162 | 11.74 | 34.42%
[5 empty] | 11.76 | 1144000 | 660 | 100% | 100% | 10.36% | 0.32811 | 54600 | 243540 | 83300.377 | 381440.377 | 533.8768 | 8620.3088 | 11.76 | 34.6%
[5 empty] | 11.78 | 1144000 | 660 | 100% | 100% | 10.6% | 0.32992 | 54600 | 243540 | 85243.417 | 383383.417 | 541.7915 | 8748.1032 | 11.78 | 34.77%
[5 empty] | 11.8 | 1144000 | 660 | 100% | 100% | 10.84% | 0.33173 | 54600 | 243540 | 87186.457 | 385326.457 | 549.7462 | 8876.5454 | 11.8 | 34.95%
[5 empty] | 11.82 | 1144000 | 660 | 100% | 100% | 11.08% | 0.33354 | 54600 | 243540 | 89129.497 | 387269.497 | 557.7411 | 9005.6352 | 11.82 | 35.12%
[5 empty] | 11.84 | 1144000 | 660 | 100% | 100% | 11.32% | 0.33535 | 54600 | 243540 | 91072.537 | 389212.537 | 565.776 | 9135.3727 | 11.84 | 35.3%
[5 empty] | 11.86 | 1144000 | 660 | 100% | 100% | 11.56% | 0.33716 | 54600 | 243540 | 93015.577 | 391155.577 | 573.8511 | 9265.7579 | 11.86 | 35.48%
[5 empty] | 11.88 | 1144000 | 660 | 100% | 100% | 11.8% | 0.33897 | 54600 | 243540 | 94958.617 | 393098.617 | 581.9663 | 9396.7908 | 11.88 | 35.65%
[5 empty] | 11.9 | 1144000 | 660 | 100% | 100% | 12.05% | 0.34078 | 54600 | 243540 | 96901.657 | 395041.657 | 590.1216 | 9528.4713 | 11.9 | 35.83%
[5 empty] | 11.92 | 1144000 | 660 | 100% | 100% | 12.29% | 0.34259 | 54600 | 243540 | 98844.697 | 396984.697 | 598.317 | 9660.7996 | 11.92 | 36.01%
[5 empty] | 11.94 | 1144000 | 660 | 100% | 100% | 12.53% | 0.3444 | 54600 | 243540 | 100787.737 | 398927.737 | 606.5525 | 9793.7755 | 11.94 | 36.18%
[5 empty] | 11.96 | 1144000 | 660 | 100% | 100% | 12.77% | 0.34622 | 54600 | 243540 | 102730.777 | 400870.777 | 614.8281 | 9927.3991 | 11.96 | 36.36%
[5 empty] | 11.98 | 1144000 | 660 | 100% | 100% | 13.01% | 0.34803 | 54600 | 243540 | 104673.817 | 402813.817 | 623.1439 | 10061.6704 | 11.98 | 36.53%
[5 empty] | 12 | 1144000 | 660 | 100% | 100% | 13.25% | 0.34984 | 54600 | 243540 | 106616.857 | 404756.857 | 631.4998 | 10196.5893 | 12 | 36.71%
[5 empty] | 12.02 | 1144000 | 660 | 100% | 100% | 13.5% | 0.35165 | 54600 | 243540 | 108559.897 | 406699.897 | 639.8957 | 10332.1559 | 12.02 | 36.89%
[5 empty] | 12.04 | 1144000 | 660 | 100% | 100% | 13.74% | 0.35346 | 54600 | 243540 | 110502.937 | 408642.937 | 648.3318 | 10468.3702 | 12.04 | 37.06%
[5 empty] | 12.06 | 1144000 | 660 | 100% | 100% | 13.98% | 0.35527 | 54600 | 243540 | 112445.977 | 410585.977 | 656.808 | 10605.2322 | 12.06 | 37.24%
[5 empty] | 12.08 | 1144000 | 660 | 100% | 100% | 14.22% | 0.35708 | 54600 | 243540 | 114389.017 | 412529.017 | 665.3243 | 10742.7419 | 12.08 | 37.42%
[5 empty] | 12.1 | 1144000 | 660 | 100% | 100% | 14.46% | 0.35889 | 54600 | 243540 | 116332.057 | 414472.057 | 673.8808 | 10880.8993 | 12.1 | 37.59%
[5 empty] | 12.12 | 1144000 | 660 | 100% | 100% | 14.7% | 0.3607 | 54600 | 243540 | 118275.097 | 416415.097 | 682.4773 | 11019.7043 | 12.12 | 37.77%
[5 empty] | 12.14 | 1144000 | 660 | 100% | 100% | 14.94% | 0.36251 | 54600 | 243540 | 120218.137 | 418358.137 | 691.1139 | 11159.157 | 12.14 | 37.94%
[5 empty] | 12.16 | 1144000 | 660 | 100% | 100% | 15.19% | 0.36432 | 54600 | 243540 | 122161.177 | 420301.177 | 699.7907 | 11299.2574 | 12.16 | 38.12%
[5 empty] | 12.18 | 1144000 | 660 | 100% | 100% | 15.43% | 0.36613 | 54600 | 243540 | 124104.217 | 422244.217 | 708.5076 | 11440.0055 | 12.18 | 38.3%
[5 empty] | 12.2 | 1144000 | 660 | 100% | 100% | 15.67% | 0.36794 | 54600 | 243540 | 126047.257 | 424187.257 | 717.2646 | 11581.4012 | 12.2 | 38.47%
[5 empty] | 12.22 | 1144000 | 660 | 100% | 100% | 15.91% | 0.36975 | 54600 | 243540 | 127990.297 | 426130.297 | 726.0617 | 11723.4447 | 12.22 | 38.65%
[5 empty] | 12.24 | 1144000 | 660 | 100% | 100% | 16.15% | 0.37156 | 54600 | 243540 | 129933.337 | 428073.337 | 734.8989 | 11866.1358 | 12.24 | 38.83%
[5 empty] | 12.26 | 1144000 | 660 | 100% | 100% | 16.39% | 0.37337 | 54600 | 243540 | 131876.377 | 430016.377 | 743.7762 | 12009.4746 | 12.26 | 39%
[5 empty] | 12.28 | 1144000 | 660 | 100% | 100% | 16.64% | 0.37518 | 54600 | 243540 | 133819.417 | 431959.417 | 752.6936 | 12153.461 | 12.28 | 39.18%
[5 empty] | 12.3 | 1144000 | 660 | 100% | 100% | 16.88% | 0.37699 | 54600 | 243540 | 135762.457 | 433902.457 | 761.6512 | 12298.0952 | 12.3 | 39.35%
[5 empty] | 12.32 | 1144000 | 660 | 100% | 100% | 17.12% | 0.3788 | 54600 | 243540 | 137705.497 | 435845.497 | 770.6488 | 12443.377 | 12.32 | 39.53%
[5 empty] | 12.34 | 1144000 | 660 | 100% | 100% | 17.36% | 0.38061 | 54600 | 243540 | 139648.537 | 437788.537 | 779.6866 | 12589.3065 | 12.34 | 39.71%
[5 empty] | 12.36 | 1144000 | 660 | 100% | 100% | 17.6% | 0.38242 | 54600 | 243540 | 141591.577 | 439731.577 | 788.7645 | 12735.8837 | 12.36 | 39.88%
[5 empty] | 12.38 | 1144000 | 660 | 100% | 100% | 17.84% | 0.38423 | 54600 | 243540 | 143534.617 | 441674.617 | 797.8825 | 12883.1086 | 12.38 | 40.06%
[5 empty] | 12.4 | 1144000 | 660 | 100% | 100% | 18.08% | 0.38604 | 54600 | 243540 | 145477.657 | 443617.657 | 807.0406 | 13030.9812 | 12.4 | 40.24%
[5 empty] | 12.42 | 1144000 | 660 | 100% | 100% | 18.33% | 0.38785 | 54600 | 243540 | 147420.697 | 445560.697 | 816.2388 | 13179.5014 | 12.42 | 40.41%
[5 empty] | 12.44 | 1144000 | 660 | 100% | 100% | 18.57% | 0.38966 | 54600 | 243540 | 149363.737 | 447503.737 | 825.4771 | 13328.6693 | 12.44 | 40.59%
[5 empty] | 12.46 | 1144000 | 660 | 100% | 100% | 18.81% | 0.39147 | 54600 | 243540 | 151306.777 | 449446.777 | 834.7556 | 13478.4849 | 12.46 | 40.76%
[5 empty] | 12.48 | 1144000 | 660 | 100% | 100% | 19.05% | 0.39329 | 54600 | 243540 | 153249.817 | 451389.817 | 844.0742 | 13628.9482 | 12.48 | 40.94%
[5 empty] | 12.5 | 1144000 | 660 | 100% | 100% | 19.29% | 0.3951 | 54600 | 243540 | 155192.857 | 453332.857 | 853.4328 | 13780.0591 | 12.5 | 41.12%
[5 empty] | 12.52 | 1144000 | 660 | 100% | 100% | 19.53% | 0.39691 | 54600 | 243540 | 157135.897 | 455275.897 | 862.8316 | 13931.8177 | 12.52 | 41.29%
[5 empty] | 12.54 | 1144000 | 660 | 100% | 100% | 19.78% | 0.39872 | 54600 | 243540 | 159078.937 | 457218.937 | 872.2705 | 14084.2241 | 12.54 | 41.47%
[5 empty] | 12.56 | 1144000 | 660 | 100% | 100% | 20.02% | 0.40053 | 54600 | 243540 | 161021.977 | 459161.977 | 881.7495 | 14237.278 | 12.56 | 41.65%
[5 empty] | 12.58 | 1144000 | 660 | 100% | 100% | 20.26% | 0.40234 | 54600 | 243540 | 162965.017 | 461105.017 | 891.2686 | 14390.9797 | 12.58 | 41.82%
[5 empty] | 12.6 | 1144000 | 660 | 100% | 100% | 20.5% | 0.40415 | 54600 | 243540 | 164908.057 | 463048.057 | 900.8279 | 14545.3291 | 12.6 | 42%
[5 empty] | 12.62 | 1144000 | 660 | 100% | 100% | 20.74% | 0.40596 | 54600 | 243540 | 166851.097 | 464991.097 | 910.4272 | 14700.3261 | 12.62 | 42.17%
[5 empty] | 12.64 | 1144000 | 660 | 100% | 100% | 20.98% | 0.40777 | 54600 | 243540 | 168794.137 | 466934.137 | 920.0667 | 14855.9708 | 12.64 | 42.35%
[5 empty] | 12.66 | 1144000 | 660 | 100% | 100% | 21.22% | 0.40958 | 54600 | 243540 | 170737.177 | 468877.177 | 929.7462 | 15012.2632 | 12.66 | 42.53%
[5 empty] | 12.68 | 1144000 | 660 | 100% | 100% | 21.47% | 0.41139 | 54600 | 243540 | 172680.217 | 470820.217 | 939.4659 | 15169.2033 | 12.68 | 42.7%
[5 empty] | 12.7 | 1144000 | 660 | 100% | 100% | 21.71% | 0.4132 | 54600 | 243540 | 174623.257 | 472763.257 | 949.2257 | 15326.791 | 12.7 | 42.88%
[5 empty] | 12.72 | 1144000 | 660 | 100% | 100% | 21.95% | 0.41501 | 54600 | 243540 | 176566.297 | 474706.297 | 959.0256 | 15485.0265 | 12.72 | 43.05%
[5 empty] | 12.74 | 1144000 | 660 | 100% | 100% | 22.19% | 0.41682 | 54600 | 243540 | 178509.337 | 476649.337 | 968.8656 | 15643.9096 | 12.74 | 43.23%
[5 empty] | 12.76 | 1144000 | 660 | 100% | 100% | 22.43% | 0.41863 | 54600 | 243540 | 180452.377 | 478592.377 | 978.7458 | 15803.4404 | 12.76 | 43.41%
[5 empty] | 12.78 | 1144000 | 660 | 100% | 100% | 22.67% | 0.42044 | 54600 | 243540 | 182395.417 | 480535.417 | 988.666 | 15963.6188 | 12.78 | 43.58%
[5 empty] | 12.8 | 1144000 | 660 | 100% | 100% | 22.92% | 0.42225 | 54600 | 243540 | 184338.457 | 482478.457 | 998.6264 | 16124.445 | 12.8 | 43.76%
[5 empty] | 12.82 | 1144000 | 660 | 100% | 100% | 23.16% | 0.42406 | 54600 | 243540 | 186281.497 | 484421.497 | 1008.6269 | 16285.9188 | 12.82 | 43.94%
[5 empty] | 12.84 | 1144000 | 660 | 100% | 100% | 23.4% | 0.42587 | 54600 | 243540 | 188224.537 | 486364.537 | 1018.6674 | 16448.0403 | 12.84 | 44.11%
[5 empty] | 12.86 | 1144000 | 660 | 100% | 100% | 23.64% | 0.42768 | 54600 | 243540 | 190167.577 | 488307.577 | 1028.7481 | 16610.8095 | 12.86 | 44.29%
[5 empty] | 12.88 | 1144000 | 660 | 100% | 100% | 23.88% | 0.42949 | 54600 | 243540 | 192110.617 | 490250.617 | 1038.8689 | 16774.2264 | 12.88 | 44.46%
[5 empty] | 12.9 | 1144000 | 660 | 100% | 100% | 24.12% | 0.4313 | 54600 | 243540 | 194053.657 | 492193.657 | 1049.0299 | 16938.291 | 12.9 | 44.64%
[5 empty] | 12.92 | 1144000 | 660 | 100% | 100% | 24.37% | 0.43311 | 54600 | 243540 | 195996.697 | 494136.697 | 1059.2309 | 17103.0032 | 12.92 | 44.82%
[5 empty] | 12.94 | 1144000 | 660 | 100% | 100% | 24.61% | 0.43492 | 54600 | 243540 | 197939.737 | 496079.737 | 1069.472 | 17268.3631 | 12.94 | 44.99%
[5 empty] | 12.96 | 1144000 | 660 | 100% | 100% | 24.85% | 0.43673 | 54600 | 243540 | 199882.777 | 498022.777 | 1079.7533 | 17434.3707 | 12.96 | 45.17%
[5 empty] | 12.98 | 1144000 | 660 | 100% | 100% | 25.09% | 0.43855 | 54600 | 243540 | 201825.817 | 499965.817 | 1090.0747 | 17601.026 | 12.98 | 45.35%
[5 empty] | 13 | 1144000 | 660 | 100% | 100% | 25.33% | 0.44036 | 54600 | 243540 | 203768.857 | 501908.857 | 1100.4361 | 17768.3289 | 13 | 45.52%
[5 empty] | 13.02 | 1144000 | 660 | 100% | 100% | 25.57% | 0.44217 | 54600 | 243540 | 205711.897 | 503851.897 | 1110.8377 | 17936.2796 | 13.02 | 45.7%
[5 empty] | 13.04 | 1144000 | 660 | 100% | 100% | 25.81% | 0.44398 | 54600 | 243540 | 207654.937 | 505794.937 | 1121.2794 | 18104.8779 | 13.04 | 45.87%
[5 empty] | 13.06 | 1144000 | 660 | 100% | 100% | 26.06% | 0.44579 | 54600 | 243540 | 209597.977 | 507737.977 | 1131.7613 | 18274.1239 | 13.06 | 46.05%
[5 empty] | 13.08 | 1144000 | 660 | 100% | 100% | 26.3% | 0.4476 | 54600 | 243540 | 211541.017 | 509681.017 | 1142.2832 | 18444.0175 | 13.08 | 46.23%
[5 empty] | 13.1 | 1144000 | 660 | 100% | 100% | 26.54% | 0.44941 | 54600 | 243540 | 213484.057 | 511624.057 | 1152.8452 | 18614.5589 | 13.1 | 46.4%
[5 empty] | 13.12 | 1144000 | 660 | 100% | 100% | 26.78% | 0.45122 | 54600 | 243540 | 215427.097 | 513567.097 | 1163.4474 | 18785.7479 | 13.12 | 46.58%
[5 empty] | 13.14 | 1144000 | 660 | 100% | 100% | 27.02% | 0.45303 | 54600 | 243540 | 217370.137 | 515510.137 | 1174.0897 | 18957.5846 | 13.14 | 46.76%
[5 empty] | 13.16 | 1144000 | 660 | 100% | 100% | 27.26% | 0.45484 | 54600 | 243540 | 219313.177 | 517453.177 | 1184.772 | 19130.069 | 13.16 | 46.93%
[5 empty] | 13.18 | 1144000 | 660 | 100% | 100% | 27.51% | 0.45665 | 54600 | 243540 | 221256.217 | 519396.217 | 1195.4945 | 19303.2011 | 13.18 | 47.11%
[5 empty] | 13.2 | 1144000 | 660 | 100% | 100% | 27.75% | 0.45846 | 54600 | 243540 | 223199.257 | 521339.257 | 1206.2571 | 19476.9808 | 13.2 | 47.28%
[5 empty] | 13.22 | 1144000 | 660 | 100% | 100% | 27.99% | 0.46027 | 54600 | 243540 | 225142.297 | 523282.297 | 1217.0599 | 19651.4083 | 13.22 | 47.46%
[5 empty] | 13.24 | 1144000 | 660 | 100% | 100% | 28.23% | 0.46208 | 54600 | 243540 | 227085.337 | 525225.337 | 1227.9027 | 19826.4834 | 13.24 | 47.64%
[5 empty] | 13.26 | 1144000 | 660 | 100% | 100% | 28.47% | 0.46389 | 54600 | 243540 | 229028.377 | 527168.377 | 1238.7856 | 20002.2062 | 13.26 | 47.81%
[5 empty] | 13.28 | 1144000 | 660 | 100% | 100% | 28.71% | 0.4657 | 54600 | 243540 | 230971.417 | 529111.417 | 1249.7087 | 20178.5767 | 13.28 | 47.99%
[5 empty] | 13.3 | 1144000 | 660 | 100% | 100% | 28.95% | 0.46751 | 54600 | 243540 | 232914.457 | 531054.457 | 1260.6719 | 20355.5948 | 13.3 | 48.17%
[5 empty] | 13.32 | 1144000 | 660 | 100% | 100% | 29.2% | 0.46932 | 54600 | 243540 | 234857.497 | 532997.497 | 1271.6751 | 20533.2606 | 13.32 | 48.34%
[5 empty] | 13.34 | 1144000 | 660 | 100% | 100% | 29.44% | 0.47113 | 54600 | 243540 | 236800.537 | 534940.537 | 1282.7185 | 20711.5742 | 13.34 | 48.52%
[5 empty] | 13.36 | 1144000 | 660 | 100% | 100% | 29.68% | 0.47294 | 54600 | 243540 | 238743.577 | 536883.577 | 1293.802 | 20890.5353 | 13.36 | 48.69%
[5 empty] | 13.38 | 1144000 | 660 | 100% | 100% | 29.92% | 0.47475 | 54600 | 243540 | 240686.617 | 538826.617 | 1304.9257 | 21070.1442 | 13.38 | 48.87%
[5 empty] | 13.4 | 1144000 | 660 | 100% | 100% | 30.16% | 0.47656 | 54600 | 243540 | 242629.657 | 540769.657 | 1316.0894 | 21250.4008 | 13.4 | 49.05%
[5 empty] | 13.42 | 1144000 | 660 | 100% | 100% | 30.4% | 0.47837 | 54600 | 243540 | 244572.697 | 542712.697 | 1327.2932 | 21431.305 | 13.42 | 49.22%
[5 empty] | 13.44 | 1144000 | 660 | 100% | 100% | 30.65% | 0.48018 | 54600 | 243540 | 246515.737 | 544655.737 | 1338.5372 | 21612.8569 | 13.44 | 49.4%
[5 empty] | 13.46 | 1144000 | 660 | 100% | 100% | 30.89% | 0.48199 | 54600 | 243540 | 248458.777 | 546598.777 | 1349.8212 | 21795.0565 | 13.46 | 49.58%
[5 empty] | 13.48 | 1144000 | 660 | 100% | 100% | 31.13% | 0.4838 | 54600 | 243540 | 250401.817 | 548541.817 | 1361.1454 | 21977.9038 | 13.48 | 49.75%
[5 empty] | 13.5 | 1144000 | 660 | 100% | 100% | 31.37% | 0.48562 | 54600 | 243540 | 252344.857 | 550484.857 | 1372.5097 | 22161.3987 | 13.5 | 49.93%
[5 empty] | 13.52 | 1144000 | 660 | 100% | 100% | 31.61% | 0.48743 | 54600 | 243540 | 254287.897 | 552427.897 | 1383.9141 | 22345.5414 | 13.52 | 50.1%
[5 empty] | 13.54 | 1144000 | 660 | 100% | 100% | 31.85% | 0.48924 | 54600 | 243540 | 256230.937 | 554370.937 | 1395.3586 | 22530.3317 | 13.54 | 50.28%
[5 empty] | 13.56 | 1144000 | 660 | 100% | 100% | 32.09% | 0.49105 | 54600 | 243540 | 258173.977 | 556313.977 | 1406.8433 | 22715.7697 | 13.56 | 50.46%
[5 empty] | 13.58 | 1144000 | 660 | 100% | 100% | 32.34% | 0.49286 | 54600 | 243540 | 260117.017 | 558257.017 | 1418.368 | 22901.8553 | 13.58 | 50.63%
[5 empty] | 13.6 | 1144000 | 660 | 100% | 100% | 32.58% | 0.49467 | 54600 | 243540 | 262060.057 | 560200.057 | 1429.9329 | 23088.5887 | 13.6 | 50.81%
[5 empty] | 13.62 | 1144000 | 660 | 100% | 100% | 32.82% | 0.49648 | 54600 | 243540 | 264003.097 | 562143.097 | 1441.5378 | 23275.9697 | 13.62 | 50.99%
[5 empty] | 13.64 | 1144000 | 660 | 100% | 100% | 33.06% | 0.49829 | 54600 | 243540 | 265946.137 | 564086.137 | 1453.1829 | 23463.9984 | 13.64 | 51.16%
[5 empty] | 13.66 | 1144000 | 660 | 100% | 100% | 33.3% | 0.5001 | 54600 | 243540 | 267889.177 | 566029.177 | 1464.8681 | 23652.6748 | 13.66 | 51.34%
[5 empty] | 13.68 | 1144000 | 660 | 100% | 100% | 33.54% | 0.50191 | 54600 | 243540 | 269832.217 | 567972.217 | 1476.5934 | 23841.9989 | 13.68 | 51.51%
[5 empty] | 13.7 | 1144000 | 660 | 100% | 100% | 33.79% | 0.50372 | 54600 | 243540 | 271775.257 | 569915.257 | 1488.3588 | 24031.9707 | 13.7 | 51.69%
[5 empty] | 13.72 | 1144000 | 660 | 100% | 100% | 34.03% | 0.50553 | 54600 | 243540 | 273718.297 | 571858.297 | 1500.1644 | 24222.5901 | 13.72 | 51.87%
[5 empty] | 13.74 | 1144000 | 660 | 100% | 100% | 34.27% | 0.50734 | 54600 | 243540 | 275661.337 | 573801.337 | 1512.01 | 24413.8572 | 13.74 | 52.04%
[5 empty] | 13.76 | 1144000 | 660 | 100% | 100% | 34.51% | 0.50915 | 54600 | 243540 | 277604.377 | 575744.377 | 1523.8957 | 24605.772 | 13.76 | 52.22%
[5 empty] | 13.78 | 1144000 | 660 | 100% | 100% | 34.75% | 0.51096 | 54600 | 243540 | 279547.417 | 577687.417 | 1535.8216 | 24798.3345 | 13.78 | 52.4%
[5 empty] | 13.8 | 1144000 | 660 | 100% | 100% | 34.99% | 0.51277 | 54600 | 243540 | 281490.457 | 579630.457 | 1547.7876 | 24991.5446 | 13.8 | 52.57%
[5 empty] | 13.82 | 1144000 | 660 | 100% | 100% | 35.23% | 0.51458 | 54600 | 243540 | 283433.497 | 581573.497 | 1559.7937 | 25185.4024 | 13.82 | 52.75%
[5 empty] | 13.84 | 1144000 | 660 | 100% | 100% | 35.48% | 0.51639 | 54600 | 243540 | 285376.537 | 583516.537 | 1571.8399 | 25379.908 | 13.84 | 52.92%
[5 empty] | 13.86 | 1144000 | 660 | 100% | 100% | 35.72% | 0.5182 | 54600 | 243540 | 287319.577 | 585459.577 | 1583.9262 | 25575.0612 | 13.86 | 53.1%
[5 empty] | 13.88 | 1144000 | 660 | 100% | 100% | 35.96% | 0.52001 | 54600 | 243540 | 289262.617 | 587402.617 | 1596.0526 | 25770.862 | 13.88 | 53.28%
[5 empty] | 13.9 | 1144000 | 660 | 100% | 100% | 36.2% | 0.52182 | 54600 | 243540 | 291205.657 | 589345.657 | 1608.2192 | 25967.3106 | 13.9 | 53.45%
[5 empty] | 13.92 | 1144000 | 660 | 100% | 100% | 36.44% | 0.52363 | 54600 | 243540 | 293148.697 | 591288.697 | 1620.4258 | 26164.4068 | 13.92 | 53.63%
[5 empty] | 13.94 | 1144000 | 660 | 100% | 100% | 36.68% | 0.52544 | 54600 | 243540 | 295091.737 | 593231.737 | 1632.6726 | 26362.1507 | 13.94 | 53.81%
[5 empty] | 13.96 | 1144000 | 660 | 100% | 100% | 36.93% | 0.52725 | 54600 | 243540 | 297034.777 | 595174.777 | 1644.9595 | 26560.5423 | 13.96 | 53.98%
[5 empty] | 13.98 | 1144000 | 660 | 100% | 100% | 37.17% | 0.52906 | 54600 | 243540 | 298977.817 | 597117.817 | 1657.2865 | 26759.5816 | 13.98 | 54.16%
[5 empty] | 14 | 1144000 | 660 | 100% | 100% | 37.41% | 0.53088 | 54600 | 243540 | 300920.857 | 599060.857 | 1669.6536 | 26959.2685 | 14 | 54.33%
[5 empty] | 14.02 | 1144000 | 660 | 100% | 100% | 37.65% | 0.53269 | 54600 | 243540 | 302863.897 | 601003.897 | 1682.0608 | 27159.6032 | 14.02 | 54.51%
[5 empty] | 14.04 | 1144000 | 660 | 100% | 100% | 37.89% | 0.5345 | 54600 | 243540 | 304806.937 | 602946.937 | 1694.5081 | 27360.5855 | 14.04 | 54.69%
[5 empty] | 14.06 | 1144000 | 660 | 100% | 100% | 38.13% | 0.53631 | 54600 | 243540 | 306749.977 | 604889.977 | 1706.9955 | 27562.2155 | 14.06 | 54.86%
[5 empty] | 14.08 | 1144000 | 660 | 100% | 100% | 38.37% | 0.53812 | 54600 | 243540 | 308693.017 | 606833.017 | 1719.5231 | 27764.4931 | 14.08 | 55.04%
[5 empty] | 14.1 | 1144000 | 660 | 100% | 100% | 38.62% | 0.53993 | 54600 | 243540 | 310636.057 | 608776.057 | 1732.0907 | 27967.4185 | 14.1 | 55.21%
[5 empty] | 14.12 | 1144000 | 660 | 100% | 100% | 38.86% | 0.54174 | 54600 | 243540 | 312579.097 | 610719.097 | 1744.6985 | 28170.9915 | 14.12 | 55.39%
[5 empty] | 14.14 | 1144000 | 660 | 100% | 100% | 39.1% | 0.54355 | 54600 | 243540 | 314522.137 | 612662.137 | 1757.3464 | 28375.2122 | 14.14 | 55.57%
[5 empty] | 14.16 | 1144000 | 660 | 100% | 100% | 39.34% | 0.54536 | 54600 | 243540 | 316465.177 | 614605.177 | 1770.0344 | 28580.0806 | 14.16 | 55.74%
[5 empty] | 14.18 | 1144000 | 660 | 100% | 100% | 39.58% | 0.54717 | 54600 | 243540 | 318408.217 | 616548.217 | 1782.7625 | 28785.5967 | 14.18 | 55.92%
[5 empty] | 14.2 | 1144000 | 660 | 100% | 100% | 39.82% | 0.54898 | 54600 | 243540 | 320351.257 | 618491.257 | 1795.5308 | 28991.7605 | 14.2 | 56.1%
[5 empty] | 14.22 | 1144000 | 660 | 100% | 100% | 40.07% | 0.55079 | 54600 | 243540 | 322294.297 | 620434.297 | 1808.3391 | 29198.5719 | 14.22 | 56.27%
[5 empty] | 14.24 | 1144000 | 660 | 100% | 100% | 40.31% | 0.5526 | 54600 | 243540 | 324237.337 | 622377.337 | 1821.1875 | 29406.031 | 14.24 | 56.45%
[5 empty] | 14.26 | 1144000 | 660 | 100% | 100% | 40.55% | 0.55441 | 54600 | 243540 | 326180.377 | 624320.377 | 1834.0761 | 29614.1378 | 14.26 | 56.62%
[5 empty] | 14.28 | 1144000 | 660 | 100% | 100% | 40.79% | 0.55622 | 54600 | 243540 | 328123.417 | 626263.417 | 1847.0048 | 29822.8923 | 14.28 | 56.8%
[5 empty] | 14.3 | 1144000 | 660 | 100% | 100% | 41.03% | 0.55803 | 54600 | 243540 | 330066.457 | 628206.457 | 1859.9736 | 30032.2944 | 14.3 | 56.98%
[5 empty] | 14.32 | 1144000 | 660 | 100% | 100% | 41.27% | 0.55984 | 54600 | 243540 | 332009.497 | 630149.497 | 1872.9825 | 30242.3443 | 14.32 | 57.15%
[5 empty] | 14.34 | 1144000 | 660 | 100% | 100% | 41.51% | 0.56165 | 54600 | 243540 | 333952.537 | 632092.537 | 1886.0315 | 30453.0418 | 14.34 | 57.33%
[5 empty] | 14.36 | 1144000 | 660 | 100% | 100% | 41.76% | 0.56346 | 54600 | 243540 | 335895.577 | 634035.577 | 1899.1206 | 30664.387 | 14.36 | 57.51%
[5 empty] | 14.38 | 1144000 | 660 | 100% | 100% | 42% | 0.56527 | 54600 | 243540 | 337838.617 | 635978.617 | 1912.2499 | 30876.3798 | 14.38 | 57.68%
[5 empty] | 14.4 | 1144000 | 660 | 100% | 100% | 42.24% | 0.56708 | 54600 | 243540 | 339781.657 | 637921.657 | 1925.4192 | 31089.0204 | 14.4 | 57.86%
[5 empty] | 14.42 | 1144000 | 660 | 100% | 100% | 42.48% | 0.56889 | 54600 | 243540 | 341724.697 | 639864.697 | 1938.6287 | 31302.3086 | 14.42 | 58.03%
[5 empty] | 14.44 | 1144000 | 660 | 100% | 100% | 42.72% | 0.5707 | 54600 | 243540 | 343667.737 | 641807.737 | 1951.8782 | 31516.2445 | 14.44 | 58.21%
[5 empty] | 14.46 | 1144000 | 660 | 100% | 100% | 42.96% | 0.57251 | 54600 | 243540 | 345610.777 | 643750.777 | 1965.1679 | 31730.8281 | 14.46 | 58.39%
[5 empty] | 14.48 | 1144000 | 660 | 100% | 100% | 43.21% | 0.57432 | 54600 | 243540 | 347553.817 | 645693.817 | 1978.4977 | 31946.0594 | 14.48 | 58.56%
[5 empty] | 14.5 | 1144000 | 660 | 100% | 100% | 43.45% | 0.57613 | 54600 | 243540 | 349496.857 | 647636.857 | 1991.8676 | 32161.9383 | 14.5 | 58.74%
[5 empty] | 14.52 | 1144000 | 660 | 100% | 100% | 43.69% | 0.57795 | 54600 | 243540 | 351439.897 | 649579.897 | 2005.2777 | 32378.465 | 14.52 | 58.92%
[5 empty] | 14.54 | 1144000 | 660 | 100% | 100% | 43.93% | 0.57976 | 54600 | 243540 | 353382.937 | 651522.937 | 2018.7278 | 32595.6393 | 14.54 | 59.09%
[5 empty] | 14.56 | 1144000 | 660 | 100% | 100% | 44.17% | 0.58157 | 54600 | 243540 | 355325.977 | 653465.977 | 2032.2181 | 32813.4613 | 14.56 | 59.27%
[5 empty] | 14.58 | 1144000 | 660 | 100% | 100% | 44.41% | 0.58338 | 54600 | 243540 | 357269.017 | 655409.017 | 2045.7484 | 33031.931 | 14.58 | 59.44%
[5 empty] | 14.6 | 1144000 | 660 | 100% | 100% | 44.65% | 0.58519 | 54600 | 243540 | 359212.057 | 657352.057 | 2059.3189 | 33251.0483 | 14.6 | 59.62%
[5 empty] | 14.62 | 1144000 | 660 | 100% | 100% | 44.9% | 0.587 | 54600 | 243540 | 361155.097 | 659295.097 | 2072.9295 | 33470.8133 | 14.62 | 59.8%
[5 empty] | 14.64 | 1144000 | 660 | 100% | 100% | 45.14% | 0.58881 | 54600 | 243540 | 363098.137 | 661238.137 | 2086.5802 | 33691.2261 | 14.64 | 59.97%
[5 empty] | 14.66 | 1144000 | 660 | 100% | 100% | 45.38% | 0.59062 | 54600 | 243540 | 365041.177 | 663181.177 | 2100.271 | 33912.2864 | 14.66 | 60.15%
[5 empty] | 14.68 | 1144000 | 660 | 100% | 100% | 45.62% | 0.59243 | 54600 | 243540 | 366984.217 | 665124.217 | 2114.0019 | 34133.9945 | 14.68 | 60.33%
[5 empty] | 14.7 | 1144000 | 660 | 100% | 100% | 45.86% | 0.59424 | 54600 | 243540 | 368927.257 | 667067.257 | 2127.7729 | 34356.3503 | 14.7 | 60.5%
[5 empty] | 14.72 | 1144000 | 660 | 100% | 100% | 46.1% | 0.59605 | 54600 | 243540 | 370870.297 | 669010.297 | 2141.5841 | 34579.3537 | 14.72 | 60.68%
[5 empty] | 14.74 | 1144000 | 660 | 100% | 100% | 46.35% | 0.59786 | 54600 | 243540 | 372813.337 | 670953.337 | 2155.4354 | 34803.0048 | 14.74 | 60.85%
[5 empty] | 14.76 | 1144000 | 660 | 100% | 100% | 46.59% | 0.59967 | 54600 | 243540 | 374756.377 | 672896.377 | 2169.3267 | 35027.3036 | 14.76 | 61.03%
[5 empty] | 14.78 | 1144000 | 660 | 100% | 100% | 46.83% | 0.60148 | 54600 | 243540 | 376699.417 | 674839.417 | 2183.2582 | 35252.2501 | 14.78 | 61.21%
[5 empty] | 14.8 | 1144000 | 660 | 100% | 100% | 47.07% | 0.60329 | 54600 | 243540 | 378642.457 | 676782.457 | 2197.2298 | 35477.8442 | 14.8 | 61.38%
[5 empty] | 14.82 | 1144000 | 660 | 100% | 100% | 47.31% | 0.6051 | 54600 | 243540 | 380585.497 | 678725.497 | 2211.2415 | 35704.0861 | 14.82 | 61.56%
[5 empty] | 14.84 | 1144000 | 660 | 100% | 100% | 47.55% | 0.60691 | 54600 | 243540 | 382528.537 | 680668.537 | 2225.2934 | 35930.9756 | 14.84 | 61.74%
[5 empty] | 14.86 | 1144000 | 660 | 100% | 100% | 47.79% | 0.60872 | 54600 | 243540 | 384471.577 | 682611.577 | 2239.3853 | 36158.5128 | 14.86 | 61.91%
[5 empty] | 14.88 | 1144000 | 660 | 100% | 100% | 48.04% | 0.61053 | 54600 | 243540 | 386414.617 | 684554.617 | 2253.5173 | 36386.6976 | 14.88 | 62.09%
[5 empty] | 14.9 | 1144000 | 660 | 100% | 100% | 48.28% | 0.61234 | 54600 | 243540 | 388357.657 | 686497.657 | 2267.6895 | 36615.5302 | 14.9 | 62.26%
[5 empty] | 14.92 | 1144000 | 660 | 100% | 100% | 48.52% | 0.61415 | 54600 | 243540 | 390300.697 | 688440.697 | 2281.9018 | 36845.0104 | 14.92 | 62.44%
[5 empty] | 14.94 | 1144000 | 660 | 100% | 100% | 48.76% | 0.61596 | 54600 | 243540 | 392243.737 | 690383.737 | 2296.1542 | 37075.1383 | 14.94 | 62.62%
[5 empty] | 14.96 | 1144000 | 660 | 100% | 100% | 49% | 0.61777 | 54600 | 243540 | 394186.777 | 692326.777 | 2310.4467 | 37305.9139 | 14.96 | 62.79%
[5 empty] | 14.98 | 1144000 | 660 | 100% | 100% | 49.24% | 0.61958 | 54600 | 243540 | 396129.817 | 694269.817 | 2324.7793 | 37537.3372 | 14.98 | 62.97%
[5 empty] | 15 | 1144000 | 660 | 100% | 100% | 49.49% | 0.62139 | 54600 | 243540 | 398072.857 | 696212.857 | 2339.152 | 37769.4082 | 15 | 63.15%
[5 empty] | 15.02 | 1144000 | 660 | 100% | 100% | 49.73% | 0.62321 | 54600 | 243540 | 400015.897 | 698155.897 | 2353.5648 | 38002.1268 | 15.02 | 63.32%
[5 empty] | 15.04 | 1144000 | 660 | 100% | 100% | 49.97% | 0.62502 | 54600 | 243540 | 401958.937 | 700098.937 | 2368.0178 | 38235.4931 | 15.04 | 63.5%
[5 empty] | 15.06 | 1144000 | 660 | 100% | 100% | 50.21% | 0.62683 | 54600 | 243540 | 403901.977 | 702041.977 | 2382.5108 | 38469.5071 | 15.06 | 63.67%
[5 empty] | 15.08 | 1144000 | 660 | 100% | 100% | 50.45% | 0.62864 | 54600 | 243540 | 405845.017 | 703985.017 | 2397.044 | 38704.1688 | 15.08 | 63.85%
[5 empty] | 15.1 | 1144000 | 660 | 100% | 100% | 50.69% | 0.63045 | 54600 | 243540 | 407788.057 | 705928.057 | 2411.6173 | 38939.4781 | 15.1 | 64.03%
[5 empty] | 15.12 | 1144000 | 660 | 100% | 100% | 50.94% | 0.63226 | 54600 | 243540 | 409731.097 | 707871.097 | 2426.2307 | 39175.4351 | 15.12 | 64.2%
[5 empty] | 15.14 | 1144000 | 660 | 100% | 100% | 51.18% | 0.63407 | 54600 | 243540 | 411674.137 | 709814.137 | 2440.8842 | 39412.0399 | 15.14 | 64.38%
[5 empty] | 15.16 | 1144000 | 660 | 100% | 100% | 51.42% | 0.63588 | 54600 | 243540 | 413617.177 | 711757.177 | 2455.5778 | 39649.2923 | 15.16 | 64.56%
[5 empty] | 15.18 | 1144000 | 660 | 100% | 100% | 51.66% | 0.63769 | 54600 | 243540 | 415560.217 | 713700.217 | 2470.3115 | 39887.1923 | 15.18 | 64.73%
[5 empty] | 15.2 | 1144000 | 660 | 100% | 100% | 51.9% | 0.6395 | 54600 | 243540 | 417503.257 | 715643.257 | 2485.0854 | 40125.7401 | 15.2 | 64.91%
[5 empty] | 15.22 | 1144000 | 660 | 100% | 100% | 52.14% | 0.64131 | 54600 | 243540 | 419446.297 | 717586.297 | 2499.8994 | 40364.9355 | 15.22 | 65.08%
[5 empty] | 15.24 | 1144000 | 660 | 100% | 100% | 52.38% | 0.64312 | 54600 | 243540 | 421389.337 | 719529.337 | 2514.7534 | 40604.7786 | 15.24 | 65.26%
[5 empty] | 15.26 | 1144000 | 660 | 100% | 100% | 52.63% | 0.64493 | 54600 | 243540 | 423332.377 | 721472.377 | 2529.6476 | 40845.2694 | 15.26 | 65.44%
[5 empty] | 15.28 | 1144000 | 660 | 100% | 100% | 52.87% | 0.64674 | 54600 | 243540 | 425275.417 | 723415.417 | 2544.5819 | 41086.4079 | 15.28 | 65.61%
[5 empty] | 15.3 | 1144000 | 660 | 100% | 100% | 53.11% | 0.64855 | 54600 | 243540 | 427218.457 | 725358.457 | 2559.5563 | 41328.194 | 15.3 | 65.79%
[5 empty] | 15.32 | 1144000 | 660 | 100% | 100% | 53.35% | 0.65036 | 54600 | 243540 | 429161.497 | 727301.497 | 2574.5708 | 41570.6279 | 15.32 | 65.96%
[5 empty] | 15.34 | 1144000 | 660 | 100% | 100% | 53.59% | 0.65217 | 54600 | 243540 | 431104.537 | 729244.537 | 2589.6255 | 41813.7094 | 15.34 | 66.14%
[5 empty] | 15.36 | 1144000 | 660 | 100% | 100% | 53.83% | 0.65398 | 54600 | 243540 | 433047.577 | 731187.577 | 2604.7202 | 42057.4386 | 15.36 | 66.32%
[5 empty] | 15.38 | 1144000 | 660 | 100% | 100% | 54.08% | 0.65579 | 54600 | 243540 | 434990.617 | 733130.617 | 2619.8551 | 42301.8154 | 15.38 | 66.49%
[5 empty] | 15.4 | 1144000 | 660 | 100% | 100% | 54.32% | 0.6576 | 54600 | 243540 | 436933.657 | 735073.657 | 2635.03 | 42546.84 | 15.4 | 66.67%
[5 empty] | 15.42 | 1144000 | 660 | 100% | 100% | 54.56% | 0.65941 | 54600 | 243540 | 438876.697 | 737016.697 | 2650.2451 | 42792.5122 | 15.42 | 66.85%
[5 empty] | 15.44 | 1144000 | 660 | 100% | 100% | 54.8% | 0.66122 | 54600 | 243540 | 440819.737 | 738959.737 | 2665.5003 | 43038.8321 | 15.44 | 67.02%
[5 empty] | 15.46 | 1144000 | 660 | 100% | 100% | 55.04% | 0.66303 | 54600 | 243540 | 442762.777 | 740902.777 | 2680.7956 | 43285.7997 | 15.46 | 67.2%
[5 empty] | 15.48 | 1144000 | 660 | 100% | 100% | 55.28% | 0.66484 | 54600 | 243540 | 444705.817 | 742845.817 | 2696.1311 | 43533.415 | 15.48 | 67.37%
[5 empty] | 15.5 | 1144000 | 660 | 100% | 100% | 55.52% | 0.66665 | 54600 | 243540 | 446648.857 | 744788.857 | 2711.5066 | 43781.678 | 15.5 | 67.55%
[5 empty] | 15.52 | 1144000 | 660 | 100% | 100% | 55.77% | 0.66846 | 54600 | 243540 | 448591.897 | 746731.897 | 2726.9222 | 44030.5886 | 15.52 | 67.73%
[5 empty] | 15.54 | 1144000 | 660 | 100% | 100% | 56.01% | 0.67028 | 54600 | 243540 | 450534.937 | 748674.937 | 2742.378 | 44280.1469 | 15.54 | 67.9%
[5 empty] | 15.56 | 1144000 | 660 | 100% | 100% | 56.25% | 0.67209 | 54600 | 243540 | 452477.977 | 750617.977 | 2757.8739 | 44530.3529 | 15.56 | 68.08%
[5 empty] | 15.58 | 1144000 | 660 | 100% | 100% | 56.49% | 0.6739 | 54600 | 243540 | 454421.017 | 752561.017 | 2773.4098 | 44781.2066 | 15.58 | 68.26%
[5 empty] | 15.6 | 1144000 | 660 | 100% | 100% | 56.73% | 0.67571 | 54600 | 243540 | 456364.057 | 754504.057 | 2788.9859 | 45032.7079 | 15.6 | 68.43%
[5 empty] | 15.62 | 1144000 | 660 | 100% | 100% | 56.97% | 0.67752 | 54600 | 243540 | 458307.097 | 756447.097 | 2804.6021 | 45284.857 | 15.62 | 68.61%
[5 empty] | 15.64 | 1144000 | 660 | 100% | 100% | 57.22% | 0.67933 | 54600 | 243540 | 460250.137 | 758390.137 | 2820.2585 | 45537.6537 | 15.64 | 68.78%
[5 empty] | 15.66 | 1144000 | 660 | 100% | 100% | 57.46% | 0.68114 | 54600 | 243540 | 462193.177 | 760333.177 | 2835.9549 | 45791.0981 | 15.66 | 68.96%
[5 empty] | 15.68 | 1144000 | 660 | 100% | 100% | 57.7% | 0.68295 | 54600 | 243540 | 464136.217 | 762276.217 | 2851.6914 | 46045.1901 | 15.68 | 69.14%
[5 empty] | 15.7 | 1144000 | 660 | 100% | 100% | 57.94% | 0.68476 | 54600 | 243540 | 466079.257 | 764219.257 | 2867.4681 | 46299.9299 | 15.7 | 69.31%
[5 empty] | 15.72 | 1144000 | 660 | 100% | 100% | 58.18% | 0.68657 | 54600 | 243540 | 468022.297 | 766162.297 | 2883.2849 | 46555.3173 | 15.72 | 69.49%
[5 empty] | 15.74 | 1144000 | 660 | 100% | 100% | 58.42% | 0.68838 | 54600 | 243540 | 469965.337 | 768105.337 | 2899.1417 | 46811.3524 | 15.74 | 69.67%
[5 empty] | 15.76 | 1144000 | 660 | 100% | 100% | 58.66% | 0.69019 | 54600 | 243540 | 471908.377 | 770048.377 | 2915.0387 | 47068.0352 | 15.76 | 69.84%
[5 empty] | 15.78 | 1144000 | 660 | 100% | 100% | 58.91% | 0.692 | 54600 | 243540 | 473851.417 | 771991.417 | 2930.9758 | 47325.3657 | 15.78 | 70.02%
[5 empty] | 15.8 | 1144000 | 660 | 100% | 100% | 59.15% | 0.69381 | 54600 | 243540 | 475794.457 | 773934.457 | 2946.9531 | 47583.3438 | 15.8 | 70.19%
[5 empty] | 15.82 | 1144000 | 660 | 100% | 100% | 59.39% | 0.69562 | 54600 | 243540 | 477737.497 | 775877.497 | 2962.9704 | 47841.9697 | 15.82 | 70.37%
[5 empty] | 15.84 | 1144000 | 660 | 100% | 100% | 59.63% | 0.69743 | 54600 | 243540 | 479680.537 | 777820.537 | 2979.0278 | 48101.2432 | 15.84 | 70.55%
[5 empty] | 15.86 | 1144000 | 660 | 100% | 100% | 59.87% | 0.69924 | 54600 | 243540 | 481623.577 | 779763.577 | 2995.1254 | 48361.1644 | 15.86 | 70.72%
[5 empty] | 15.88 | 1144000 | 660 | 100% | 100% | 60.11% | 0.70105 | 54600 | 243540 | 483566.617 | 781706.617 | 3011.2631 | 48621.7333 | 15.88 | 70.9%
[5 empty] | 15.9 | 1144000 | 660 | 100% | 100% | 60.36% | 0.70286 | 54600 | 243540 | 485509.657 | 783649.657 | 3027.4408 | 48882.9498 | 15.9 | 71.08%
[5 empty] | 15.92 | 1144000 | 660 | 100% | 100% | 60.6% | 0.70467 | 54600 | 243540 | 487452.697 | 785592.697 | 3043.6587 | 49144.814 | 15.92 | 71.25%
[5 empty] | 15.94 | 1144000 | 660 | 100% | 100% | 60.84% | 0.70648 | 54600 | 243540 | 489395.737 | 787535.737 | 3059.9167 | 49407.326 | 15.94 | 71.43%
[5 empty] | 15.96 | 1144000 | 660 | 100% | 100% | 61.08% | 0.70829 | 54600 | 243540 | 491338.777 | 789478.777 | 3076.2149 | 49670.4855 | 15.96 | 71.6%
[5 empty] | 15.98 | 1144000 | 660 | 100% | 100% | 61.32% | 0.7101 | 54600 | 243540 | 493281.817 | 791421.817 | 3092.5531 | 49934.2928 | 15.98 | 71.78%
[5 empty] | 16 | 1144000 | 660 | 100% | 100% | 61.56% | 0.71191 | 54600 | 243540 | 495224.857 | 793364.857 | 3108.9314 | 50198.7478 | 16 | 71.96%
[5 empty] | 16.02 | 1144000 | 660 | 100% | 100% | 61.8% | 0.71372 | 54600 | 243540 | 497167.897 | 795307.897 | 3125.3499 | 50463.8504 | 16.02 | 72.13%
[5 empty] | 16.04 | 1144000 | 660 | 100% | 100% | 62.05% | 0.71554 | 54600 | 243540 | 499110.937 | 797250.937 | 3141.8085 | 50729.6007 | 16.04 | 72.31%
[5 empty] | 16.06 | 1144000 | 660 | 100% | 100% | 62.29% | 0.71735 | 54600 | 243540 | 501053.977 | 799193.977 | 3158.3071 | 50995.9987 | 16.06 | 72.49%
[5 empty] | 16.08 | 1144000 | 660 | 100% | 100% | 62.53% | 0.71916 | 54600 | 243540 | 502997.017 | 801137.017 | 3174.8459 | 51263.0444 | 16.08 | 72.66%
[5 empty] | 16.1 | 1144000 | 660 | 100% | 100% | 62.77% | 0.72097 | 54600 | 243540 | 504940.057 | 803080.057 | 3191.4248 | 51530.7377 | 16.1 | 72.84%
[5 empty] | 16.12 | 1144000 | 660 | 100% | 100% | 63.01% | 0.72278 | 54600 | 243540 | 506883.097 | 805023.097 | 3208.0439 | 51799.0788 | 16.12 | 73.01%
[5 empty] | 16.14 | 1144000 | 660 | 100% | 100% | 63.25% | 0.72459 | 54600 | 243540 | 508826.137 | 806966.137 | 3224.703 | 52068.0675 | 16.14 | 73.19%
[5 empty] | 16.16 | 1144000 | 660 | 100% | 100% | 63.5% | 0.7264 | 54600 | 243540 | 510769.177 | 808909.177 | 3241.4022 | 52337.7039 | 16.16 | 73.37%
[5 empty] | 16.18 | 1144000 | 660 | 100% | 100% | 63.74% | 0.72821 | 54600 | 243540 | 512712.217 | 810852.217 | 3258.1416 | 52607.9879 | 16.18 | 73.54%
[5 empty] | 16.2 | 1144000 | 660 | 100% | 100% | 63.98% | 0.73002 | 54600 | 243540 | 514655.257 | 812795.257 | 3274.9211 | 52878.9197 | 16.2 | 73.72%
[5 empty] | 16.22 | 1144000 | 660 | 100% | 100% | 64.22% | 0.73183 | 54600 | 243540 | 516598.297 | 814738.297 | 3291.7406 | 53150.4991 | 16.22 | 73.9%
[5 empty] | 16.24 | 1144000 | 660 | 100% | 100% | 64.46% | 0.73364 | 54600 | 243540 | 518541.337 | 816681.337 | 3308.6003 | 53422.7262 | 16.24 | 74.07%
[5 empty] | 16.26 | 1144000 | 660 | 100% | 100% | 64.7% | 0.73545 | 54600 | 243540 | 520484.377 | 818624.377 | 3325.5001 | 53695.601 | 16.26 | 74.25%
[5 empty] | 16.28 | 1144000 | 660 | 100% | 100% | 64.94% | 0.73726 | 54600 | 243540 | 522427.417 | 820567.417 | 3342.44 | 53969.1235 | 16.28 | 74.42%
[5 empty] | 16.3 | 1144000 | 660 | 100% | 100% | 65.19% | 0.73907 | 54600 | 243540 | 524370.457 | 822510.457 | 3359.4201 | 54243.2937 | 16.3 | 74.6%
[5 empty] | 16.32 | 1144000 | 660 | 100% | 100% | 65.43% | 0.74088 | 54600 | 243540 | 526313.497 | 824453.497 | 3376.4402 | 54518.1115 | 16.32 | 74.78%
[5 empty] | 16.34 | 1144000 | 660 | 100% | 100% | 65.67% | 0.74269 | 54600 | 243540 | 528256.537 | 826396.537 | 3393.5005 | 54793.577 | 16.34 | 74.95%
[5 empty] | 16.36 | 1144000 | 660 | 100% | 100% | 65.91% | 0.7445 | 54600 | 243540 | 530199.577 | 828339.577 | 3410.6008 | 55069.6902 | 16.36 | 75.13%
[5 empty] | 16.38 | 1144000 | 660 | 100% | 100% | 66.15% | 0.74631 | 54600 | 243540 | 532142.617 | 830282.617 | 3427.7413 | 55346.4511 | 16.38 | 75.31%
[5 empty] | 16.4 | 1144000 | 660 | 100% | 100% | 66.39% | 0.74812 | 54600 | 243540 | 534085.657 | 832225.657 | 3444.9219 | 55623.8596 | 16.4 | 75.48%
[5 empty] | 16.42 | 1144000 | 660 | 100% | 100% | 66.64% | 0.74993 | 54600 | 243540 | 536028.697 | 834168.697 | 3462.1426 | 55901.9158 | 16.42 | 75.66%
[5 empty] | 16.44 | 1144000 | 660 | 100% | 100% | 66.88% | 0.75174 | 54600 | 243540 | 537971.737 | 836111.737 | 3479.4034 | 56180.6198 | 16.44 | 75.83%
[5 empty] | 16.46 | 1144000 | 660 | 100% | 100% | 67.12% | 0.75355 | 54600 | 243540 | 539914.777 | 838054.777 | 3496.7044 | 56459.9714 | 16.46 | 76.01%
[5 empty] | 16.48 | 1144000 | 660 | 100% | 100% | 67.36% | 0.75536 | 54600 | 243540 | 541857.817 | 839997.817 | 3514.0454 | 56739.9706 | 16.48 | 76.19%
[5 empty] | 16.5 | 1144000 | 660 | 100% | 100% | 67.6% | 0.75717 | 54600 | 243540 | 543800.857 | 841940.857 | 3531.4266 | 57020.6176 | 16.5 | 76.36%
[5 empty] | 16.52 | 1144000 | 660 | 100% | 100% | 67.84% | 0.75898 | 54600 | 243540 | 545743.897 | 843883.897 | 3548.8478 | 57301.9122 | 16.52 | 76.54%
[5 empty] | 16.54 | 1144000 | 660 | 100% | 100% | 68.08% | 0.76079 | 54600 | 243540 | 547686.937 | 845826.937 | 3566.3092 | 57583.8545 | 16.54 | 76.71%
[5 empty] | 16.56 | 1144000 | 660 | 100% | 100% | 68.33% | 0.76261 | 54600 | 243540 | 549629.977 | 847769.977 | 3583.8107 | 57866.4445 | 16.56 | 76.89%
[5 empty] | 16.58 | 1144000 | 660 | 100% | 100% | 68.57% | 0.76442 | 54600 | 243540 | 551573.017 | 849713.017 | 3601.3523 | 58149.6822 | 16.58 | 77.07%
[5 empty] | 16.6 | 1144000 | 660 | 100% | 100% | 68.81% | 0.76623 | 54600 | 243540 | 553516.057 | 851656.057 | 3618.934 | 58433.5675 | 16.6 | 77.24%
[5 empty] | 16.62 | 1144000 | 660 | 100% | 100% | 69.05% | 0.76804 | 54600 | 243540 | 555459.097 | 853599.097 | 3636.5558 | 58718.1006 | 16.62 | 77.42%
[5 empty] | 16.64 | 1144000 | 660 | 100% | 100% | 69.29% | 0.76985 | 54600 | 243540 | 557402.137 | 855542.137 | 3654.2178 | 59003.2813 | 16.64 | 77.6%
[5 empty] | 16.66 | 1144000 | 660 | 100% | 100% | 69.53% | 0.77166 | 54600 | 243540 | 559345.177 | 857485.177 | 3671.9198 | 59289.1097 | 16.66 | 77.77%
[5 empty] | 16.68 | 1144000 | 660 | 100% | 100% | 69.78% | 0.77347 | 54600 | 243540 | 561288.217 | 859428.217 | 3689.662 | 59575.5857 | 16.68 | 77.95%
[5 empty] | 16.7 | 1144000 | 660 | 100% | 100% | 70.02% | 0.77528 | 54600 | 243540 | 563231.257 | 861371.257 | 3707.4443 | 59862.7095 | 16.7 | 78.12%
[5 empty] | 16.72 | 1144000 | 660 | 100% | 100% | 70.26% | 0.77709 | 54600 | 243540 | 565174.297 | 863314.297 | 3725.2667 | 60150.4809 | 16.72 | 78.3%
[5 empty] | 16.74 | 1144000 | 660 | 100% | 100% | 70.5% | 0.7789 | 54600 | 243540 | 567117.337 | 865257.337 | 3743.1292 | 60438.9 | 16.74 | 78.48%
[5 empty] | 16.76 | 1144000 | 660 | 100% | 100% | 70.74% | 0.78071 | 54600 | 243540 | 569060.377 | 867200.377 | 3761.0318 | 60727.9668 | 16.76 | 78.65%
[5 empty] | 16.78 | 1144000 | 660 | 100% | 100% | 70.98% | 0.78252 | 54600 | 243540 | 571003.417 | 869143.417 | 3778.9745 | 61017.6813 | 16.78 | 78.83%
[5 empty] | 16.8 | 1144000 | 660 | 100% | 100% | 71.22% | 0.78433 | 54600 | 243540 | 572946.457 | 871086.457 | 3796.9573 | 61308.0435 | 16.8 | 79.01%
[5 empty] | 16.82 | 1144000 | 660 | 100% | 100% | 71.47% | 0.78614 | 54600 | 243540 | 574889.497 | 873029.497 | 3814.9803 | 61599.0533 | 16.82 | 79.18%
[5 empty] | 16.84 | 1144000 | 660 | 100% | 100% | 71.71% | 0.78795 | 54600 | 243540 | 576832.537 | 874972.537 | 3833.0434 | 61890.7108 | 16.84 | 79.36%
[5 empty] | 16.86 | 1144000 | 660 | 100% | 100% | 71.95% | 0.78976 | 54600 | 243540 | 578775.577 | 876915.577 | 3851.1465 | 62183.016 | 16.86 | 79.53%
[5 empty] | 16.88 | 1144000 | 660 | 100% | 100% | 72.19% | 0.79157 | 54600 | 243540 | 580718.617 | 878858.617 | 3869.2898 | 62475.9689 | 16.88 | 79.71%
[5 empty] | 16.9 | 1144000 | 660 | 100% | 100% | 72.43% | 0.79338 | 54600 | 243540 | 582661.657 | 880801.657 | 3887.4732 | 62769.5694 | 16.9 | 79.89%
[5 empty] | 16.92 | 1144000 | 660 | 100% | 100% | 72.67% | 0.79519 | 54600 | 243540 | 584604.697 | 882744.697 | 3905.6967 | 63063.8177 | 16.92 | 80.06%
[5 empty] | 16.94 | 1144000 | 660 | 100% | 100% | 72.92% | 0.797 | 54600 | 243540 | 586547.737 | 884687.737 | 3923.9604 | 63358.7136 | 16.94 | 80.24%
[5 empty] | 16.96 | 1144000 | 660 | 100% | 100% | 73.16% | 0.79881 | 54600 | 243540 | 588490.777 | 886630.777 | 3942.2641 | 63654.2572 | 16.96 | 80.42%
[5 empty] | 16.98 | 1144000 | 660 | 100% | 100% | 73.4% | 0.80062 | 54600 | 243540 | 590433.817 | 888573.817 | 3960.608 | 63950.4484 | 16.98 | 80.59%
[5 empty] | 17 | 1144000 | 660 | 100% | 100% | 73.64% | 0.80243 | 54600 | 243540 | 592376.857 | 890516.857 | 3978.9919 | 64247.2874 | 17 | 80.77%
[5 empty] | 17.02 | 1144000 | 660 | 100% | 100% | 73.88% | 0.80424 | 54600 | 243540 | 594319.897 | 892459.897 | 3997.416 | 64544.774 | 17.02 | 80.94%
[5 empty] | 17.04 | 1144000 | 660 | 100% | 100% | 74.12% | 0.80605 | 54600 | 243540 | 596262.937 | 894402.937 | 4015.8802 | 64842.9083 | 17.04 | 81.12%
[5 empty] | 17.06 | 1144000 | 660 | 100% | 100% | 74.37% | 0.80787 | 54600 | 243540 | 598205.977 | 896345.977 | 4034.3845 | 65141.6903 | 17.06 | 81.3%
[5 empty] | 17.08 | 1144000 | 660 | 100% | 100% | 74.61% | 0.80968 | 54600 | 243540 | 600149.017 | 898289.017 | 4052.9289 | 65441.12 | 17.08 | 81.47%
[5 empty] | 17.1 | 1144000 | 660 | 100% | 100% | 74.85% | 0.81149 | 54600 | 243540 | 602092.057 | 900232.057 | 4071.5134 | 65741.1973 | 17.1 | 81.65%
[5 empty] | 17.12 | 1144000 | 660 | 100% | 100% | 75.09% | 0.8133 | 54600 | 243540 | 604035.097 | 902175.097 | 4090.1381 | 66041.9224 | 17.12 | 81.83%
[5 empty] | 17.14 | 1144000 | 660 | 100% | 100% | 75.33% | 0.81511 | 54600 | 243540 | 605978.137 | 904118.137 | 4108.8028 | 66343.2951 | 17.14 | 82%
[5 empty] | 17.16 | 1144000 | 660 | 100% | 100% | 75.57% | 0.81692 | 54600 | 243540 | 607921.177 | 906061.177 | 4127.5077 | 66645.3155 | 17.16 | 82.18%
[5 empty] | 17.18 | 1144000 | 660 | 100% | 100% | 75.81% | 0.81873 | 54600 | 243540 | 609864.217 | 908004.217 | 4146.2526 | 66947.9836 | 17.18 | 82.35%
[5 empty] | 17.2 | 1144000 | 660 | 100% | 100% | 76.06% | 0.82054 | 54600 | 243540 | 611807.257 | 909947.257 | 4165.0377 | 67251.2993 | 17.2 | 82.53%
[5 empty] | 17.22 | 1144000 | 660 | 100% | 100% | 76.3% | 0.82235 | 54600 | 243540 | 613750.297 | 911890.297 | 4183.8629 | 67555.2627 | 17.22 | 82.71%
[5 empty] | 17.24 | 1144000 | 660 | 100% | 100% | 76.54% | 0.82416 | 54600 | 243540 | 615693.337 | 913833.337 | 4202.7282 | 67859.8739 | 17.24 | 82.88%
[5 empty] | 17.26 | 1144000 | 660 | 100% | 100% | 76.78% | 0.82597 | 54600 | 243540 | 617636.377 | 915776.377 | 4221.6337 | 68165.1326 | 17.26 | 83.06%
[5 empty] | 17.28 | 1144000 | 660 | 100% | 100% | 77.02% | 0.82778 | 54600 | 243540 | 619579.417 | 917719.417 | 4240.5792 | 68471.0391 | 17.28 | 83.24%
[5 empty] | 17.3 | 1144000 | 660 | 100% | 100% | 77.26% | 0.82959 | 54600 | 243540 | 621522.457 | 919662.457 | 4259.5649 | 68777.5933 | 17.3 | 83.41%
[5 empty] | 17.32 | 1144000 | 660 | 100% | 100% | 77.51% | 0.8314 | 54600 | 243540 | 623465.497 | 921605.497 | 4278.5906 | 69084.7951 | 17.32 | 83.59%
[5 empty] | 17.34 | 1144000 | 660 | 100% | 100% | 77.75% | 0.83321 | 54600 | 243540 | 625408.537 | 923548.537 | 4297.6565 | 69392.6446 | 17.34 | 83.76%
[5 empty] | 17.36 | 1144000 | 660 | 100% | 100% | 77.99% | 0.83502 | 54600 | 243540 | 627351.577 | 925491.577 | 4316.7625 | 69701.1418 | 17.36 | 83.94%
[5 empty] | 17.38 | 1144000 | 660 | 100% | 100% | 78.23% | 0.83683 | 54600 | 243540 | 629294.617 | 927434.617 | 4335.9086 | 70010.2867 | 17.38 | 84.12%
[5 empty] | 17.4 | 1144000 | 660 | 100% | 100% | 78.47% | 0.83864 | 54600 | 243540 | 631237.657 | 929377.657 | 4355.0948 | 70320.0792 | 17.4 | 84.29%
[5 empty] | 17.42 | 1144000 | 660 | 100% | 100% | 78.71% | 0.84045 | 54600 | 243540 | 633180.697 | 931320.697 | 4374.3211 | 70630.5195 | 17.42 | 84.47%
[5 empty] | 17.44 | 1144000 | 660 | 100% | 100% | 78.95% | 0.84226 | 54600 | 243540 | 635123.737 | 933263.737 | 4393.5876 | 70941.6074 | 17.44 | 84.65%
[5 empty] | 17.46 | 1144000 | 660 | 100% | 100% | 79.2% | 0.84407 | 54600 | 243540 | 637066.777 | 935206.777 | 4412.8941 | 71253.343 | 17.46 | 84.82%
[5 empty] | 17.48 | 1144000 | 660 | 100% | 100% | 79.44% | 0.84588 | 54600 | 243540 | 639009.817 | 937149.817 | 4432.2408 | 71565.7262 | 17.48 | 85%
[5 empty] | 17.5 | 1144000 | 660 | 100% | 100% | 79.68% | 0.84769 | 54600 | 243540 | 640952.857 | 939092.857 | 4451.6275 | 71878.7572 | 17.5 | 85.17%
[5 empty] | 17.52 | 1144000 | 660 | 100% | 100% | 79.92% | 0.8495 | 54600 | 243540 | 642895.897 | 941035.897 | 4471.0544 | 72192.4358 | 17.52 | 85.35%
[5 empty] | 17.54 | 1144000 | 660 | 100% | 100% | 80.16% | 0.85131 | 54600 | 243540 | 644838.937 | 942978.937 | 4490.5214 | 72506.7621 | 17.54 | 85.53%
[5 empty] | 17.56 | 1144000 | 660 | 100% | 100% | 80.4% | 0.85312 | 54600 | 243540 | 646781.977 | 944921.977 | 4510.0285 | 72821.7361 | 17.56 | 85.7%
[5 empty] | 17.58 | 1144000 | 660 | 100% | 100% | 80.65% | 0.85494 | 54600 | 243540 | 648725.017 | 946865.017 | 4529.5758 | 73137.3578 | 17.58 | 85.88%
[5 empty] | 17.6 | 1144000 | 660 | 100% | 100% | 80.89% | 0.85675 | 54600 | 243540 | 650668.057 | 948808.057 | 4549.1631 | 73453.6272 | 17.6 | 86.06%
[5 empty] | 17.62 | 1144000 | 660 | 100% | 100% | 81.13% | 0.85856 | 54600 | 243540 | 652611.097 | 950751.097 | 4568.7905 | 73770.5442 | 17.62 | 86.23%
[5 empty] | 17.64 | 1144000 | 660 | 100% | 100% | 81.37% | 0.86037 | 54600 | 243540 | 654554.137 | 952694.137 | 4588.4581 | 74088.1089 | 17.64 | 86.41%
[5 empty] | 17.66 | 1144000 | 660 | 100% | 100% | 81.61% | 0.86218 | 54600 | 243540 | 656497.177 | 954637.177 | 4608.1658 | 74406.3213 | 17.66 | 86.58%
[5 empty] | 17.68 | 1144000 | 660 | 100% | 100% | 81.85% | 0.86399 | 54600 | 243540 | 658440.217 | 956580.217 | 4627.9136 | 74725.1814 | 17.68 | 86.76%
[5 empty] | 17.7 | 1144000 | 660 | 100% | 100% | 82.09% | 0.8658 | 54600 | 243540 | 660383.257 | 958523.257 | 4647.7015 | 75044.6891 | 17.7 | 86.94%
[5 empty] | 17.72 | 1144000 | 660 | 100% | 100% | 82.34% | 0.86761 | 54600 | 243540 | 662326.297 | 960466.297 | 4667.5295 | 75364.8445 | 17.72 | 87.11%
[5 empty] | 17.74 | 1144000 | 660 | 100% | 100% | 82.58% | 0.86942 | 54600 | 243540 | 664269.337 | 962409.337 | 4687.3976 | 75685.6477 | 17.74 | 87.29%
[5 empty] | 17.76 | 1144000 | 660 | 100% | 100% | 82.82% | 0.87123 | 54600 | 243540 | 666212.377 | 964352.377 | 4707.3058 | 76007.0985 | 17.76 | 87.46%
[5 empty] | 17.78 | 1144000 | 660 | 100% | 100% | 83.06% | 0.87304 | 54600 | 243540 | 668155.417 | 966295.417 | 4727.2542 | 76329.1969 | 17.78 | 87.64%
[5 empty] | 17.8 | 1144000 | 660 | 100% | 100% | 83.3% | 0.87485 | 54600 | 243540 | 670098.457 | 968238.457 | 4747.2426 | 76651.9431 | 17.8 | 87.82%
[5 empty] | 17.82 | 1144000 | 660 | 100% | 100% | 83.54% | 0.87666 | 54600 | 243540 | 672041.497 | 970181.497 | 4767.2712 | 76975.3369 | 17.82 | 87.99%
[5 empty] | 17.84 | 1144000 | 660 | 100% | 100% | 83.79% | 0.87847 | 54600 | 243540 | 673984.537 | 972124.537 | 4787.3399 | 77299.3784 | 17.84 | 88.17%
[5 empty] | 17.86 | 1144000 | 660 | 100% | 100% | 84.03% | 0.88028 | 54600 | 243540 | 675927.577 | 974067.577 | 4807.4487 | 77624.0676 | 17.86 | 88.35%
[5 empty] | 17.88 | 1144000 | 660 | 100% | 100% | 84.27% | 0.88209 | 54600 | 243540 | 677870.617 | 976010.617 | 4827.5976 | 77949.4045 | 17.88 | 88.52%
[5 empty] | 17.9 | 1144000 | 660 | 100% | 100% | 84.51% | 0.8839 | 54600 | 243540 | 679813.657 | 977953.657 | 4847.7866 | 78275.389 | 17.9 | 88.7%
[5 empty] | 17.92 | 1144000 | 660 | 100% | 100% | 84.75% | 0.88571 | 54600 | 243540 | 681756.697 | 979896.697 | 4868.0158 | 78602.0213 | 17.92 | 88.87%
[5 empty] | 17.94 | 1144000 | 660 | 100% | 100% | 84.99% | 0.88752 | 54600 | 243540 | 683699.737 | 981839.737 | 4888.285 | 78929.3012 | 17.94 | 89.05%
[5 empty] | 17.96 | 1144000 | 660 | 100% | 100% | 85.23% | 0.88933 | 54600 | 243540 | 685642.777 | 983782.777 | 4908.5944 | 79257.2288 | 17.96 | 89.23%
[5 empty] | 17.98 | 1144000 | 660 | 100% | 100% | 85.48% | 0.89114 | 54600 | 243540 | 687585.817 | 985725.817 | 4928.9438 | 79585.804 | 17.98 | 89.4%
[5 empty] | 18 | 1144000 | 660 | 100% | 100% | 85.72% | 0.89295 | 54600 | 243540 | 689528.857 | 987668.857 | 4949.3334 | 79915.027 | 18 | 89.58%
[5 empty] | 18.02 | 1144000 | 660 | 100% | 100% | 85.96% | 0.89476 | 54600 | 243540 | 691471.897 | 989611.897 | 4969.7631 | 80244.8976 | 18.02 | 89.76%
[5 empty] | 18.04 | 1144000 | 660 | 100% | 100% | 86.2% | 0.89657 | 54600 | 243540 | 693414.937 | 991554.937 | 4990.2329 | 80575.4159 | 18.04 | 89.93%
[5 empty] | 18.06 | 1144000 | 660 | 100% | 100% | 86.44% | 0.89838 | 54600 | 243540 | 695357.977 | 993497.977 | 5010.7428 | 80906.5819 | 18.06 | 90.11%
[5 empty] | 18.08 | 1144000 | 660 | 100% | 100% | 86.68% | 0.9002 | 54600 | 243540 | 697301.017 | 995441.017 | 5031.2929 | 81238.3956 | 18.08 | 90.28%
[5 empty] | 18.1 | 1144000 | 660 | 100% | 100% | 86.93% | 0.90201 | 54600 | 243540 | 699244.057 | 997384.057 | 5051.883 | 81570.857 | 18.1 | 90.46%
[5 empty] | 18.12 | 1144000 | 660 | 100% | 100% | 87.17% | 0.90382 | 54600 | 243540 | 701187.097 | 999327.097 | 5072.5133 | 81903.966 | 18.12 | 90.64%
[5 empty] | 18.14 | 1144000 | 660 | 100% | 100% | 87.41% | 0.90563 | 54600 | 243540 | 703130.137 | 1001270.137 | 5093.1837 | 82237.7227 | 18.14 | 90.81%
[5 empty] | 18.16 | 1144000 | 660 | 100% | 100% | 87.65% | 0.90744 | 54600 | 243540 | 705073.177 | 1003213.177 | 5113.8941 | 82572.1271 | 18.16 | 90.99%
[5 empty] | 18.18 | 1144000 | 660 | 100% | 100% | 87.89% | 0.90925 | 54600 | 243540 | 707016.217 | 1005156.217 | 5134.6447 | 82907.1792 | 18.18 | 91.17%
[5 empty] | 18.2 | 1144000 | 660 | 100% | 100% | 88.13% | 0.91106 | 54600 | 243540 | 708959.257 | 1007099.257 | 5155.4354 | 83242.8789 | 18.2 | 91.34%
[5 empty] | 18.22 | 1144000 | 660 | 100% | 100% | 88.37% | 0.91287 | 54600 | 243540 | 710902.297 | 1009042.297 | 5176.2663 | 83579.2264 | 18.22 | 91.52%
[5 empty] | 18.24 | 1144000 | 660 | 100% | 100% | 88.62% | 0.91468 | 54600 | 243540 | 712845.337 | 1010985.337 | 5197.1372 | 83916.2215 | 18.24 | 91.69%
[5 empty] | 18.26 | 1144000 | 660 | 100% | 100% | 88.86% | 0.91649 | 54600 | 243540 | 714788.377 | 1012928.377 | 5218.0482 | 84253.8643 | 18.26 | 91.87%
[5 empty] | 18.28 | 1144000 | 660 | 100% | 100% | 89.1% | 0.9183 | 54600 | 243540 | 716731.417 | 1014871.417 | 5238.9994 | 84592.1547 | 18.28 | 92.05%
[5 empty] | 18.3 | 1144000 | 660 | 100% | 100% | 89.34% | 0.92011 | 54600 | 243540 | 718674.457 | 1016814.457 | 5259.9907 | 84931.0929 | 18.3 | 92.22%
[5 empty] | 18.32 | 1144000 | 660 | 100% | 100% | 89.58% | 0.92192 | 54600 | 243540 | 720617.497 | 1018757.497 | 5281.0221 | 85270.6787 | 18.32 | 92.4%
[5 empty] | 18.34 | 1144000 | 660 | 100% | 100% | 89.82% | 0.92373 | 54600 | 243540 | 722560.537 | 1020700.537 | 5302.0935 | 85610.9122 | 18.34 | 92.58%
[5 empty] | 18.36 | 1144000 | 660 | 100% | 100% | 90.07% | 0.92554 | 54600 | 243540 | 724503.577 | 1022643.577 | 5323.2052 | 85951.7934 | 18.36 | 92.75%
[5 empty] | 18.38 | 1144000 | 660 | 100% | 100% | 90.31% | 0.92735 | 54600 | 243540 | 726446.617 | 1024586.617 | 5344.3569 | 86293.3223 | 18.38 | 92.93%
[5 empty] | 18.4 | 1144000 | 660 | 100% | 100% | 90.55% | 0.92916 | 54600 | 243540 | 728389.657 | 1026529.657 | 5365.5487 | 86635.4988 | 18.4 | 93.1%
[5 empty] | 18.42 | 1144000 | 660 | 100% | 100% | 90.79% | 0.93097 | 54600 | 243540 | 730332.697 | 1028472.697 | 5386.7807 | 86978.3231 | 18.42 | 93.28%
[5 empty] | 18.44 | 1144000 | 660 | 100% | 100% | 91.03% | 0.93278 | 54600 | 243540 | 732275.737 | 1030415.737 | 5408.0527 | 87321.795 | 18.44 | 93.46%
[5 empty] | 18.46 | 1144000 | 660 | 100% | 100% | 91.27% | 0.93459 | 54600 | 243540 | 734218.777 | 1032358.777 | 5429.3649 | 87665.9146 | 18.46 | 93.63%
[5 empty] | 18.48 | 1144000 | 660 | 100% | 100% | 91.51% | 0.9364 | 54600 | 243540 | 736161.817 | 1034301.817 | 5450.7172 | 88010.6819 | 18.48 | 93.81%
[5 empty] | 18.5 | 1144000 | 660 | 100% | 100% | 91.76% | 0.93821 | 54600 | 243540 | 738104.857 | 1036244.857 | 5472.1096 | 88356.0968 | 18.5 | 93.99%
[5 empty] | 18.52 | 1144000 | 660 | 100% | 100% | 92% | 0.94002 | 54600 | 243540 | 740047.897 | 1038187.897 | 5493.5421 | 88702.1594 | 18.52 | 94.16%
[5 empty] | 18.54 | 1144000 | 660 | 100% | 100% | 92.24% | 0.94183 | 54600 | 243540 | 741990.937 | 1040130.937 | 5515.0147 | 89048.8698 | 18.54 | 94.34%
[5 empty] | 18.56 | 1144000 | 660 | 100% | 100% | 92.48% | 0.94364 | 54600 | 243540 | 743933.977 | 1042073.977 | 5536.5274 | 89396.2277 | 18.56 | 94.51%
[5 empty] | 18.58 | 1144000 | 660 | 100% | 100% | 92.72% | 0.94545 | 54600 | 243540 | 745877.017 | 1044017.017 | 5558.0803 | 89744.2334 | 18.58 | 94.69%
[5 empty] | 18.6 | 1144000 | 660 | 100% | 100% | 92.96% | 0.94727 | 54600 | 243540 | 747820.057 | 1045960.057 | 5579.6732 | 90092.8868 | 18.6 | 94.87%
[5 empty] | 18.62 | 1144000 | 660 | 100% | 100% | 93.21% | 0.94908 | 54600 | 243540 | 749763.097 | 1047903.097 | 5601.3063 | 90442.1878 | 18.62 | 95.04%
[5 empty] | 18.64 | 1144000 | 660 | 100% | 100% | 93.45% | 0.95089 | 54600 | 243540 | 751706.137 | 1049846.137 | 5622.9795 | 90792.1365 | 18.64 | 95.22%
[5 empty] | 18.66 | 1144000 | 660 | 100% | 100% | 93.69% | 0.9527 | 54600 | 243540 | 753649.177 | 1051789.177 | 5644.6928 | 91142.7329 | 18.66 | 95.4%
[5 empty] | 18.68 | 1144000 | 660 | 100% | 100% | 93.93% | 0.95451 | 54600 | 243540 | 755592.217 | 1053732.217 | 5666.4462 | 91493.977 | 18.68 | 95.57%
[5 empty] | 18.7 | 1144000 | 660 | 100% | 100% | 94.17% | 0.95632 | 54600 | 243540 | 757535.257 | 1055675.257 | 5688.2397 | 91845.8687 | 18.7 | 95.75%
[5 empty] | 18.72 | 1144000 | 660 | 100% | 100% | 94.41% | 0.95813 | 54600 | 243540 | 759478.297 | 1057618.297 | 5710.0733 | 92198.4082 | 18.72 | 95.92%
[5 empty] | 18.74 | 1144000 | 660 | 100% | 100% | 94.65% | 0.95994 | 54600 | 243540 | 761421.337 | 1059561.337 | 5731.9471 | 92551.5953 | 18.74 | 96.1%
[5 empty] | 18.76 | 1144000 | 660 | 100% | 100% | 94.9% | 0.96175 | 54600 | 243540 | 763364.377 | 1061504.377 | 5753.8609 | 92905.4301 | 18.76 | 96.28%
[5 empty] | 18.78 | 1144000 | 660 | 100% | 100% | 95.14% | 0.96356 | 54600 | 243540 | 765307.417 | 1063447.417 | 5775.8149 | 93259.9125 | 18.78 | 96.45%
[5 empty] | 18.8 | 1144000 | 660 | 100% | 100% | 95.38% | 0.96537 | 54600 | 243540 | 767250.457 | 1065390.457 | 5797.809 | 93615.0427 | 18.8 | 96.63%
[5 empty] | 18.82 | 1144000 | 660 | 100% | 100% | 95.62% | 0.96718 | 54600 | 243540 | 769193.497 | 1067333.497 | 5819.8432 | 93970.8205 | 18.82 | 96.81%
[5 empty] | 18.84 | 1144000 | 660 | 100% | 100% | 95.86% | 0.96899 | 54600 | 243540 | 771136.537 | 1069276.537 | 5841.9175 | 94327.246 | 18.84 | 96.98%
[5 empty] | 18.86 | 1144000 | 660 | 100% | 100% | 96.1% | 0.9708 | 54600 | 243540 | 773079.577 | 1071219.577 | 5864.0319 | 94684.3192 | 18.86 | 97.16%
[5 empty] | 18.88 | 1144000 | 660 | 100% | 100% | 96.35% | 0.97261 | 54600 | 243540 | 775022.617 | 1073162.617 | 5886.1864 | 95042.0401 | 18.88 | 97.33%
[5 empty] | 18.9 | 1144000 | 660 | 100% | 100% | 96.59% | 0.97442 | 54600 | 243540 | 776965.657 | 1075105.657 | 5908.381 | 95400.4087 | 18.9 | 97.51%
[5 empty] | 18.92 | 1144000 | 660 | 100% | 100% | 96.83% | 0.97623 | 54600 | 243540 | 778908.697 | 1077048.697 | 5930.6158 | 95759.4249 | 18.92 | 97.69%
[5 empty] | 18.94 | 1144000 | 660 | 100% | 100% | 97.07% | 0.97804 | 54600 | 243540 | 780851.737 | 1078991.737 | 5952.8907 | 96119.0888 | 18.94 | 97.86%
[5 empty] | 18.96 | 1144000 | 660 | 100% | 100% | 97.31% | 0.97985 | 54600 | 243540 | 782794.777 | 1080934.777 | 5975.2056 | 96479.4004 | 18.96 | 98.04%
[5 empty] | 18.98 | 1144000 | 660 | 100% | 100% | 97.55% | 0.98166 | 54600 | 243540 | 784737.817 | 1082877.817 | 5997.5607 | 96840.3597 | 18.98 | 98.21%
[5 empty] | 19 | 1144000 | 660 | 100% | 100% | 97.79% | 0.98347 | 54600 | 243540 | 786680.857 | 1084820.857 | 6019.9559 | 97201.9666 | 19 | 98.39%
[5 empty] | 19.02 | 1144000 | 660 | 100% | 100% | 98.04% | 0.98528 | 54600 | 243540 | 788623.897 | 1086763.897 | 6042.3913 | 97564.2212 | 19.02 | 98.57%
[5 empty] | 19.04 | 1144000 | 660 | 100% | 100% | 98.28% | 0.98709 | 54600 | 243540 | 790566.937 | 1088706.937 | 6064.8667 | 97927.1236 | 19.04 | 98.74%
[5 empty] | 19.06 | 1144000 | 660 | 100% | 100% | 98.52% | 0.9889 | 54600 | 243540 | 792509.977 | 1090649.977 | 6087.3822 | 98290.6736 | 19.06 | 98.92%
[5 empty] | 19.08 | 1144000 | 660 | 100% | 100% | 98.76% | 0.99071 | 54600 | 243540 | 794453.017 | 1092593.017 | 6109.9379 | 98654.8712 | 19.08 | 99.1%
[5 empty] | 19.1 | 1144000 | 660 | 100% | 100% | 99% | 0.99253 | 54600 | 243540 | 796396.057 | 1094536.057 | 6132.5337 | 99019.7166 | 19.1 | 99.27%
[5 empty] | 19.12 | 1144000 | 660 | 100% | 100% | 99.24% | 0.99434 | 54600 | 243540 | 798339.097 | 1096479.097 | 6155.1695 | 99385.2096 | 19.12 | 99.45%
[5 empty] | 19.14 | 1144000 | 660 | 100% | 100% | 99.49% | 0.99615 | 54600 | 243540 | 800282.137 | 1098422.137 | 6177.8455 | 99751.3503 | 19.14 | 99.62%
[5 empty] | 19.16 | 1144000 | 660 | 100% | 100% | 99.73% | 0.99796 | 54600 | 243540 | 802225.177 | 1100365.177 | 6200.5616 | 100118.1387 | 19.16 | 99.8%
[5 empty] | 19.18 | 1144000 | 660 | 100% | 100% | 99.97% | 0.99977 | 54600 | 243540 | 804168.217 | 1102308.217 | 6223.3178 | 100485.5748 | 19.18 | 99.98%
[5 empty] | 19.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6246.0792 | 100853.0943 | 19.2 | 100%
[5 empty] | 19.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6268.8406 | 101220.6138 | 19.22 | 100%
[5 empty] | 19.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6291.602 | 101588.1333 | 19.24 | 100%
[5 empty] | 19.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6314.3634 | 101955.6529 | 19.26 | 100%
[5 empty] | 19.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6337.1248 | 102323.1724 | 19.28 | 100%
[5 empty] | 19.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6359.8862 | 102690.6919 | 19.3 | 100%
[5 empty] | 19.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6382.6475 | 103058.2114 | 19.32 | 100%
[5 empty] | 19.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6405.4089 | 103425.7309 | 19.34 | 100%
[5 empty] | 19.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6428.1703 | 103793.2505 | 19.36 | 100%
[5 empty] | 19.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6450.9317 | 104160.77 | 19.38 | 100%
[5 empty] | 19.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6473.6931 | 104528.2895 | 19.4 | 100%
[5 empty] | 19.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6496.4545 | 104895.809 | 19.42 | 100%
[5 empty] | 19.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6519.2158 | 105263.3285 | 19.44 | 100%
[5 empty] | 19.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6541.9772 | 105630.8481 | 19.46 | 100%
[5 empty] | 19.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6564.7386 | 105998.3676 | 19.48 | 100%
[5 empty] | 19.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6587.5 | 106365.8871 | 19.5 | 100%
[5 empty] | 19.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6610.2614 | 106733.4066 | 19.52 | 100%
[5 empty] | 19.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6633.0228 | 107100.9261 | 19.54 | 100%
[5 empty] | 19.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6655.7841 | 107468.4457 | 19.56 | 100%
[5 empty] | 19.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6678.5455 | 107835.9652 | 19.58 | 100%
[5 empty] | 19.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6701.3069 | 108203.4847 | 19.6 | 100%
[5 empty] | 19.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6724.0683 | 108571.0042 | 19.62 | 100%
[5 empty] | 19.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6746.8297 | 108938.5237 | 19.64 | 100%
[5 empty] | 19.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6769.5911 | 109306.0433 | 19.66 | 100%
[5 empty] | 19.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6792.3525 | 109673.5628 | 19.68 | 100%
[5 empty] | 19.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6815.1138 | 110041.0823 | 19.7 | 100%
[5 empty] | 19.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6837.8752 | 110408.6018 | 19.72 | 100%
[5 empty] | 19.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6860.6366 | 110776.1213 | 19.74 | 100%
[5 empty] | 19.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6883.398 | 111143.6409 | 19.76 | 100%
[5 empty] | 19.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6906.1594 | 111511.1604 | 19.78 | 100%
[5 empty] | 19.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6928.9208 | 111878.6799 | 19.8 | 100%
[5 empty] | 19.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6951.6821 | 112246.1994 | 19.82 | 100%
[5 empty] | 19.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6974.4435 | 112613.7189 | 19.84 | 100%
[5 empty] | 19.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 6997.2049 | 112981.2385 | 19.86 | 100%
[5 empty] | 19.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7019.9663 | 113348.758 | 19.88 | 100%
[5 empty] | 19.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7042.7277 | 113716.2775 | 19.9 | 100%
[5 empty] | 19.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7065.4891 | 114083.797 | 19.92 | 100%
[5 empty] | 19.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7088.2504 | 114451.3165 | 19.94 | 100%
[5 empty] | 19.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7111.0118 | 114818.8361 | 19.96 | 100%
[5 empty] | 19.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7133.7732 | 115186.3556 | 19.98 | 100%
[5 empty] | 20 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7156.5346 | 115553.8751 | 20 | 100%
[5 empty] | 20.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7179.296 | 115921.3946 | 20.02 | 100%
[5 empty] | 20.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7202.0574 | 116288.9141 | 20.04 | 100%
[5 empty] | 20.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7224.8188 | 116656.4337 | 20.06 | 100%
[5 empty] | 20.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7247.5801 | 117023.9532 | 20.08 | 100%
[5 empty] | 20.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7270.3415 | 117391.4727 | 20.1 | 100%
[5 empty] | 20.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7293.1029 | 117758.9922 | 20.12 | 100%
[5 empty] | 20.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7315.8643 | 118126.5117 | 20.14 | 100%
[5 empty] | 20.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7338.6257 | 118494.0313 | 20.16 | 100%
[5 empty] | 20.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7361.3871 | 118861.5508 | 20.18 | 100%
[5 empty] | 20.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7384.1484 | 119229.0703 | 20.2 | 100%
[5 empty] | 20.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7406.9098 | 119596.5898 | 20.22 | 100%
[5 empty] | 20.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7429.6712 | 119964.1093 | 20.24 | 100%
[5 empty] | 20.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7452.4326 | 120331.6289 | 20.26 | 100%
[5 empty] | 20.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7475.194 | 120699.1484 | 20.28 | 100%
[5 empty] | 20.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7497.9554 | 121066.6679 | 20.3 | 100%
[5 empty] | 20.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7520.7168 | 121434.1874 | 20.32 | 100%
[5 empty] | 20.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7543.4781 | 121801.7069 | 20.34 | 100%
[5 empty] | 20.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7566.2395 | 122169.2265 | 20.36 | 100%
[5 empty] | 20.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7589.0009 | 122536.746 | 20.38 | 100%
[5 empty] | 20.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7611.7623 | 122904.2655 | 20.4 | 100%
[5 empty] | 20.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7634.5237 | 123271.785 | 20.42 | 100%
[5 empty] | 20.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7657.2851 | 123639.3045 | 20.44 | 100%
[5 empty] | 20.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7680.0464 | 124006.8241 | 20.46 | 100%
[5 empty] | 20.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7702.8078 | 124374.3436 | 20.48 | 100%
[5 empty] | 20.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7725.5692 | 124741.8631 | 20.5 | 100%
[5 empty] | 20.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7748.3306 | 125109.3826 | 20.52 | 100%
[5 empty] | 20.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7771.092 | 125476.9021 | 20.54 | 100%
[5 empty] | 20.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7793.8534 | 125844.4217 | 20.56 | 100%
[5 empty] | 20.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7816.6147 | 126211.9412 | 20.58 | 100%
[5 empty] | 20.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7839.3761 | 126579.4607 | 20.6 | 100%
[5 empty] | 20.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7862.1375 | 126946.9802 | 20.62 | 100%
[5 empty] | 20.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7884.8989 | 127314.4997 | 20.64 | 100%
[5 empty] | 20.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7907.6603 | 127682.0193 | 20.66 | 100%
[5 empty] | 20.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7930.4217 | 128049.5388 | 20.68 | 100%
[5 empty] | 20.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7953.1831 | 128417.0583 | 20.7 | 100%
[5 empty] | 20.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7975.9444 | 128784.5778 | 20.72 | 100%
[5 empty] | 20.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 7998.7058 | 129152.0973 | 20.74 | 100%
[5 empty] | 20.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8021.4672 | 129519.6169 | 20.76 | 100%
[5 empty] | 20.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8044.2286 | 129887.1364 | 20.78 | 100%
[5 empty] | 20.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8066.99 | 130254.6559 | 20.8 | 100%
[5 empty] | 20.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8089.7514 | 130622.1754 | 20.82 | 100%
[5 empty] | 20.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8112.5127 | 130989.6949 | 20.84 | 100%
[5 empty] | 20.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8135.2741 | 131357.2145 | 20.86 | 100%
[5 empty] | 20.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8158.0355 | 131724.734 | 20.88 | 100%
[5 empty] | 20.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8180.7969 | 132092.2535 | 20.9 | 100%
[5 empty] | 20.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8203.5583 | 132459.773 | 20.92 | 100%
[5 empty] | 20.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8226.3197 | 132827.2925 | 20.94 | 100%
[5 empty] | 20.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8249.081 | 133194.8121 | 20.96 | 100%
[5 empty] | 20.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8271.8424 | 133562.3316 | 20.98 | 100%
[5 empty] | 21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8294.6038 | 133929.8511 | 21 | 100%
[5 empty] | 21.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8317.3652 | 134297.3706 | 21.02 | 100%
[5 empty] | 21.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8340.1266 | 134664.8901 | 21.04 | 100%
[5 empty] | 21.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8362.888 | 135032.4097 | 21.06 | 100%
[5 empty] | 21.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8385.6494 | 135399.9292 | 21.08 | 100%
[5 empty] | 21.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8408.4107 | 135767.4487 | 21.1 | 100%
[5 empty] | 21.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8431.1721 | 136134.9682 | 21.12 | 100%
[5 empty] | 21.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8453.9335 | 136502.4877 | 21.14 | 100%
[5 empty] | 21.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8476.6949 | 136870.0073 | 21.16 | 100%
[5 empty] | 21.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8499.4563 | 137237.5268 | 21.18 | 100%
[5 empty] | 21.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8522.2177 | 137605.0463 | 21.2 | 100%
[5 empty] | 21.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8544.979 | 137972.5658 | 21.22 | 100%
[5 empty] | 21.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8567.7404 | 138340.0853 | 21.24 | 100%
[5 empty] | 21.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8590.5018 | 138707.6049 | 21.26 | 100%
[5 empty] | 21.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8613.2632 | 139075.1244 | 21.28 | 100%
[5 empty] | 21.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8636.0246 | 139442.6439 | 21.3 | 100%
[5 empty] | 21.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8658.786 | 139810.1634 | 21.32 | 100%
[5 empty] | 21.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8681.5474 | 140177.6829 | 21.34 | 100%
[5 empty] | 21.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8704.3087 | 140545.2025 | 21.36 | 100%
[5 empty] | 21.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8727.0701 | 140912.722 | 21.38 | 100%
[5 empty] | 21.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8749.8315 | 141280.2415 | 21.4 | 100%
[5 empty] | 21.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8772.5929 | 141647.761 | 21.42 | 100%
[5 empty] | 21.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8795.3543 | 142015.2805 | 21.44 | 100%
[5 empty] | 21.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8818.1157 | 142382.8001 | 21.46 | 100%
[5 empty] | 21.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8840.877 | 142750.3196 | 21.48 | 100%
[5 empty] | 21.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8863.6384 | 143117.8391 | 21.5 | 100%
[5 empty] | 21.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8886.3998 | 143485.3586 | 21.52 | 100%
[5 empty] | 21.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8909.1612 | 143852.8781 | 21.54 | 100%
[5 empty] | 21.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8931.9226 | 144220.3977 | 21.56 | 100%
[5 empty] | 21.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8954.684 | 144587.9172 | 21.58 | 100%
[5 empty] | 21.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 8977.4453 | 144955.4367 | 21.6 | 100%
[5 empty] | 21.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9000.2067 | 145322.9562 | 21.62 | 100%
[5 empty] | 21.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9022.9681 | 145690.4757 | 21.64 | 100%
[5 empty] | 21.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9045.7295 | 146057.9953 | 21.66 | 100%
[5 empty] | 21.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9068.4909 | 146425.5148 | 21.68 | 100%
[5 empty] | 21.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9091.2523 | 146793.0343 | 21.7 | 100%
[5 empty] | 21.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9114.0137 | 147160.5538 | 21.72 | 100%
[5 empty] | 21.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9136.775 | 147528.0733 | 21.74 | 100%
[5 empty] | 21.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9159.5364 | 147895.5929 | 21.76 | 100%
[5 empty] | 21.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9182.2978 | 148263.1124 | 21.78 | 100%
[5 empty] | 21.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9205.0592 | 148630.6319 | 21.8 | 100%
[5 empty] | 21.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9227.8206 | 148998.1514 | 21.82 | 100%
[5 empty] | 21.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9250.582 | 149365.6709 | 21.84 | 100%
[5 empty] | 21.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9273.3433 | 149733.1905 | 21.86 | 100%
[5 empty] | 21.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9296.1047 | 150100.71 | 21.88 | 100%
[5 empty] | 21.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9318.8661 | 150468.2295 | 21.9 | 100%
[5 empty] | 21.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9341.6275 | 150835.749 | 21.92 | 100%
[5 empty] | 21.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9364.3889 | 151203.2685 | 21.94 | 100%
[5 empty] | 21.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9387.1503 | 151570.7881 | 21.96 | 100%
[5 empty] | 21.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9409.9116 | 151938.3076 | 21.98 | 100%
[5 empty] | 22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9432.673 | 152305.8271 | 22 | 100%
[5 empty] | 22.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9455.4344 | 152673.3466 | 22.02 | 100%
[5 empty] | 22.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9478.1958 | 153040.8661 | 22.04 | 100%
[5 empty] | 22.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9500.9572 | 153408.3857 | 22.06 | 100%
[5 empty] | 22.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9523.7186 | 153775.9052 | 22.08 | 100%
[5 empty] | 22.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9546.48 | 154143.4247 | 22.1 | 100%
[5 empty] | 22.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9569.2413 | 154510.9442 | 22.12 | 100%
[5 empty] | 22.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9592.0027 | 154878.4637 | 22.14 | 100%
[5 empty] | 22.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9614.7641 | 155245.9833 | 22.16 | 100%
[5 empty] | 22.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9637.5255 | 155613.5028 | 22.18 | 100%
[5 empty] | 22.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9660.2869 | 155981.0223 | 22.2 | 100%
[5 empty] | 22.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9683.0483 | 156348.5418 | 22.22 | 100%
[5 empty] | 22.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9705.8096 | 156716.0613 | 22.24 | 100%
[5 empty] | 22.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9728.571 | 157083.5809 | 22.26 | 100%
[5 empty] | 22.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9751.3324 | 157451.1004 | 22.28 | 100%
[5 empty] | 22.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9774.0938 | 157818.6199 | 22.3 | 100%
[5 empty] | 22.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9796.8552 | 158186.1394 | 22.32 | 100%
[5 empty] | 22.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9819.6166 | 158553.6589 | 22.34 | 100%
[5 empty] | 22.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9842.378 | 158921.1785 | 22.36 | 100%
[5 empty] | 22.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9865.1393 | 159288.698 | 22.38 | 100%
[5 empty] | 22.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9887.9007 | 159656.2175 | 22.4 | 100%
[5 empty] | 22.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9910.6621 | 160023.737 | 22.42 | 100%
[5 empty] | 22.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9933.4235 | 160391.2565 | 22.44 | 100%
[5 empty] | 22.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9956.1849 | 160758.7761 | 22.46 | 100%
[5 empty] | 22.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 9978.9463 | 161126.2956 | 22.48 | 100%
[5 empty] | 22.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10001.7076 | 161493.8151 | 22.5 | 100%
[5 empty] | 22.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10024.469 | 161861.3346 | 22.52 | 100%
[5 empty] | 22.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10047.2304 | 162228.8541 | 22.54 | 100%
[5 empty] | 22.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10069.9918 | 162596.3737 | 22.56 | 100%
[5 empty] | 22.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10092.7532 | 162963.8932 | 22.58 | 100%
[5 empty] | 22.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10115.5146 | 163331.4127 | 22.6 | 100%
[5 empty] | 22.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10138.2759 | 163698.9322 | 22.62 | 100%
[5 empty] | 22.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10161.0373 | 164066.4517 | 22.64 | 100%
[5 empty] | 22.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10183.7987 | 164433.9713 | 22.66 | 100%
[5 empty] | 22.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10206.5601 | 164801.4908 | 22.68 | 100%
[5 empty] | 22.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10229.3215 | 165169.0103 | 22.7 | 100%
[5 empty] | 22.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10252.0829 | 165536.5298 | 22.72 | 100%
[5 empty] | 22.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10274.8443 | 165904.0493 | 22.74 | 100%
[5 empty] | 22.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10297.6056 | 166271.5689 | 22.76 | 100%
[5 empty] | 22.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10320.367 | 166639.0884 | 22.78 | 100%
[5 empty] | 22.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10343.1284 | 167006.6079 | 22.8 | 100%
[5 empty] | 22.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10365.8898 | 167374.1274 | 22.82 | 100%
[5 empty] | 22.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10388.6512 | 167741.6469 | 22.84 | 100%
[5 empty] | 22.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10411.4126 | 168109.1665 | 22.86 | 100%
[5 empty] | 22.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10434.1739 | 168476.686 | 22.88 | 100%
[5 empty] | 22.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10456.9353 | 168844.2055 | 22.9 | 100%
[5 empty] | 22.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10479.6967 | 169211.725 | 22.92 | 100%
[5 empty] | 22.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10502.4581 | 169579.2445 | 22.94 | 100%
[5 empty] | 22.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10525.2195 | 169946.7641 | 22.96 | 100%
[5 empty] | 22.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10547.9809 | 170314.2836 | 22.98 | 100%
[5 empty] | 23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10570.7423 | 170681.8031 | 23 | 100%
[5 empty] | 23.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10593.5036 | 171049.3226 | 23.02 | 100%
[5 empty] | 23.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10616.265 | 171416.8421 | 23.04 | 100%
[5 empty] | 23.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10639.0264 | 171784.3617 | 23.06 | 100%
[5 empty] | 23.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10661.7878 | 172151.8812 | 23.08 | 100%
[5 empty] | 23.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10684.5492 | 172519.4007 | 23.1 | 100%
[5 empty] | 23.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10707.3106 | 172886.9202 | 23.12 | 100%
[5 empty] | 23.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10730.0719 | 173254.4397 | 23.14 | 100%
[5 empty] | 23.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10752.8333 | 173621.9593 | 23.16 | 100%
[5 empty] | 23.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10775.5947 | 173989.4788 | 23.18 | 100%
[5 empty] | 23.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10798.3561 | 174356.9983 | 23.2 | 100%
[5 empty] | 23.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10821.1175 | 174724.5178 | 23.22 | 100%
[5 empty] | 23.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10843.8789 | 175092.0373 | 23.24 | 100%
[5 empty] | 23.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10866.6402 | 175459.5569 | 23.26 | 100%
[5 empty] | 23.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10889.4016 | 175827.0764 | 23.28 | 100%
[5 empty] | 23.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10912.163 | 176194.5959 | 23.3 | 100%
[5 empty] | 23.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10934.9244 | 176562.1154 | 23.32 | 100%
[5 empty] | 23.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10957.6858 | 176929.6349 | 23.34 | 100%
[5 empty] | 23.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 10980.4472 | 177297.1545 | 23.36 | 100%
[5 empty] | 23.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11003.2086 | 177664.674 | 23.38 | 100%
[5 empty] | 23.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11025.9699 | 178032.1935 | 23.4 | 100%
[5 empty] | 23.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11048.7313 | 178399.713 | 23.42 | 100%
[5 empty] | 23.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11071.4927 | 178767.2325 | 23.44 | 100%
[5 empty] | 23.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11094.2541 | 179134.7521 | 23.46 | 100%
[5 empty] | 23.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11117.0155 | 179502.2716 | 23.48 | 100%
[5 empty] | 23.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11139.7769 | 179869.7911 | 23.5 | 100%
[5 empty] | 23.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11162.5382 | 180237.3106 | 23.52 | 100%
[5 empty] | 23.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11185.2996 | 180604.8301 | 23.54 | 100%
[5 empty] | 23.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11208.061 | 180972.3497 | 23.56 | 100%
[5 empty] | 23.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11230.8224 | 181339.8692 | 23.58 | 100%
[5 empty] | 23.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11253.5838 | 181707.3887 | 23.6 | 100%
[5 empty] | 23.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11276.3452 | 182074.9082 | 23.62 | 100%
[5 empty] | 23.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11299.1065 | 182442.4277 | 23.64 | 100%
[5 empty] | 23.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11321.8679 | 182809.9473 | 23.66 | 100%
[5 empty] | 23.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11344.6293 | 183177.4668 | 23.68 | 100%
[5 empty] | 23.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11367.3907 | 183544.9863 | 23.7 | 100%
[5 empty] | 23.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11390.1521 | 183912.5058 | 23.72 | 100%
[5 empty] | 23.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11412.9135 | 184280.0253 | 23.74 | 100%
[5 empty] | 23.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11435.6749 | 184647.5449 | 23.76 | 100%
[5 empty] | 23.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11458.4362 | 185015.0644 | 23.78 | 100%
[5 empty] | 23.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11481.1976 | 185382.5839 | 23.8 | 100%
[5 empty] | 23.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11503.959 | 185750.1034 | 23.82 | 100%
[5 empty] | 23.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11526.7204 | 186117.6229 | 23.84 | 100%
[5 empty] | 23.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11549.4818 | 186485.1425 | 23.86 | 100%
[5 empty] | 23.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11572.2432 | 186852.662 | 23.88 | 100%
[5 empty] | 23.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11595.0045 | 187220.1815 | 23.9 | 100%
[5 empty] | 23.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11617.7659 | 187587.701 | 23.92 | 100%
[5 empty] | 23.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11640.5273 | 187955.2205 | 23.94 | 100%
[5 empty] | 23.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11663.2887 | 188322.7401 | 23.96 | 100%
[5 empty] | 23.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11686.0501 | 188690.2596 | 23.98 | 100%
[5 empty] | 24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11708.8115 | 189057.7791 | 24 | 100%
[5 empty] | 24.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11731.5729 | 189425.2986 | 24.02 | 100%
[5 empty] | 24.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11754.3342 | 189792.8181 | 24.04 | 100%
[5 empty] | 24.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11777.0956 | 190160.3377 | 24.06 | 100%
[5 empty] | 24.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11799.857 | 190527.8572 | 24.08 | 100%
[5 empty] | 24.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11822.6184 | 190895.3767 | 24.1 | 100%
[5 empty] | 24.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11845.3798 | 191262.8962 | 24.12 | 100%
[5 empty] | 24.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11868.1412 | 191630.4157 | 24.14 | 100%
[5 empty] | 24.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11890.9025 | 191997.9353 | 24.16 | 100%
[5 empty] | 24.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11913.6639 | 192365.4548 | 24.18 | 100%
[5 empty] | 24.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11936.4253 | 192732.9743 | 24.2 | 100%
[5 empty] | 24.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11959.1867 | 193100.4938 | 24.22 | 100%
[5 empty] | 24.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 11981.9481 | 193468.0133 | 24.24 | 100%
[5 empty] | 24.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12004.7095 | 193835.5329 | 24.26 | 100%
[5 empty] | 24.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12027.4708 | 194203.0524 | 24.28 | 100%
[5 empty] | 24.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12050.2322 | 194570.5719 | 24.3 | 100%
[5 empty] | 24.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12072.9936 | 194938.0914 | 24.32 | 100%
[5 empty] | 24.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12095.755 | 195305.6109 | 24.34 | 100%
[5 empty] | 24.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12118.5164 | 195673.1305 | 24.36 | 100%
[5 empty] | 24.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12141.2778 | 196040.65 | 24.38 | 100%
[5 empty] | 24.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12164.0392 | 196408.1695 | 24.4 | 100%
[5 empty] | 24.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12186.8005 | 196775.689 | 24.42 | 100%
[5 empty] | 24.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12209.5619 | 197143.2085 | 24.44 | 100%
[5 empty] | 24.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12232.3233 | 197510.7281 | 24.46 | 100%
[5 empty] | 24.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12255.0847 | 197878.2476 | 24.48 | 100%
[5 empty] | 24.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12277.8461 | 198245.7671 | 24.5 | 100%
[5 empty] | 24.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12300.6075 | 198613.2866 | 24.52 | 100%
[5 empty] | 24.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12323.3688 | 198980.8061 | 24.54 | 100%
[5 empty] | 24.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12346.1302 | 199348.3257 | 24.56 | 100%
[5 empty] | 24.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12368.8916 | 199715.8452 | 24.58 | 100%
[5 empty] | 24.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12391.653 | 200083.3647 | 24.6 | 100%
[5 empty] | 24.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12414.4144 | 200450.8842 | 24.62 | 100%
[5 empty] | 24.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12437.1758 | 200818.4037 | 24.64 | 100%
[5 empty] | 24.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12459.9371 | 201185.9233 | 24.66 | 100%
[5 empty] | 24.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12482.6985 | 201553.4428 | 24.68 | 100%
[5 empty] | 24.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12505.4599 | 201920.9623 | 24.7 | 100%
[5 empty] | 24.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12528.2213 | 202288.4818 | 24.72 | 100%
[5 empty] | 24.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12550.9827 | 202656.0013 | 24.74 | 100%
[5 empty] | 24.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12573.7441 | 203023.5209 | 24.76 | 100%
[5 empty] | 24.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12596.5055 | 203391.0404 | 24.78 | 100%
[5 empty] | 24.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12619.2668 | 203758.5599 | 24.8 | 100%
[5 empty] | 24.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12642.0282 | 204126.0794 | 24.82 | 100%
[5 empty] | 24.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12664.7896 | 204493.5989 | 24.84 | 100%
[5 empty] | 24.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12687.551 | 204861.1185 | 24.86 | 100%
[5 empty] | 24.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12710.3124 | 205228.638 | 24.88 | 100%
[5 empty] | 24.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12733.0738 | 205596.1575 | 24.9 | 100%
[5 empty] | 24.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12755.8351 | 205963.677 | 24.92 | 100%
[5 empty] | 24.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12778.5965 | 206331.1965 | 24.94 | 100%
[5 empty] | 24.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12801.3579 | 206698.7161 | 24.96 | 100%
[5 empty] | 24.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12824.1193 | 207066.2356 | 24.98 | 100%
[5 empty] | 25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12846.8807 | 207433.7551 | 25 | 100%
[5 empty] | 25.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12869.6421 | 207801.2746 | 25.02 | 100%
[5 empty] | 25.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12892.4035 | 208168.7941 | 25.04 | 100%
[5 empty] | 25.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12915.1648 | 208536.3137 | 25.06 | 100%
[5 empty] | 25.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12937.9262 | 208903.8332 | 25.08 | 100%
[5 empty] | 25.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12960.6876 | 209271.3527 | 25.1 | 100%
[5 empty] | 25.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 12983.449 | 209638.8722 | 25.12 | 100%
[5 empty] | 25.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13006.2104 | 210006.3917 | 25.14 | 100%
[5 empty] | 25.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13028.9718 | 210373.9113 | 25.16 | 100%
[5 empty] | 25.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13051.7331 | 210741.4308 | 25.18 | 100%
[5 empty] | 25.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13074.4945 | 211108.9503 | 25.2 | 100%
[5 empty] | 25.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13097.2559 | 211476.4698 | 25.22 | 100%
[5 empty] | 25.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13120.0173 | 211843.9893 | 25.24 | 100%
[5 empty] | 25.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13142.7787 | 212211.5089 | 25.26 | 100%
[5 empty] | 25.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13165.5401 | 212579.0284 | 25.28 | 100%
[5 empty] | 25.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13188.3014 | 212946.5479 | 25.3 | 100%
[5 empty] | 25.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13211.0628 | 213314.0674 | 25.32 | 100%
[5 empty] | 25.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13233.8242 | 213681.5869 | 25.34 | 100%
[5 empty] | 25.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13256.5856 | 214049.1065 | 25.36 | 100%
[5 empty] | 25.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13279.347 | 214416.626 | 25.38 | 100%
[5 empty] | 25.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13302.1084 | 214784.1455 | 25.4 | 100%
[5 empty] | 25.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13324.8698 | 215151.665 | 25.42 | 100%
[5 empty] | 25.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13347.6311 | 215519.1845 | 25.44 | 100%
[5 empty] | 25.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13370.3925 | 215886.7041 | 25.46 | 100%
[5 empty] | 25.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13393.1539 | 216254.2236 | 25.48 | 100%
[5 empty] | 25.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13415.9153 | 216621.7431 | 25.5 | 100%
[5 empty] | 25.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13438.6767 | 216989.2626 | 25.52 | 100%
[5 empty] | 25.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13461.4381 | 217356.7821 | 25.54 | 100%
[5 empty] | 25.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13484.1994 | 217724.3017 | 25.56 | 100%
[5 empty] | 25.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13506.9608 | 218091.8212 | 25.58 | 100%
[5 empty] | 25.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13529.7222 | 218459.3407 | 25.6 | 100%
[5 empty] | 25.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13552.4836 | 218826.8602 | 25.62 | 100%
[5 empty] | 25.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13575.245 | 219194.3797 | 25.64 | 100%
[5 empty] | 25.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13598.0064 | 219561.8993 | 25.66 | 100%
[5 empty] | 25.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13620.7677 | 219929.4188 | 25.68 | 100%
[5 empty] | 25.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13643.5291 | 220296.9383 | 25.7 | 100%
[5 empty] | 25.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13666.2905 | 220664.4578 | 25.72 | 100%
[5 empty] | 25.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13689.0519 | 221031.9773 | 25.74 | 100%
[5 empty] | 25.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13711.8133 | 221399.4969 | 25.76 | 100%
[5 empty] | 25.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13734.5747 | 221767.0164 | 25.78 | 100%
[5 empty] | 25.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13757.3361 | 222134.5359 | 25.8 | 100%
[5 empty] | 25.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13780.0974 | 222502.0554 | 25.82 | 100%
[5 empty] | 25.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13802.8588 | 222869.5749 | 25.84 | 100%
[5 empty] | 25.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13825.6202 | 223237.0945 | 25.86 | 100%
[5 empty] | 25.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13848.3816 | 223604.614 | 25.88 | 100%
[5 empty] | 25.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13871.143 | 223972.1335 | 25.9 | 100%
[5 empty] | 25.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13893.9044 | 224339.653 | 25.92 | 100%
[5 empty] | 25.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13916.6657 | 224707.1725 | 25.94 | 100%
[5 empty] | 25.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13939.4271 | 225074.6921 | 25.96 | 100%
[5 empty] | 25.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13962.1885 | 225442.2116 | 25.98 | 100%
[5 empty] | 26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 13984.9499 | 225809.7311 | 26 | 100%
[5 empty] | 26.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14007.7113 | 226177.2506 | 26.02 | 100%
[5 empty] | 26.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14030.4727 | 226544.7701 | 26.04 | 100%
[5 empty] | 26.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14053.2341 | 226912.2897 | 26.06 | 100%
[5 empty] | 26.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14075.9954 | 227279.8092 | 26.08 | 100%
[5 empty] | 26.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14098.7568 | 227647.3287 | 26.1 | 100%
[5 empty] | 26.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14121.5182 | 228014.8482 | 26.12 | 100%
[5 empty] | 26.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14144.2796 | 228382.3677 | 26.14 | 100%
[5 empty] | 26.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14167.041 | 228749.8873 | 26.16 | 100%
[5 empty] | 26.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14189.8024 | 229117.4068 | 26.18 | 100%
[5 empty] | 26.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14212.5637 | 229484.9263 | 26.2 | 100%
[5 empty] | 26.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14235.3251 | 229852.4458 | 26.22 | 100%
[5 empty] | 26.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14258.0865 | 230219.9653 | 26.24 | 100%
[5 empty] | 26.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14280.8479 | 230587.4849 | 26.26 | 100%
[5 empty] | 26.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14303.6093 | 230955.0044 | 26.28 | 100%
[5 empty] | 26.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14326.3707 | 231322.5239 | 26.3 | 100%
[5 empty] | 26.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14349.132 | 231690.0434 | 26.32 | 100%
[5 empty] | 26.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14371.8934 | 232057.5629 | 26.34 | 100%
[5 empty] | 26.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14394.6548 | 232425.0825 | 26.36 | 100%
[5 empty] | 26.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14417.4162 | 232792.602 | 26.38 | 100%
[5 empty] | 26.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14440.1776 | 233160.1215 | 26.4 | 100%
[5 empty] | 26.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14462.939 | 233527.641 | 26.42 | 100%
[5 empty] | 26.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14485.7004 | 233895.1605 | 26.44 | 100%
[5 empty] | 26.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14508.4617 | 234262.6801 | 26.46 | 100%
[5 empty] | 26.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14531.2231 | 234630.1996 | 26.48 | 100%
[5 empty] | 26.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14553.9845 | 234997.7191 | 26.5 | 100%
[5 empty] | 26.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14576.7459 | 235365.2386 | 26.52 | 100%
[5 empty] | 26.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14599.5073 | 235732.7581 | 26.54 | 100%
[5 empty] | 26.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14622.2687 | 236100.2777 | 26.56 | 100%
[5 empty] | 26.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14645.03 | 236467.7972 | 26.58 | 100%
[5 empty] | 26.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14667.7914 | 236835.3167 | 26.6 | 100%
[5 empty] | 26.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14690.5528 | 237202.8362 | 26.62 | 100%
[5 empty] | 26.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14713.3142 | 237570.3557 | 26.64 | 100%
[5 empty] | 26.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14736.0756 | 237937.8753 | 26.66 | 100%
[5 empty] | 26.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14758.837 | 238305.3948 | 26.68 | 100%
[5 empty] | 26.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14781.5984 | 238672.9143 | 26.7 | 100%
[5 empty] | 26.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14804.3597 | 239040.4338 | 26.72 | 100%
[5 empty] | 26.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14827.1211 | 239407.9533 | 26.74 | 100%
[5 empty] | 26.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14849.8825 | 239775.4729 | 26.76 | 100%
[5 empty] | 26.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14872.6439 | 240142.9924 | 26.78 | 100%
[5 empty] | 26.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14895.4053 | 240510.5119 | 26.8 | 100%
[5 empty] | 26.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14918.1667 | 240878.0314 | 26.82 | 100%
[5 empty] | 26.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14940.928 | 241245.5509 | 26.84 | 100%
[5 empty] | 26.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14963.6894 | 241613.0705 | 26.86 | 100%
[5 empty] | 26.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 14986.4508 | 241980.59 | 26.88 | 100%
[5 empty] | 26.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15009.2122 | 242348.1095 | 26.9 | 100%
[5 empty] | 26.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15031.9736 | 242715.629 | 26.92 | 100%
[5 empty] | 26.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15054.735 | 243083.1485 | 26.94 | 100%
[5 empty] | 26.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15077.4963 | 243450.6681 | 26.96 | 100%
[5 empty] | 26.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15100.2577 | 243818.1876 | 26.98 | 100%
[5 empty] | 27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15123.0191 | 244185.7071 | 27 | 100%
[5 empty] | 27.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15145.7805 | 244553.2266 | 27.02 | 100%
[5 empty] | 27.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15168.5419 | 244920.7461 | 27.04 | 100%
[5 empty] | 27.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15191.3033 | 245288.2657 | 27.06 | 100%
[5 empty] | 27.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15214.0647 | 245655.7852 | 27.08 | 100%
[5 empty] | 27.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15236.826 | 246023.3047 | 27.1 | 100%
[5 empty] | 27.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15259.5874 | 246390.8242 | 27.12 | 100%
[5 empty] | 27.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15282.3488 | 246758.3437 | 27.14 | 100%
[5 empty] | 27.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15305.1102 | 247125.8633 | 27.16 | 100%
[5 empty] | 27.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15327.8716 | 247493.3828 | 27.18 | 100%
[5 empty] | 27.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15350.633 | 247860.9023 | 27.2 | 100%
[5 empty] | 27.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15373.3943 | 248228.4218 | 27.22 | 100%
[5 empty] | 27.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15396.1557 | 248595.9413 | 27.24 | 100%
[5 empty] | 27.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15418.9171 | 248963.4609 | 27.26 | 100%
[5 empty] | 27.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15441.6785 | 249330.9804 | 27.28 | 100%
[5 empty] | 27.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15464.4399 | 249698.4999 | 27.3 | 100%
[5 empty] | 27.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15487.2013 | 250066.0194 | 27.32 | 100%
[5 empty] | 27.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15509.9626 | 250433.5389 | 27.34 | 100%
[5 empty] | 27.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15532.724 | 250801.0585 | 27.36 | 100%
[5 empty] | 27.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15555.4854 | 251168.578 | 27.38 | 100%
[5 empty] | 27.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15578.2468 | 251536.0975 | 27.4 | 100%
[5 empty] | 27.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15601.0082 | 251903.617 | 27.42 | 100%
[5 empty] | 27.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15623.7696 | 252271.1365 | 27.44 | 100%
[5 empty] | 27.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15646.531 | 252638.6561 | 27.46 | 100%
[5 empty] | 27.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15669.2923 | 253006.1756 | 27.48 | 100%
[5 empty] | 27.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15692.0537 | 253373.6951 | 27.5 | 100%
[5 empty] | 27.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15714.8151 | 253741.2146 | 27.52 | 100%
[5 empty] | 27.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15737.5765 | 254108.7341 | 27.54 | 100%
[5 empty] | 27.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15760.3379 | 254476.2537 | 27.56 | 100%
[5 empty] | 27.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15783.0993 | 254843.7732 | 27.58 | 100%
[5 empty] | 27.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15805.8606 | 255211.2927 | 27.6 | 100%
[5 empty] | 27.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15828.622 | 255578.8122 | 27.62 | 100%
[5 empty] | 27.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15851.3834 | 255946.3317 | 27.64 | 100%
[5 empty] | 27.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15874.1448 | 256313.8513 | 27.66 | 100%
[5 empty] | 27.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15896.9062 | 256681.3708 | 27.68 | 100%
[5 empty] | 27.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15919.6676 | 257048.8903 | 27.7 | 100%
[5 empty] | 27.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15942.429 | 257416.4098 | 27.72 | 100%
[5 empty] | 27.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15965.1903 | 257783.9293 | 27.74 | 100%
[5 empty] | 27.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 15987.9517 | 258151.4489 | 27.76 | 100%
[5 empty] | 27.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16010.7131 | 258518.9684 | 27.78 | 100%
[5 empty] | 27.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16033.4745 | 258886.4879 | 27.8 | 100%
[5 empty] | 27.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16056.2359 | 259254.0074 | 27.82 | 100%
[5 empty] | 27.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16078.9973 | 259621.5269 | 27.84 | 100%
[5 empty] | 27.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16101.7586 | 259989.0465 | 27.86 | 100%
[5 empty] | 27.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16124.52 | 260356.566 | 27.88 | 100%
[5 empty] | 27.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16147.2814 | 260724.0855 | 27.9 | 100%
[5 empty] | 27.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16170.0428 | 261091.605 | 27.92 | 100%
[5 empty] | 27.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16192.8042 | 261459.1245 | 27.94 | 100%
[5 empty] | 27.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16215.5656 | 261826.6441 | 27.96 | 100%
[5 empty] | 27.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16238.3269 | 262194.1636 | 27.98 | 100%
[5 empty] | 28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16261.0883 | 262561.6831 | 28 | 100%
[5 empty] | 28.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16283.8497 | 262929.2026 | 28.02 | 100%
[5 empty] | 28.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16306.6111 | 263296.7221 | 28.04 | 100%
[5 empty] | 28.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16329.3725 | 263664.2417 | 28.06 | 100%
[5 empty] | 28.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16352.1339 | 264031.7612 | 28.08 | 100%
[5 empty] | 28.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16374.8953 | 264399.2807 | 28.1 | 100%
[5 empty] | 28.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16397.6566 | 264766.8002 | 28.12 | 100%
[5 empty] | 28.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16420.418 | 265134.3197 | 28.14 | 100%
[5 empty] | 28.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16443.1794 | 265501.8393 | 28.16 | 100%
[5 empty] | 28.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16465.9408 | 265869.3588 | 28.18 | 100%
[5 empty] | 28.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16488.7022 | 266236.8783 | 28.2 | 100%
[5 empty] | 28.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16511.4636 | 266604.3978 | 28.22 | 100%
[5 empty] | 28.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16534.2249 | 266971.9173 | 28.24 | 100%
[5 empty] | 28.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16556.9863 | 267339.4369 | 28.26 | 100%
[5 empty] | 28.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16579.7477 | 267706.9564 | 28.28 | 100%
[5 empty] | 28.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16602.5091 | 268074.4759 | 28.3 | 100%
[5 empty] | 28.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16625.2705 | 268441.9954 | 28.32 | 100%
[5 empty] | 28.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16648.0319 | 268809.5149 | 28.34 | 100%
[5 empty] | 28.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16670.7932 | 269177.0345 | 28.36 | 100%
[5 empty] | 28.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16693.5546 | 269544.554 | 28.38 | 100%
[5 empty] | 28.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16716.316 | 269912.0735 | 28.4 | 100%
[5 empty] | 28.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16739.0774 | 270279.593 | 28.42 | 100%
[5 empty] | 28.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16761.8388 | 270647.1125 | 28.44 | 100%
[5 empty] | 28.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16784.6002 | 271014.6321 | 28.46 | 100%
[5 empty] | 28.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16807.3616 | 271382.1516 | 28.48 | 100%
[5 empty] | 28.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16830.1229 | 271749.6711 | 28.5 | 100%
[5 empty] | 28.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16852.8843 | 272117.1906 | 28.52 | 100%
[5 empty] | 28.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16875.6457 | 272484.7101 | 28.54 | 100%
[5 empty] | 28.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16898.4071 | 272852.2297 | 28.56 | 100%
[5 empty] | 28.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16921.1685 | 273219.7492 | 28.58 | 100%
[5 empty] | 28.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16943.9299 | 273587.2687 | 28.6 | 100%
[5 empty] | 28.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16966.6912 | 273954.7882 | 28.62 | 100%
[5 empty] | 28.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 16989.4526 | 274322.3077 | 28.64 | 100%
[5 empty] | 28.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17012.214 | 274689.8273 | 28.66 | 100%
[5 empty] | 28.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17034.9754 | 275057.3468 | 28.68 | 100%
[5 empty] | 28.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17057.7368 | 275424.8663 | 28.7 | 100%
[5 empty] | 28.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17080.4982 | 275792.3858 | 28.72 | 100%
[5 empty] | 28.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17103.2596 | 276159.9053 | 28.74 | 100%
[5 empty] | 28.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17126.0209 | 276527.4249 | 28.76 | 100%
[5 empty] | 28.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17148.7823 | 276894.9444 | 28.78 | 100%
[5 empty] | 28.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17171.5437 | 277262.4639 | 28.8 | 100%
[5 empty] | 28.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17194.3051 | 277629.9834 | 28.82 | 100%
[5 empty] | 28.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17217.0665 | 277997.5029 | 28.84 | 100%
[5 empty] | 28.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17239.8279 | 278365.0225 | 28.86 | 100%
[5 empty] | 28.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17262.5892 | 278732.542 | 28.88 | 100%
[5 empty] | 28.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17285.3506 | 279100.0615 | 28.9 | 100%
[5 empty] | 28.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17308.112 | 279467.581 | 28.92 | 100%
[5 empty] | 28.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17330.8734 | 279835.1005 | 28.94 | 100%
[5 empty] | 28.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17353.6348 | 280202.6201 | 28.96 | 100%
[5 empty] | 28.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17376.3962 | 280570.1396 | 28.98 | 100%
[5 empty] | 29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17399.1575 | 280937.6591 | 29 | 100%
[5 empty] | 29.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17421.9189 | 281305.1786 | 29.02 | 100%
[5 empty] | 29.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17444.6803 | 281672.6981 | 29.04 | 100%
[5 empty] | 29.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17467.4417 | 282040.2177 | 29.06 | 100%
[5 empty] | 29.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17490.2031 | 282407.7372 | 29.08 | 100%
[5 empty] | 29.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17512.9645 | 282775.2567 | 29.1 | 100%
[5 empty] | 29.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17535.7259 | 283142.7762 | 29.12 | 100%
[5 empty] | 29.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17558.4872 | 283510.2957 | 29.14 | 100%
[5 empty] | 29.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17581.2486 | 283877.8153 | 29.16 | 100%
[5 empty] | 29.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17604.01 | 284245.3348 | 29.18 | 100%
[5 empty] | 29.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17626.7714 | 284612.8543 | 29.2 | 100%
[5 empty] | 29.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17649.5328 | 284980.3738 | 29.22 | 100%
[5 empty] | 29.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17672.2942 | 285347.8933 | 29.24 | 100%
[5 empty] | 29.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17695.0555 | 285715.4129 | 29.26 | 100%
[5 empty] | 29.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17717.8169 | 286082.9324 | 29.28 | 100%
[5 empty] | 29.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17740.5783 | 286450.4519 | 29.3 | 100%
[5 empty] | 29.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17763.3397 | 286817.9714 | 29.32 | 100%
[5 empty] | 29.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17786.1011 | 287185.4909 | 29.34 | 100%
[5 empty] | 29.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17808.8625 | 287553.0105 | 29.36 | 100%
[5 empty] | 29.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17831.6238 | 287920.53 | 29.38 | 100%
[5 empty] | 29.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17854.3852 | 288288.0495 | 29.4 | 100%
[5 empty] | 29.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17877.1466 | 288655.569 | 29.42 | 100%
[5 empty] | 29.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17899.908 | 289023.0885 | 29.44 | 100%
[5 empty] | 29.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17922.6694 | 289390.6081 | 29.46 | 100%
[5 empty] | 29.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17945.4308 | 289758.1276 | 29.48 | 100%
[5 empty] | 29.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17968.1922 | 290125.6471 | 29.5 | 100%
[5 empty] | 29.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 17990.9535 | 290493.1666 | 29.52 | 100%
[5 empty] | 29.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18013.7149 | 290860.6861 | 29.54 | 100%
[5 empty] | 29.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18036.4763 | 291228.2057 | 29.56 | 100%
[5 empty] | 29.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18059.2377 | 291595.7252 | 29.58 | 100%
[5 empty] | 29.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18081.9991 | 291963.2447 | 29.6 | 100%
[5 empty] | 29.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18104.7605 | 292330.7642 | 29.62 | 100%
[5 empty] | 29.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18127.5218 | 292698.2837 | 29.64 | 100%
[5 empty] | 29.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18150.2832 | 293065.8033 | 29.66 | 100%
[5 empty] | 29.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18173.0446 | 293433.3228 | 29.68 | 100%
[5 empty] | 29.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18195.806 | 293800.8423 | 29.7 | 100%
[5 empty] | 29.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18218.5674 | 294168.3618 | 29.72 | 100%
[5 empty] | 29.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18241.3288 | 294535.8813 | 29.74 | 100%
[5 empty] | 29.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18264.0902 | 294903.4009 | 29.76 | 100%
[5 empty] | 29.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18286.8515 | 295270.9204 | 29.78 | 100%
[5 empty] | 29.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18309.6129 | 295638.4399 | 29.8 | 100%
[5 empty] | 29.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18332.3743 | 296005.9594 | 29.82 | 100%
[5 empty] | 29.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18355.1357 | 296373.4789 | 29.84 | 100%
[5 empty] | 29.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18377.8971 | 296740.9985 | 29.86 | 100%
[5 empty] | 29.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18400.6585 | 297108.518 | 29.88 | 100%
[5 empty] | 29.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18423.4198 | 297476.0375 | 29.9 | 100%
[5 empty] | 29.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18446.1812 | 297843.557 | 29.92 | 100%
[5 empty] | 29.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18468.9426 | 298211.0765 | 29.94 | 100%
[5 empty] | 29.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18491.704 | 298578.5961 | 29.96 | 100%
[5 empty] | 29.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18514.4654 | 298946.1156 | 29.98 | 100%
[5 empty] | 30 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18537.2268 | 299313.6351 | 30 | 100%
[5 empty] | 30.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18559.9881 | 299681.1546 | 30.02 | 100%
[5 empty] | 30.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18582.7495 | 300048.6741 | 30.04 | 100%
[5 empty] | 30.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18605.5109 | 300416.1937 | 30.06 | 100%
[5 empty] | 30.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18628.2723 | 300783.7132 | 30.08 | 100%
[5 empty] | 30.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18651.0337 | 301151.2327 | 30.1 | 100%
[5 empty] | 30.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18673.7951 | 301518.7522 | 30.12 | 100%
[5 empty] | 30.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18696.5565 | 301886.2717 | 30.14 | 100%
[5 empty] | 30.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18719.3178 | 302253.7913 | 30.16 | 100%
[5 empty] | 30.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18742.0792 | 302621.3108 | 30.18 | 100%
[5 empty] | 30.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18764.8406 | 302988.8303 | 30.2 | 100%
[5 empty] | 30.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18787.602 | 303356.3498 | 30.22 | 100%
[5 empty] | 30.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18810.3634 | 303723.8693 | 30.24 | 100%
[5 empty] | 30.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18833.1248 | 304091.3889 | 30.26 | 100%
[5 empty] | 30.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18855.8861 | 304458.9084 | 30.28 | 100%
[5 empty] | 30.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18878.6475 | 304826.4279 | 30.3 | 100%
[5 empty] | 30.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18901.4089 | 305193.9474 | 30.32 | 100%
[5 empty] | 30.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18924.1703 | 305561.4669 | 30.34 | 100%
[5 empty] | 30.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18946.9317 | 305928.9865 | 30.36 | 100%
[5 empty] | 30.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18969.6931 | 306296.506 | 30.38 | 100%
[5 empty] | 30.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 18992.4545 | 306664.0255 | 30.4 | 100%
[5 empty] | 30.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19015.2158 | 307031.545 | 30.42 | 100%
[5 empty] | 30.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19037.9772 | 307399.0645 | 30.44 | 100%
[5 empty] | 30.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19060.7386 | 307766.5841 | 30.46 | 100%
[5 empty] | 30.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19083.5 | 308134.1036 | 30.48 | 100%
[5 empty] | 30.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19106.2614 | 308501.6231 | 30.5 | 100%
[5 empty] | 30.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19129.0228 | 308869.1426 | 30.52 | 100%
[5 empty] | 30.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19151.7841 | 309236.6621 | 30.54 | 100%
[5 empty] | 30.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19174.5455 | 309604.1817 | 30.56 | 100%
[5 empty] | 30.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19197.3069 | 309971.7012 | 30.58 | 100%
[5 empty] | 30.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19220.0683 | 310339.2207 | 30.6 | 100%
[5 empty] | 30.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19242.8297 | 310706.7402 | 30.62 | 100%
[5 empty] | 30.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19265.5911 | 311074.2597 | 30.64 | 100%
[5 empty] | 30.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19288.3524 | 311441.7793 | 30.66 | 100%
[5 empty] | 30.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19311.1138 | 311809.2988 | 30.68 | 100%
[5 empty] | 30.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19333.8752 | 312176.8183 | 30.7 | 100%
[5 empty] | 30.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19356.6366 | 312544.3378 | 30.72 | 100%
[5 empty] | 30.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19379.398 | 312911.8573 | 30.74 | 100%
[5 empty] | 30.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19402.1594 | 313279.3769 | 30.76 | 100%
[5 empty] | 30.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19424.9208 | 313646.8964 | 30.78 | 100%
[5 empty] | 30.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19447.6821 | 314014.4159 | 30.8 | 100%
[5 empty] | 30.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19470.4435 | 314381.9354 | 30.82 | 100%
[5 empty] | 30.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19493.2049 | 314749.4549 | 30.84 | 100%
[5 empty] | 30.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19515.9663 | 315116.9745 | 30.86 | 100%
[5 empty] | 30.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19538.7277 | 315484.494 | 30.88 | 100%
[5 empty] | 30.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19561.4891 | 315852.0135 | 30.9 | 100%
[5 empty] | 30.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19584.2504 | 316219.533 | 30.92 | 100%
[5 empty] | 30.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19607.0118 | 316587.0525 | 30.94 | 100%
[5 empty] | 30.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19629.7732 | 316954.5721 | 30.96 | 100%
[5 empty] | 30.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19652.5346 | 317322.0916 | 30.98 | 100%
[5 empty] | 31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19675.296 | 317689.6111 | 31 | 100%
[5 empty] | 31.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19698.0574 | 318057.1306 | 31.02 | 100%
[5 empty] | 31.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19720.8187 | 318424.6501 | 31.04 | 100%
[5 empty] | 31.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19743.5801 | 318792.1697 | 31.06 | 100%
[5 empty] | 31.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19766.3415 | 319159.6892 | 31.08 | 100%
[5 empty] | 31.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19789.1029 | 319527.2087 | 31.1 | 100%
[5 empty] | 31.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19811.8643 | 319894.7282 | 31.12 | 100%
[5 empty] | 31.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19834.6257 | 320262.2477 | 31.14 | 100%
[5 empty] | 31.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19857.3871 | 320629.7673 | 31.16 | 100%
[5 empty] | 31.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19880.1484 | 320997.2868 | 31.18 | 100%
[5 empty] | 31.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19902.9098 | 321364.8063 | 31.2 | 100%
[5 empty] | 31.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19925.6712 | 321732.3258 | 31.22 | 100%
[5 empty] | 31.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19948.4326 | 322099.8453 | 31.24 | 100%
[5 empty] | 31.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19971.194 | 322467.3649 | 31.26 | 100%
[5 empty] | 31.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 19993.9554 | 322834.8844 | 31.28 | 100%
[5 empty] | 31.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20016.7167 | 323202.4039 | 31.3 | 100%
[5 empty] | 31.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20039.4781 | 323569.9234 | 31.32 | 100%
[5 empty] | 31.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20062.2395 | 323937.4429 | 31.34 | 100%
[5 empty] | 31.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20085.0009 | 324304.9625 | 31.36 | 100%
[5 empty] | 31.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20107.7623 | 324672.482 | 31.38 | 100%
[5 empty] | 31.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20130.5237 | 325040.0015 | 31.4 | 100%
[5 empty] | 31.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20153.2851 | 325407.521 | 31.42 | 100%
[5 empty] | 31.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20176.0464 | 325775.0405 | 31.44 | 100%
[5 empty] | 31.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20198.8078 | 326142.5601 | 31.46 | 100%
[5 empty] | 31.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20221.5692 | 326510.0796 | 31.48 | 100%
[5 empty] | 31.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20244.3306 | 326877.5991 | 31.5 | 100%
[5 empty] | 31.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20267.092 | 327245.1186 | 31.52 | 100%
[5 empty] | 31.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20289.8534 | 327612.6381 | 31.54 | 100%
[5 empty] | 31.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20312.6147 | 327980.1577 | 31.56 | 100%
[5 empty] | 31.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20335.3761 | 328347.6772 | 31.58 | 100%
[5 empty] | 31.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20358.1375 | 328715.1967 | 31.6 | 100%
[5 empty] | 31.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20380.8989 | 329082.7162 | 31.62 | 100%
[5 empty] | 31.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20403.6603 | 329450.2357 | 31.64 | 100%
[5 empty] | 31.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20426.4217 | 329817.7553 | 31.66 | 100%
[5 empty] | 31.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20449.183 | 330185.2748 | 31.68 | 100%
[5 empty] | 31.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20471.9444 | 330552.7943 | 31.7 | 100%
[5 empty] | 31.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20494.7058 | 330920.3138 | 31.72 | 100%
[5 empty] | 31.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20517.4672 | 331287.8333 | 31.74 | 100%
[5 empty] | 31.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20540.2286 | 331655.3529 | 31.76 | 100%
[5 empty] | 31.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20562.99 | 332022.8724 | 31.78 | 100%
[5 empty] | 31.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20585.7514 | 332390.3919 | 31.8 | 100%
[5 empty] | 31.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20608.5127 | 332757.9114 | 31.82 | 100%
[5 empty] | 31.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20631.2741 | 333125.4309 | 31.84 | 100%
[5 empty] | 31.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20654.0355 | 333492.9505 | 31.86 | 100%
[5 empty] | 31.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20676.7969 | 333860.47 | 31.88 | 100%
[5 empty] | 31.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20699.5583 | 334227.9895 | 31.9 | 100%
[5 empty] | 31.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20722.3197 | 334595.509 | 31.92 | 100%
[5 empty] | 31.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20745.081 | 334963.0285 | 31.94 | 100%
[5 empty] | 31.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20767.8424 | 335330.5481 | 31.96 | 100%
[5 empty] | 31.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20790.6038 | 335698.0676 | 31.98 | 100%
[5 empty] | 32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20813.3652 | 336065.5871 | 32 | 100%
[5 empty] | 32.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20836.1266 | 336433.1066 | 32.02 | 100%
[5 empty] | 32.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20858.888 | 336800.6261 | 32.04 | 100%
[5 empty] | 32.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20881.6493 | 337168.1457 | 32.06 | 100%
[5 empty] | 32.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20904.4107 | 337535.6652 | 32.08 | 100%
[5 empty] | 32.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20927.1721 | 337903.1847 | 32.1 | 100%
[5 empty] | 32.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20949.9335 | 338270.7042 | 32.12 | 100%
[5 empty] | 32.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20972.6949 | 338638.2237 | 32.14 | 100%
[5 empty] | 32.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 20995.4563 | 339005.7433 | 32.16 | 100%
[5 empty] | 32.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21018.2177 | 339373.2628 | 32.18 | 100%
[5 empty] | 32.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21040.979 | 339740.7823 | 32.2 | 100%
[5 empty] | 32.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21063.7404 | 340108.3018 | 32.22 | 100%
[5 empty] | 32.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21086.5018 | 340475.8213 | 32.24 | 100%
[5 empty] | 32.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21109.2632 | 340843.3409 | 32.26 | 100%
[5 empty] | 32.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21132.0246 | 341210.8604 | 32.28 | 100%
[5 empty] | 32.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21154.786 | 341578.3799 | 32.3 | 100%
[5 empty] | 32.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21177.5473 | 341945.8994 | 32.32 | 100%
[5 empty] | 32.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21200.3087 | 342313.4189 | 32.34 | 100%
[5 empty] | 32.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21223.0701 | 342680.9385 | 32.36 | 100%
[5 empty] | 32.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21245.8315 | 343048.458 | 32.38 | 100%
[5 empty] | 32.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21268.5929 | 343415.9775 | 32.4 | 100%
[5 empty] | 32.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21291.3543 | 343783.497 | 32.42 | 100%
[5 empty] | 32.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21314.1157 | 344151.0165 | 32.44 | 100%
[5 empty] | 32.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21336.877 | 344518.5361 | 32.46 | 100%
[5 empty] | 32.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21359.6384 | 344886.0556 | 32.48 | 100%
[5 empty] | 32.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21382.3998 | 345253.5751 | 32.5 | 100%
[5 empty] | 32.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21405.1612 | 345621.0946 | 32.52 | 100%
[5 empty] | 32.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21427.9226 | 345988.6141 | 32.54 | 100%
[5 empty] | 32.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21450.684 | 346356.1337 | 32.56 | 100%
[5 empty] | 32.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21473.4453 | 346723.6532 | 32.58 | 100%
[5 empty] | 32.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21496.2067 | 347091.1727 | 32.6 | 100%
[5 empty] | 32.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21518.9681 | 347458.6922 | 32.62 | 100%
[5 empty] | 32.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21541.7295 | 347826.2117 | 32.64 | 100%
[5 empty] | 32.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21564.4909 | 348193.7313 | 32.66 | 100%
[5 empty] | 32.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21587.2523 | 348561.2508 | 32.68 | 100%
[5 empty] | 32.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21610.0136 | 348928.7703 | 32.7 | 100%
[5 empty] | 32.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21632.775 | 349296.2898 | 32.72 | 100%
[5 empty] | 32.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21655.5364 | 349663.8093 | 32.74 | 100%
[5 empty] | 32.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21678.2978 | 350031.3289 | 32.76 | 100%
[5 empty] | 32.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21701.0592 | 350398.8484 | 32.78 | 100%
[5 empty] | 32.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21723.8206 | 350766.3679 | 32.8 | 100%
[5 empty] | 32.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21746.582 | 351133.8874 | 32.82 | 100%
[5 empty] | 32.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21769.3433 | 351501.4069 | 32.84 | 100%
[5 empty] | 32.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21792.1047 | 351868.9265 | 32.86 | 100%
[5 empty] | 32.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21814.8661 | 352236.446 | 32.88 | 100%
[5 empty] | 32.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21837.6275 | 352603.9655 | 32.9 | 100%
[5 empty] | 32.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21860.3889 | 352971.485 | 32.92 | 100%
[5 empty] | 32.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21883.1503 | 353339.0045 | 32.94 | 100%
[5 empty] | 32.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21905.9116 | 353706.5241 | 32.96 | 100%
[5 empty] | 32.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21928.673 | 354074.0436 | 32.98 | 100%
[5 empty] | 33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21951.4344 | 354441.5631 | 33 | 100%
[5 empty] | 33.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21974.1958 | 354809.0826 | 33.02 | 100%
[5 empty] | 33.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 21996.9572 | 355176.6021 | 33.04 | 100%
[5 empty] | 33.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22019.7186 | 355544.1217 | 33.06 | 100%
[5 empty] | 33.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22042.48 | 355911.6412 | 33.08 | 100%
[5 empty] | 33.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22065.2413 | 356279.1607 | 33.1 | 100%
[5 empty] | 33.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22088.0027 | 356646.6802 | 33.12 | 100%
[5 empty] | 33.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22110.7641 | 357014.1997 | 33.14 | 100%
[5 empty] | 33.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22133.5255 | 357381.7193 | 33.16 | 100%
[5 empty] | 33.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22156.2869 | 357749.2388 | 33.18 | 100%
[5 empty] | 33.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22179.0483 | 358116.7583 | 33.2 | 100%
[5 empty] | 33.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22201.8096 | 358484.2778 | 33.22 | 100%
[5 empty] | 33.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22224.571 | 358851.7973 | 33.24 | 100%
[5 empty] | 33.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22247.3324 | 359219.3169 | 33.26 | 100%
[5 empty] | 33.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22270.0938 | 359586.8364 | 33.28 | 100%
[5 empty] | 33.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22292.8552 | 359954.3559 | 33.3 | 100%
[5 empty] | 33.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22315.6166 | 360321.8754 | 33.32 | 100%
[5 empty] | 33.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22338.3779 | 360689.3949 | 33.34 | 100%
[5 empty] | 33.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22361.1393 | 361056.9145 | 33.36 | 100%
[5 empty] | 33.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22383.9007 | 361424.434 | 33.38 | 100%
[5 empty] | 33.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22406.6621 | 361791.9535 | 33.4 | 100%
[5 empty] | 33.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22429.4235 | 362159.473 | 33.42 | 100%
[5 empty] | 33.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22452.1849 | 362526.9925 | 33.44 | 100%
[5 empty] | 33.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22474.9463 | 362894.5121 | 33.46 | 100%
[5 empty] | 33.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22497.7076 | 363262.0316 | 33.48 | 100%
[5 empty] | 33.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22520.469 | 363629.5511 | 33.5 | 100%
[5 empty] | 33.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22543.2304 | 363997.0706 | 33.52 | 100%
[5 empty] | 33.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22565.9918 | 364364.5901 | 33.54 | 100%
[5 empty] | 33.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22588.7532 | 364732.1097 | 33.56 | 100%
[5 empty] | 33.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22611.5146 | 365099.6292 | 33.58 | 100%
[5 empty] | 33.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22634.2759 | 365467.1487 | 33.6 | 100%
[5 empty] | 33.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22657.0373 | 365834.6682 | 33.62 | 100%
[5 empty] | 33.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22679.7987 | 366202.1877 | 33.64 | 100%
[5 empty] | 33.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22702.5601 | 366569.7073 | 33.66 | 100%
[5 empty] | 33.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22725.3215 | 366937.2268 | 33.68 | 100%
[5 empty] | 33.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22748.0829 | 367304.7463 | 33.7 | 100%
[5 empty] | 33.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22770.8442 | 367672.2658 | 33.72 | 100%
[5 empty] | 33.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22793.6056 | 368039.7853 | 33.74 | 100%
[5 empty] | 33.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22816.367 | 368407.3049 | 33.76 | 100%
[5 empty] | 33.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22839.1284 | 368774.8244 | 33.78 | 100%
[5 empty] | 33.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22861.8898 | 369142.3439 | 33.8 | 100%
[5 empty] | 33.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22884.6512 | 369509.8634 | 33.82 | 100%
[5 empty] | 33.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22907.4126 | 369877.3829 | 33.84 | 100%
[5 empty] | 33.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22930.1739 | 370244.9025 | 33.86 | 100%
[5 empty] | 33.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22952.9353 | 370612.422 | 33.88 | 100%
[5 empty] | 33.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22975.6967 | 370979.9415 | 33.9 | 100%
[5 empty] | 33.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 22998.4581 | 371347.461 | 33.92 | 100%
[5 empty] | 33.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23021.2195 | 371714.9805 | 33.94 | 100%
[5 empty] | 33.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23043.9809 | 372082.5001 | 33.96 | 100%
[5 empty] | 33.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23066.7422 | 372450.0196 | 33.98 | 100%
[5 empty] | 34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23089.5036 | 372817.5391 | 34 | 100%
[5 empty] | 34.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23112.265 | 373185.0586 | 34.02 | 100%
[5 empty] | 34.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23135.0264 | 373552.5781 | 34.04 | 100%
[5 empty] | 34.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23157.7878 | 373920.0977 | 34.06 | 100%
[5 empty] | 34.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23180.5492 | 374287.6172 | 34.08 | 100%
[5 empty] | 34.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23203.3106 | 374655.1367 | 34.1 | 100%
[5 empty] | 34.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23226.0719 | 375022.6562 | 34.12 | 100%
[5 empty] | 34.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23248.8333 | 375390.1757 | 34.14 | 100%
[5 empty] | 34.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23271.5947 | 375757.6953 | 34.16 | 100%
[5 empty] | 34.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23294.3561 | 376125.2148 | 34.18 | 100%
[5 empty] | 34.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23317.1175 | 376492.7343 | 34.2 | 100%
[5 empty] | 34.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23339.8789 | 376860.2538 | 34.22 | 100%
[5 empty] | 34.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23362.6402 | 377227.7733 | 34.24 | 100%
[5 empty] | 34.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23385.4016 | 377595.2929 | 34.26 | 100%
[5 empty] | 34.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23408.163 | 377962.8124 | 34.28 | 100%
[5 empty] | 34.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23430.9244 | 378330.3319 | 34.3 | 100%
[5 empty] | 34.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23453.6858 | 378697.8514 | 34.32 | 100%
[5 empty] | 34.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23476.4472 | 379065.3709 | 34.34 | 100%
[5 empty] | 34.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23499.2085 | 379432.8905 | 34.36 | 100%
[5 empty] | 34.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23521.9699 | 379800.41 | 34.38 | 100%
[5 empty] | 34.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23544.7313 | 380167.9295 | 34.4 | 100%
[5 empty] | 34.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23567.4927 | 380535.449 | 34.42 | 100%
[5 empty] | 34.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23590.2541 | 380902.9685 | 34.44 | 100%
[5 empty] | 34.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23613.0155 | 381270.4881 | 34.46 | 100%
[5 empty] | 34.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23635.7769 | 381638.0076 | 34.48 | 100%
[5 empty] | 34.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23658.5382 | 382005.5271 | 34.5 | 100%
[5 empty] | 34.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23681.2996 | 382373.0466 | 34.52 | 100%
[5 empty] | 34.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23704.061 | 382740.5661 | 34.54 | 100%
[5 empty] | 34.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23726.8224 | 383108.0857 | 34.56 | 100%
[5 empty] | 34.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23749.5838 | 383475.6052 | 34.58 | 100%
[5 empty] | 34.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23772.3452 | 383843.1247 | 34.6 | 100%
[5 empty] | 34.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23795.1065 | 384210.6442 | 34.62 | 100%
[5 empty] | 34.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23817.8679 | 384578.1637 | 34.64 | 100%
[5 empty] | 34.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23840.6293 | 384945.6833 | 34.66 | 100%
[5 empty] | 34.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23863.3907 | 385313.2028 | 34.68 | 100%
[5 empty] | 34.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23886.1521 | 385680.7223 | 34.7 | 100%
[5 empty] | 34.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23908.9135 | 386048.2418 | 34.72 | 100%
[5 empty] | 34.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23931.6748 | 386415.7613 | 34.74 | 100%
[5 empty] | 34.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23954.4362 | 386783.2809 | 34.76 | 100%
[5 empty] | 34.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23977.1976 | 387150.8004 | 34.78 | 100%
[5 empty] | 34.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 23999.959 | 387518.3199 | 34.8 | 100%
[5 empty] | 34.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24022.7204 | 387885.8394 | 34.82 | 100%
[5 empty] | 34.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24045.4818 | 388253.3589 | 34.84 | 100%
[5 empty] | 34.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24068.2432 | 388620.8785 | 34.86 | 100%
[5 empty] | 34.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24091.0045 | 388988.398 | 34.88 | 100%
[5 empty] | 34.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24113.7659 | 389355.9175 | 34.9 | 100%
[5 empty] | 34.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24136.5273 | 389723.437 | 34.92 | 100%
[5 empty] | 34.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24159.2887 | 390090.9565 | 34.94 | 100%
[5 empty] | 34.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24182.0501 | 390458.4761 | 34.96 | 100%
[5 empty] | 34.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24204.8115 | 390825.9956 | 34.98 | 100%
[5 empty] | 35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24227.5728 | 391193.5151 | 35 | 100%
[5 empty] | 35.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24250.3342 | 391561.0346 | 35.02 | 100%
[5 empty] | 35.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24273.0956 | 391928.5541 | 35.04 | 100%
[5 empty] | 35.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24295.857 | 392296.0737 | 35.06 | 100%
[5 empty] | 35.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24318.6184 | 392663.5932 | 35.08 | 100%
[5 empty] | 35.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24341.3798 | 393031.1127 | 35.1 | 100%
[5 empty] | 35.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24364.1412 | 393398.6322 | 35.12 | 100%
[5 empty] | 35.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24386.9025 | 393766.1517 | 35.14 | 100%
[5 empty] | 35.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24409.6639 | 394133.6713 | 35.16 | 100%
[5 empty] | 35.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24432.4253 | 394501.1908 | 35.18 | 100%
[5 empty] | 35.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24455.1867 | 394868.7103 | 35.2 | 100%
[5 empty] | 35.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24477.9481 | 395236.2298 | 35.22 | 100%
[5 empty] | 35.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24500.7095 | 395603.7493 | 35.24 | 100%
[5 empty] | 35.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24523.4708 | 395971.2689 | 35.26 | 100%
[5 empty] | 35.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24546.2322 | 396338.7884 | 35.28 | 100%
[5 empty] | 35.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24568.9936 | 396706.3079 | 35.3 | 100%
[5 empty] | 35.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24591.755 | 397073.8274 | 35.32 | 100%
[5 empty] | 35.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24614.5164 | 397441.3469 | 35.34 | 100%
[5 empty] | 35.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24637.2778 | 397808.8665 | 35.36 | 100%
[5 empty] | 35.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24660.0391 | 398176.386 | 35.38 | 100%
[5 empty] | 35.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24682.8005 | 398543.9055 | 35.4 | 100%
[5 empty] | 35.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24705.5619 | 398911.425 | 35.42 | 100%
[5 empty] | 35.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24728.3233 | 399278.9445 | 35.44 | 100%
[5 empty] | 35.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24751.0847 | 399646.4641 | 35.46 | 100%
[5 empty] | 35.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24773.8461 | 400013.9836 | 35.48 | 100%
[5 empty] | 35.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24796.6075 | 400381.5031 | 35.5 | 100%
[5 empty] | 35.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24819.3688 | 400749.0226 | 35.52 | 100%
[5 empty] | 35.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24842.1302 | 401116.5421 | 35.54 | 100%
[5 empty] | 35.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24864.8916 | 401484.0617 | 35.56 | 100%
[5 empty] | 35.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24887.653 | 401851.5812 | 35.58 | 100%
[5 empty] | 35.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24910.4144 | 402219.1007 | 35.6 | 100%
[5 empty] | 35.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24933.1758 | 402586.6202 | 35.62 | 100%
[5 empty] | 35.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24955.9371 | 402954.1397 | 35.64 | 100%
[5 empty] | 35.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 24978.6985 | 403321.6593 | 35.66 | 100%
[5 empty] | 35.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25001.4599 | 403689.1788 | 35.68 | 100%
[5 empty] | 35.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25024.2213 | 404056.6983 | 35.7 | 100%
[5 empty] | 35.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25046.9827 | 404424.2178 | 35.72 | 100%
[5 empty] | 35.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25069.7441 | 404791.7373 | 35.74 | 100%
[5 empty] | 35.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25092.5054 | 405159.2569 | 35.76 | 100%
[5 empty] | 35.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25115.2668 | 405526.7764 | 35.78 | 100%
[5 empty] | 35.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25138.0282 | 405894.2959 | 35.8 | 100%
[5 empty] | 35.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25160.7896 | 406261.8154 | 35.82 | 100%
[5 empty] | 35.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25183.551 | 406629.3349 | 35.84 | 100%
[5 empty] | 35.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25206.3124 | 406996.8545 | 35.86 | 100%
[5 empty] | 35.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25229.0738 | 407364.374 | 35.88 | 100%
[5 empty] | 35.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25251.8351 | 407731.8935 | 35.9 | 100%
[5 empty] | 35.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25274.5965 | 408099.413 | 35.92 | 100%
[5 empty] | 35.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25297.3579 | 408466.9325 | 35.94 | 100%
[5 empty] | 35.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25320.1193 | 408834.4521 | 35.96 | 100%
[5 empty] | 35.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25342.8807 | 409201.9716 | 35.98 | 100%
[5 empty] | 36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25365.6421 | 409569.4911 | 36 | 100%
[5 empty] | 36.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25388.4034 | 409937.0106 | 36.02 | 100%
[5 empty] | 36.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25411.1648 | 410304.5301 | 36.04 | 100%
[5 empty] | 36.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25433.9262 | 410672.0497 | 36.06 | 100%
[5 empty] | 36.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25456.6876 | 411039.5692 | 36.08 | 100%
[5 empty] | 36.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25479.449 | 411407.0887 | 36.1 | 100%
[5 empty] | 36.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25502.2104 | 411774.6082 | 36.12 | 100%
[5 empty] | 36.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25524.9718 | 412142.1277 | 36.14 | 100%
[5 empty] | 36.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25547.7331 | 412509.6473 | 36.16 | 100%
[5 empty] | 36.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25570.4945 | 412877.1668 | 36.18 | 100%
[5 empty] | 36.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25593.2559 | 413244.6863 | 36.2 | 100%
[5 empty] | 36.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25616.0173 | 413612.2058 | 36.22 | 100%
[5 empty] | 36.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25638.7787 | 413979.7253 | 36.24 | 100%
[5 empty] | 36.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25661.5401 | 414347.2449 | 36.26 | 100%
[5 empty] | 36.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25684.3014 | 414714.7644 | 36.28 | 100%
[5 empty] | 36.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25707.0628 | 415082.2839 | 36.3 | 100%
[5 empty] | 36.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25729.8242 | 415449.8034 | 36.32 | 100%
[5 empty] | 36.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25752.5856 | 415817.3229 | 36.34 | 100%
[5 empty] | 36.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25775.347 | 416184.8425 | 36.36 | 100%
[5 empty] | 36.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25798.1084 | 416552.362 | 36.38 | 100%
[5 empty] | 36.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25820.8697 | 416919.8815 | 36.4 | 100%
[5 empty] | 36.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25843.6311 | 417287.401 | 36.42 | 100%
[5 empty] | 36.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25866.3925 | 417654.9205 | 36.44 | 100%
[5 empty] | 36.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25889.1539 | 418022.4401 | 36.46 | 100%
[5 empty] | 36.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25911.9153 | 418389.9596 | 36.48 | 100%
[5 empty] | 36.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25934.6767 | 418757.4791 | 36.5 | 100%
[5 empty] | 36.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25957.4381 | 419124.9986 | 36.52 | 100%
[5 empty] | 36.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 25980.1994 | 419492.5181 | 36.54 | 100%
[5 empty] | 36.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26002.9608 | 419860.0377 | 36.56 | 100%
[5 empty] | 36.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26025.7222 | 420227.5572 | 36.58 | 100%
[5 empty] | 36.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26048.4836 | 420595.0767 | 36.6 | 100%
[5 empty] | 36.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26071.245 | 420962.5962 | 36.62 | 100%
[5 empty] | 36.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26094.0064 | 421330.1157 | 36.64 | 100%
[5 empty] | 36.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26116.7677 | 421697.6353 | 36.66 | 100%
[5 empty] | 36.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26139.5291 | 422065.1548 | 36.68 | 100%
[5 empty] | 36.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26162.2905 | 422432.6743 | 36.7 | 100%
[5 empty] | 36.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26185.0519 | 422800.1938 | 36.72 | 100%
[5 empty] | 36.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26207.8133 | 423167.7133 | 36.74 | 100%
[5 empty] | 36.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26230.5747 | 423535.2329 | 36.76 | 100%
[5 empty] | 36.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26253.3361 | 423902.7524 | 36.78 | 100%
[5 empty] | 36.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26276.0974 | 424270.2719 | 36.8 | 100%
[5 empty] | 36.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26298.8588 | 424637.7914 | 36.82 | 100%
[5 empty] | 36.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26321.6202 | 425005.3109 | 36.84 | 100%
[5 empty] | 36.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26344.3816 | 425372.8305 | 36.86 | 100%
[5 empty] | 36.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26367.143 | 425740.35 | 36.88 | 100%
[5 empty] | 36.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26389.9044 | 426107.8695 | 36.9 | 100%
[5 empty] | 36.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26412.6657 | 426475.389 | 36.92 | 100%
[5 empty] | 36.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26435.4271 | 426842.9085 | 36.94 | 100%
[5 empty] | 36.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26458.1885 | 427210.4281 | 36.96 | 100%
[5 empty] | 36.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26480.9499 | 427577.9476 | 36.98 | 100%
[5 empty] | 37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26503.7113 | 427945.4671 | 37 | 100%
[5 empty] | 37.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26526.4727 | 428312.9866 | 37.02 | 100%
[5 empty] | 37.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26549.234 | 428680.5061 | 37.04 | 100%
[5 empty] | 37.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26571.9954 | 429048.0257 | 37.06 | 100%
[5 empty] | 37.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26594.7568 | 429415.5452 | 37.08 | 100%
[5 empty] | 37.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26617.5182 | 429783.0647 | 37.1 | 100%
[5 empty] | 37.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26640.2796 | 430150.5842 | 37.12 | 100%
[5 empty] | 37.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26663.041 | 430518.1037 | 37.14 | 100%
[5 empty] | 37.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26685.8024 | 430885.6233 | 37.16 | 100%
[5 empty] | 37.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26708.5637 | 431253.1428 | 37.18 | 100%
[5 empty] | 37.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26731.3251 | 431620.6623 | 37.2 | 100%
[5 empty] | 37.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26754.0865 | 431988.1818 | 37.22 | 100%
[5 empty] | 37.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26776.8479 | 432355.7013 | 37.24 | 100%
[5 empty] | 37.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26799.6093 | 432723.2209 | 37.26 | 100%
[5 empty] | 37.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26822.3707 | 433090.7404 | 37.28 | 100%
[5 empty] | 37.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26845.132 | 433458.2599 | 37.3 | 100%
[5 empty] | 37.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26867.8934 | 433825.7794 | 37.32 | 100%
[5 empty] | 37.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26890.6548 | 434193.2989 | 37.34 | 100%
[5 empty] | 37.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26913.4162 | 434560.8185 | 37.36 | 100%
[5 empty] | 37.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26936.1776 | 434928.338 | 37.38 | 100%
[5 empty] | 37.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26958.939 | 435295.8575 | 37.4 | 100%
[5 empty] | 37.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 26981.7003 | 435663.377 | 37.42 | 100%
[5 empty] | 37.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27004.4617 | 436030.8965 | 37.44 | 100%
[5 empty] | 37.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27027.2231 | 436398.4161 | 37.46 | 100%
[5 empty] | 37.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27049.9845 | 436765.9356 | 37.48 | 100%
[5 empty] | 37.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27072.7459 | 437133.4551 | 37.5 | 100%
[5 empty] | 37.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27095.5073 | 437500.9746 | 37.52 | 100%
[5 empty] | 37.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27118.2687 | 437868.4941 | 37.54 | 100%
[5 empty] | 37.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27141.03 | 438236.0137 | 37.56 | 100%
[5 empty] | 37.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27163.7914 | 438603.5332 | 37.58 | 100%
[5 empty] | 37.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27186.5528 | 438971.0527 | 37.6 | 100%
[5 empty] | 37.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27209.3142 | 439338.5722 | 37.62 | 100%
[5 empty] | 37.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27232.0756 | 439706.0917 | 37.64 | 100%
[5 empty] | 37.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27254.837 | 440073.6113 | 37.66 | 100%
[5 empty] | 37.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27277.5983 | 440441.1308 | 37.68 | 100%
[5 empty] | 37.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27300.3597 | 440808.6503 | 37.7 | 100%
[5 empty] | 37.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27323.1211 | 441176.1698 | 37.72 | 100%
[5 empty] | 37.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27345.8825 | 441543.6893 | 37.74 | 100%
[5 empty] | 37.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27368.6439 | 441911.2089 | 37.76 | 100%
[5 empty] | 37.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27391.4053 | 442278.7284 | 37.78 | 100%
[5 empty] | 37.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27414.1667 | 442646.2479 | 37.8 | 100%
[5 empty] | 37.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27436.928 | 443013.7674 | 37.82 | 100%
[5 empty] | 37.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27459.6894 | 443381.2869 | 37.84 | 100%
[5 empty] | 37.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27482.4508 | 443748.8065 | 37.86 | 100%
[5 empty] | 37.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27505.2122 | 444116.326 | 37.88 | 100%
[5 empty] | 37.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27527.9736 | 444483.8455 | 37.9 | 100%
[5 empty] | 37.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27550.735 | 444851.365 | 37.92 | 100%
[5 empty] | 37.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27573.4963 | 445218.8845 | 37.94 | 100%
[5 empty] | 37.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27596.2577 | 445586.4041 | 37.96 | 100%
[5 empty] | 37.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27619.0191 | 445953.9236 | 37.98 | 100%
[5 empty] | 38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27641.7805 | 446321.4431 | 38 | 100%
[5 empty] | 38.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27664.5419 | 446688.9626 | 38.02 | 100%
[5 empty] | 38.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27687.3033 | 447056.4821 | 38.04 | 100%
[5 empty] | 38.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27710.0646 | 447424.0017 | 38.06 | 100%
[5 empty] | 38.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27732.826 | 447791.5212 | 38.08 | 100%
[5 empty] | 38.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27755.5874 | 448159.0407 | 38.1 | 100%
[5 empty] | 38.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27778.3488 | 448526.5602 | 38.12 | 100%
[5 empty] | 38.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27801.1102 | 448894.0797 | 38.14 | 100%
[5 empty] | 38.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27823.8716 | 449261.5993 | 38.16 | 100%
[5 empty] | 38.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27846.633 | 449629.1188 | 38.18 | 100%
[5 empty] | 38.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27869.3943 | 449996.6383 | 38.2 | 100%
[5 empty] | 38.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27892.1557 | 450364.1578 | 38.22 | 100%
[5 empty] | 38.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27914.9171 | 450731.6773 | 38.24 | 100%
[5 empty] | 38.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27937.6785 | 451099.1969 | 38.26 | 100%
[5 empty] | 38.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27960.4399 | 451466.7164 | 38.28 | 100%
[5 empty] | 38.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 27983.2013 | 451834.2359 | 38.3 | 100%
[5 empty] | 38.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28005.9626 | 452201.7554 | 38.32 | 100%
[5 empty] | 38.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28028.724 | 452569.2749 | 38.34 | 100%
[5 empty] | 38.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28051.4854 | 452936.7945 | 38.36 | 100%
[5 empty] | 38.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28074.2468 | 453304.314 | 38.38 | 100%
[5 empty] | 38.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28097.0082 | 453671.8335 | 38.4 | 100%
[5 empty] | 38.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28119.7696 | 454039.353 | 38.42 | 100%
[5 empty] | 38.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28142.5309 | 454406.8725 | 38.44 | 100%
[5 empty] | 38.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28165.2923 | 454774.3921 | 38.46 | 100%
[5 empty] | 38.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28188.0537 | 455141.9116 | 38.48 | 100%
[5 empty] | 38.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28210.8151 | 455509.4311 | 38.5 | 100%
[5 empty] | 38.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28233.5765 | 455876.9506 | 38.52 | 100%
[5 empty] | 38.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28256.3379 | 456244.4701 | 38.54 | 100%
[5 empty] | 38.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28279.0993 | 456611.9897 | 38.56 | 100%
[5 empty] | 38.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28301.8606 | 456979.5092 | 38.58 | 100%
[5 empty] | 38.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28324.622 | 457347.0287 | 38.6 | 100%
[5 empty] | 38.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28347.3834 | 457714.5482 | 38.62 | 100%
[5 empty] | 38.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28370.1448 | 458082.0677 | 38.64 | 100%
[5 empty] | 38.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28392.9062 | 458449.5873 | 38.66 | 100%
[5 empty] | 38.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28415.6676 | 458817.1068 | 38.68 | 100%
[5 empty] | 38.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28438.4289 | 459184.6263 | 38.7 | 100%
[5 empty] | 38.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28461.1903 | 459552.1458 | 38.72 | 100%
[5 empty] | 38.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28483.9517 | 459919.6653 | 38.74 | 100%
[5 empty] | 38.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28506.7131 | 460287.1849 | 38.76 | 100%
[5 empty] | 38.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28529.4745 | 460654.7044 | 38.78 | 100%
[5 empty] | 38.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28552.2359 | 461022.2239 | 38.8 | 100%
[5 empty] | 38.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28574.9973 | 461389.7434 | 38.82 | 100%
[5 empty] | 38.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28597.7586 | 461757.2629 | 38.84 | 100%
[5 empty] | 38.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28620.52 | 462124.7825 | 38.86 | 100%
[5 empty] | 38.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28643.2814 | 462492.302 | 38.88 | 100%
[5 empty] | 38.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28666.0428 | 462859.8215 | 38.9 | 100%
[5 empty] | 38.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28688.8042 | 463227.341 | 38.92 | 100%
[5 empty] | 38.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28711.5656 | 463594.8605 | 38.94 | 100%
[5 empty] | 38.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28734.3269 | 463962.3801 | 38.96 | 100%
[5 empty] | 38.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28757.0883 | 464329.8996 | 38.98 | 100%
[5 empty] | 39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28779.8497 | 464697.4191 | 39 | 100%
[5 empty] | 39.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28802.6111 | 465064.9386 | 39.02 | 100%
[5 empty] | 39.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28825.3725 | 465432.4581 | 39.04 | 100%
[5 empty] | 39.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28848.1339 | 465799.9777 | 39.06 | 100%
[5 empty] | 39.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28870.8952 | 466167.4972 | 39.08 | 100%
[5 empty] | 39.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28893.6566 | 466535.0167 | 39.1 | 100%
[5 empty] | 39.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28916.418 | 466902.5362 | 39.12 | 100%
[5 empty] | 39.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28939.1794 | 467270.0557 | 39.14 | 100%
[5 empty] | 39.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28961.9408 | 467637.5753 | 39.16 | 100%
[5 empty] | 39.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 28984.7022 | 468005.0948 | 39.18 | 100%
[5 empty] | 39.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29007.4636 | 468372.6143 | 39.2 | 100%
[5 empty] | 39.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29030.2249 | 468740.1338 | 39.22 | 100%
[5 empty] | 39.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29052.9863 | 469107.6533 | 39.24 | 100%
[5 empty] | 39.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29075.7477 | 469475.1729 | 39.26 | 100%
[5 empty] | 39.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29098.5091 | 469842.6924 | 39.28 | 100%
[5 empty] | 39.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29121.2705 | 470210.2119 | 39.3 | 100%
[5 empty] | 39.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29144.0319 | 470577.7314 | 39.32 | 100%
[5 empty] | 39.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29166.7932 | 470945.2509 | 39.34 | 100%
[5 empty] | 39.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29189.5546 | 471312.7705 | 39.36 | 100%
[5 empty] | 39.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29212.316 | 471680.29 | 39.38 | 100%
[5 empty] | 39.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29235.0774 | 472047.8095 | 39.4 | 100%
[5 empty] | 39.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29257.8388 | 472415.329 | 39.42 | 100%
[5 empty] | 39.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29280.6002 | 472782.8485 | 39.44 | 100%
[5 empty] | 39.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29303.3615 | 473150.3681 | 39.46 | 100%
[5 empty] | 39.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29326.1229 | 473517.8876 | 39.48 | 100%
[5 empty] | 39.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29348.8843 | 473885.4071 | 39.5 | 100%
[5 empty] | 39.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29371.6457 | 474252.9266 | 39.52 | 100%
[5 empty] | 39.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29394.4071 | 474620.4461 | 39.54 | 100%
[5 empty] | 39.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29417.1685 | 474987.9657 | 39.56 | 100%
[5 empty] | 39.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29439.9299 | 475355.4852 | 39.58 | 100%
[5 empty] | 39.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29462.6912 | 475723.0047 | 39.6 | 100%
[5 empty] | 39.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29485.4526 | 476090.5242 | 39.62 | 100%
[5 empty] | 39.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29508.214 | 476458.0437 | 39.64 | 100%
[5 empty] | 39.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29530.9754 | 476825.5633 | 39.66 | 100%
[5 empty] | 39.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29553.7368 | 477193.0828 | 39.68 | 100%
[5 empty] | 39.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29576.4982 | 477560.6023 | 39.7 | 100%
[5 empty] | 39.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29599.2595 | 477928.1218 | 39.72 | 100%
[5 empty] | 39.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29622.0209 | 478295.6413 | 39.74 | 100%
[5 empty] | 39.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29644.7823 | 478663.1609 | 39.76 | 100%
[5 empty] | 39.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29667.5437 | 479030.6804 | 39.78 | 100%
[5 empty] | 39.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29690.3051 | 479398.1999 | 39.8 | 100%
[5 empty] | 39.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29713.0665 | 479765.7194 | 39.82 | 100%
[5 empty] | 39.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29735.8279 | 480133.2389 | 39.84 | 100%
[5 empty] | 39.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29758.5892 | 480500.7585 | 39.86 | 100%
[5 empty] | 39.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29781.3506 | 480868.278 | 39.88 | 100%
[5 empty] | 39.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29804.112 | 481235.7975 | 39.9 | 100%
[5 empty] | 39.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29826.8734 | 481603.317 | 39.92 | 100%
[5 empty] | 39.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29849.6348 | 481970.8365 | 39.94 | 100%
[5 empty] | 39.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29872.3962 | 482338.3561 | 39.96 | 100%
[5 empty] | 39.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29895.1575 | 482705.8756 | 39.98 | 100%
[5 empty] | 40 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29917.9189 | 483073.3951 | 40 | 100%
[5 empty] | 40.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29940.6803 | 483440.9146 | 40.02 | 100%
[5 empty] | 40.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29963.4417 | 483808.4341 | 40.04 | 100%
[5 empty] | 40.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 29986.2031 | 484175.9537 | 40.06 | 100%
[5 empty] | 40.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30008.9645 | 484543.4732 | 40.08 | 100%
[5 empty] | 40.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30031.7258 | 484910.9927 | 40.1 | 100%
[5 empty] | 40.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30054.4872 | 485278.5122 | 40.12 | 100%
[5 empty] | 40.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30077.2486 | 485646.0317 | 40.14 | 100%
[5 empty] | 40.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30100.01 | 486013.5513 | 40.16 | 100%
[5 empty] | 40.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30122.7714 | 486381.0708 | 40.18 | 100%
[5 empty] | 40.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30145.5328 | 486748.5903 | 40.2 | 100%
[5 empty] | 40.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30168.2942 | 487116.1098 | 40.22 | 100%
[5 empty] | 40.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30191.0555 | 487483.6293 | 40.24 | 100%
[5 empty] | 40.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30213.8169 | 487851.1489 | 40.26 | 100%
[5 empty] | 40.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30236.5783 | 488218.6684 | 40.28 | 100%
[5 empty] | 40.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30259.3397 | 488586.1879 | 40.3 | 100%
[5 empty] | 40.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30282.1011 | 488953.7074 | 40.32 | 100%
[5 empty] | 40.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30304.8625 | 489321.2269 | 40.34 | 100%
[5 empty] | 40.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30327.6238 | 489688.7465 | 40.36 | 100%
[5 empty] | 40.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30350.3852 | 490056.266 | 40.38 | 100%
[5 empty] | 40.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30373.1466 | 490423.7855 | 40.4 | 100%
[5 empty] | 40.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30395.908 | 490791.305 | 40.42 | 100%
[5 empty] | 40.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30418.6694 | 491158.8245 | 40.44 | 100%
[5 empty] | 40.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30441.4308 | 491526.3441 | 40.46 | 100%
[5 empty] | 40.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30464.1922 | 491893.8636 | 40.48 | 100%
[5 empty] | 40.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30486.9535 | 492261.3831 | 40.5 | 100%
[5 empty] | 40.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30509.7149 | 492628.9026 | 40.52 | 100%
[5 empty] | 40.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30532.4763 | 492996.4221 | 40.54 | 100%
[5 empty] | 40.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30555.2377 | 493363.9417 | 40.56 | 100%
[5 empty] | 40.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30577.9991 | 493731.4612 | 40.58 | 100%
[5 empty] | 40.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30600.7605 | 494098.9807 | 40.6 | 100%
[5 empty] | 40.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30623.5218 | 494466.5002 | 40.62 | 100%
[5 empty] | 40.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30646.2832 | 494834.0197 | 40.64 | 100%
[5 empty] | 40.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30669.0446 | 495201.5393 | 40.66 | 100%
[5 empty] | 40.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30691.806 | 495569.0588 | 40.68 | 100%
[5 empty] | 40.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30714.5674 | 495936.5783 | 40.7 | 100%
[5 empty] | 40.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30737.3288 | 496304.0978 | 40.72 | 100%
[5 empty] | 40.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30760.0901 | 496671.6173 | 40.74 | 100%
[5 empty] | 40.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30782.8515 | 497039.1369 | 40.76 | 100%
[5 empty] | 40.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30805.6129 | 497406.6564 | 40.78 | 100%
[5 empty] | 40.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30828.3743 | 497774.1759 | 40.8 | 100%
[5 empty] | 40.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30851.1357 | 498141.6954 | 40.82 | 100%
[5 empty] | 40.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30873.8971 | 498509.2149 | 40.84 | 100%
[5 empty] | 40.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30896.6585 | 498876.7345 | 40.86 | 100%
[5 empty] | 40.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30919.4198 | 499244.254 | 40.88 | 100%
[5 empty] | 40.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30942.1812 | 499611.7735 | 40.9 | 100%
[5 empty] | 40.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30964.9426 | 499979.293 | 40.92 | 100%
[5 empty] | 40.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 30987.704 | 500346.8125 | 40.94 | 100%
[5 empty] | 40.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31010.4654 | 500714.3321 | 40.96 | 100%
[5 empty] | 40.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31033.2268 | 501081.8516 | 40.98 | 100%
[5 empty] | 41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31055.9881 | 501449.3711 | 41 | 100%
[5 empty] | 41.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31078.7495 | 501816.8906 | 41.02 | 100%
[5 empty] | 41.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31101.5109 | 502184.4101 | 41.04 | 100%
[5 empty] | 41.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31124.2723 | 502551.9297 | 41.06 | 100%
[5 empty] | 41.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31147.0337 | 502919.4492 | 41.08 | 100%
[5 empty] | 41.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31169.7951 | 503286.9687 | 41.1 | 100%
[5 empty] | 41.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31192.5564 | 503654.4882 | 41.12 | 100%
[5 empty] | 41.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31215.3178 | 504022.0077 | 41.14 | 100%
[5 empty] | 41.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31238.0792 | 504389.5273 | 41.16 | 100%
[5 empty] | 41.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31260.8406 | 504757.0468 | 41.18 | 100%
[5 empty] | 41.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31283.602 | 505124.5663 | 41.2 | 100%
[5 empty] | 41.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31306.3634 | 505492.0858 | 41.22 | 100%
[5 empty] | 41.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31329.1248 | 505859.6053 | 41.24 | 100%
[5 empty] | 41.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31351.8861 | 506227.1249 | 41.26 | 100%
[5 empty] | 41.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31374.6475 | 506594.6444 | 41.28 | 100%
[5 empty] | 41.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31397.4089 | 506962.1639 | 41.3 | 100%
[5 empty] | 41.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31420.1703 | 507329.6834 | 41.32 | 100%
[5 empty] | 41.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31442.9317 | 507697.2029 | 41.34 | 100%
[5 empty] | 41.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31465.6931 | 508064.7225 | 41.36 | 100%
[5 empty] | 41.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31488.4544 | 508432.242 | 41.38 | 100%
[5 empty] | 41.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31511.2158 | 508799.7615 | 41.4 | 100%
[5 empty] | 41.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31533.9772 | 509167.281 | 41.42 | 100%
[5 empty] | 41.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31556.7386 | 509534.8005 | 41.44 | 100%
[5 empty] | 41.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31579.5 | 509902.3201 | 41.46 | 100%
[5 empty] | 41.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31602.2614 | 510269.8396 | 41.48 | 100%
[5 empty] | 41.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31625.0228 | 510637.3591 | 41.5 | 100%
[5 empty] | 41.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31647.7841 | 511004.8786 | 41.52 | 100%
[5 empty] | 41.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31670.5455 | 511372.3981 | 41.54 | 100%
[5 empty] | 41.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31693.3069 | 511739.9177 | 41.56 | 100%
[5 empty] | 41.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31716.0683 | 512107.4372 | 41.58 | 100%
[5 empty] | 41.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31738.8297 | 512474.9567 | 41.6 | 100%
[5 empty] | 41.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31761.5911 | 512842.4762 | 41.62 | 100%
[5 empty] | 41.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31784.3524 | 513209.9957 | 41.64 | 100%
[5 empty] | 41.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31807.1138 | 513577.5153 | 41.66 | 100%
[5 empty] | 41.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31829.8752 | 513945.0348 | 41.68 | 100%
[5 empty] | 41.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31852.6366 | 514312.5543 | 41.7 | 100%
[5 empty] | 41.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31875.398 | 514680.0738 | 41.72 | 100%
[5 empty] | 41.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31898.1594 | 515047.5933 | 41.74 | 100%
[5 empty] | 41.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31920.9207 | 515415.1129 | 41.76 | 100%
[5 empty] | 41.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31943.6821 | 515782.6324 | 41.78 | 100%
[5 empty] | 41.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31966.4435 | 516150.1519 | 41.8 | 100%
[5 empty] | 41.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 31989.2049 | 516517.6714 | 41.82 | 100%
[5 empty] | 41.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32011.9663 | 516885.1909 | 41.84 | 100%
[5 empty] | 41.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32034.7277 | 517252.7105 | 41.86 | 100%
[5 empty] | 41.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32057.4891 | 517620.23 | 41.88 | 100%
[5 empty] | 41.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32080.2504 | 517987.7495 | 41.9 | 100%
[5 empty] | 41.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32103.0118 | 518355.269 | 41.92 | 100%
[5 empty] | 41.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32125.7732 | 518722.7885 | 41.94 | 100%
[5 empty] | 41.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32148.5346 | 519090.3081 | 41.96 | 100%
[5 empty] | 41.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32171.296 | 519457.8276 | 41.98 | 100%
[5 empty] | 42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32194.0574 | 519825.3471 | 42 | 100%
[5 empty] | 42.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32216.8187 | 520192.8666 | 42.02 | 100%
[5 empty] | 42.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32239.5801 | 520560.3861 | 42.04 | 100%
[5 empty] | 42.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32262.3415 | 520927.9057 | 42.06 | 100%
[5 empty] | 42.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32285.1029 | 521295.4252 | 42.08 | 100%
[5 empty] | 42.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32307.8643 | 521662.9447 | 42.1 | 100%
[5 empty] | 42.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32330.6257 | 522030.4642 | 42.12 | 100%
[5 empty] | 42.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32353.387 | 522397.9837 | 42.14 | 100%
[5 empty] | 42.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32376.1484 | 522765.5033 | 42.16 | 100%
[5 empty] | 42.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32398.9098 | 523133.0228 | 42.18 | 100%
[5 empty] | 42.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32421.6712 | 523500.5423 | 42.2 | 100%
[5 empty] | 42.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32444.4326 | 523868.0618 | 42.22 | 100%
[5 empty] | 42.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32467.194 | 524235.5813 | 42.24 | 100%
[5 empty] | 42.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32489.9554 | 524603.1009 | 42.26 | 100%
[5 empty] | 42.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32512.7167 | 524970.6204 | 42.28 | 100%
[5 empty] | 42.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32535.4781 | 525338.1399 | 42.3 | 100%
[5 empty] | 42.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32558.2395 | 525705.6594 | 42.32 | 100%
[5 empty] | 42.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32581.0009 | 526073.1789 | 42.34 | 100%
[5 empty] | 42.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32603.7623 | 526440.6985 | 42.36 | 100%
[5 empty] | 42.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32626.5237 | 526808.218 | 42.38 | 100%
[5 empty] | 42.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32649.285 | 527175.7375 | 42.4 | 100%
[5 empty] | 42.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32672.0464 | 527543.257 | 42.42 | 100%
[5 empty] | 42.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32694.8078 | 527910.7765 | 42.44 | 100%
[5 empty] | 42.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32717.5692 | 528278.2961 | 42.46 | 100%
[5 empty] | 42.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32740.3306 | 528645.8156 | 42.48 | 100%
[5 empty] | 42.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32763.092 | 529013.3351 | 42.5 | 100%
[5 empty] | 42.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32785.8534 | 529380.8546 | 42.52 | 100%
[5 empty] | 42.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32808.6147 | 529748.3741 | 42.54 | 100%
[5 empty] | 42.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32831.3761 | 530115.8937 | 42.56 | 100%
[5 empty] | 42.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32854.1375 | 530483.4132 | 42.58 | 100%
[5 empty] | 42.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32876.8989 | 530850.9327 | 42.6 | 100%
[5 empty] | 42.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32899.6603 | 531218.4522 | 42.62 | 100%
[5 empty] | 42.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32922.4217 | 531585.9717 | 42.64 | 100%
[5 empty] | 42.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32945.183 | 531953.4913 | 42.66 | 100%
[5 empty] | 42.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32967.9444 | 532321.0108 | 42.68 | 100%
[5 empty] | 42.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 32990.7058 | 532688.5303 | 42.7 | 100%
[5 empty] | 42.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33013.4672 | 533056.0498 | 42.72 | 100%
[5 empty] | 42.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33036.2286 | 533423.5693 | 42.74 | 100%
[5 empty] | 42.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33058.99 | 533791.0889 | 42.76 | 100%
[5 empty] | 42.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33081.7513 | 534158.6084 | 42.78 | 100%
[5 empty] | 42.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33104.5127 | 534526.1279 | 42.8 | 100%
[5 empty] | 42.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33127.2741 | 534893.6474 | 42.82 | 100%
[5 empty] | 42.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33150.0355 | 535261.1669 | 42.84 | 100%
[5 empty] | 42.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33172.7969 | 535628.6865 | 42.86 | 100%
[5 empty] | 42.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33195.5583 | 535996.206 | 42.88 | 100%
[5 empty] | 42.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33218.3197 | 536363.7255 | 42.9 | 100%
[5 empty] | 42.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33241.081 | 536731.245 | 42.92 | 100%
[5 empty] | 42.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33263.8424 | 537098.7645 | 42.94 | 100%
[5 empty] | 42.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33286.6038 | 537466.2841 | 42.96 | 100%
[5 empty] | 42.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33309.3652 | 537833.8036 | 42.98 | 100%
[5 empty] | 43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33332.1266 | 538201.3231 | 43 | 100%
[5 empty] | 43.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33354.888 | 538568.8426 | 43.02 | 100%
[5 empty] | 43.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33377.6493 | 538936.3621 | 43.04 | 100%
[5 empty] | 43.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33400.4107 | 539303.8817 | 43.06 | 100%
[5 empty] | 43.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33423.1721 | 539671.4012 | 43.08 | 100%
[5 empty] | 43.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33445.9335 | 540038.9207 | 43.1 | 100%
[5 empty] | 43.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33468.6949 | 540406.4402 | 43.12 | 100%
[5 empty] | 43.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33491.4563 | 540773.9597 | 43.14 | 100%
[5 empty] | 43.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33514.2177 | 541141.4793 | 43.16 | 100%
[5 empty] | 43.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33536.979 | 541508.9988 | 43.18 | 100%
[5 empty] | 43.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33559.7404 | 541876.5183 | 43.2 | 100%
[5 empty] | 43.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33582.5018 | 542244.0378 | 43.22 | 100%
[5 empty] | 43.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33605.2632 | 542611.5573 | 43.24 | 100%
[5 empty] | 43.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33628.0246 | 542979.0769 | 43.26 | 100%
[5 empty] | 43.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33650.786 | 543346.5964 | 43.28 | 100%
[5 empty] | 43.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33673.5473 | 543714.1159 | 43.3 | 100%
[5 empty] | 43.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33696.3087 | 544081.6354 | 43.32 | 100%
[5 empty] | 43.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33719.0701 | 544449.1549 | 43.34 | 100%
[5 empty] | 43.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33741.8315 | 544816.6745 | 43.36 | 100%
[5 empty] | 43.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33764.5929 | 545184.194 | 43.38 | 100%
[5 empty] | 43.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33787.3543 | 545551.7135 | 43.4 | 100%
[5 empty] | 43.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33810.1156 | 545919.233 | 43.42 | 100%
[5 empty] | 43.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33832.877 | 546286.7525 | 43.44 | 100%
[5 empty] | 43.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33855.6384 | 546654.2721 | 43.46 | 100%
[5 empty] | 43.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33878.3998 | 547021.7916 | 43.48 | 100%
[5 empty] | 43.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33901.1612 | 547389.3111 | 43.5 | 100%
[5 empty] | 43.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33923.9226 | 547756.8306 | 43.52 | 100%
[5 empty] | 43.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33946.684 | 548124.3501 | 43.54 | 100%
[5 empty] | 43.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33969.4453 | 548491.8697 | 43.56 | 100%
[5 empty] | 43.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 33992.2067 | 548859.3892 | 43.58 | 100%
[5 empty] | 43.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34014.9681 | 549226.9087 | 43.6 | 100%
[5 empty] | 43.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34037.7295 | 549594.4282 | 43.62 | 100%
[5 empty] | 43.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34060.4909 | 549961.9477 | 43.64 | 100%
[5 empty] | 43.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34083.2523 | 550329.4673 | 43.66 | 100%
[5 empty] | 43.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34106.0136 | 550696.9868 | 43.68 | 100%
[5 empty] | 43.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34128.775 | 551064.5063 | 43.7 | 100%
[5 empty] | 43.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34151.5364 | 551432.0258 | 43.72 | 100%
[5 empty] | 43.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34174.2978 | 551799.5453 | 43.74 | 100%
[5 empty] | 43.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34197.0592 | 552167.0649 | 43.76 | 100%
[5 empty] | 43.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34219.8206 | 552534.5844 | 43.78 | 100%
[5 empty] | 43.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34242.5819 | 552902.1039 | 43.8 | 100%
[5 empty] | 43.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34265.3433 | 553269.6234 | 43.82 | 100%
[5 empty] | 43.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34288.1047 | 553637.1429 | 43.84 | 100%
[5 empty] | 43.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34310.8661 | 554004.6625 | 43.86 | 100%
[5 empty] | 43.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34333.6275 | 554372.182 | 43.88 | 100%
[5 empty] | 43.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34356.3889 | 554739.7015 | 43.9 | 100%
[5 empty] | 43.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34379.1503 | 555107.221 | 43.92 | 100%
[5 empty] | 43.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34401.9116 | 555474.7405 | 43.94 | 100%
[5 empty] | 43.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34424.673 | 555842.2601 | 43.96 | 100%
[5 empty] | 43.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34447.4344 | 556209.7796 | 43.98 | 100%
[5 empty] | 44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34470.1958 | 556577.2991 | 44 | 100%
[5 empty] | 44.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34492.9572 | 556944.8186 | 44.02 | 100%
[5 empty] | 44.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34515.7186 | 557312.3381 | 44.04 | 100%
[5 empty] | 44.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34538.4799 | 557679.8577 | 44.06 | 100%
[5 empty] | 44.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34561.2413 | 558047.3772 | 44.08 | 100%
[5 empty] | 44.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34584.0027 | 558414.8967 | 44.1 | 100%
[5 empty] | 44.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34606.7641 | 558782.4162 | 44.12 | 100%
[5 empty] | 44.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34629.5255 | 559149.9357 | 44.14 | 100%
[5 empty] | 44.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34652.2869 | 559517.4553 | 44.16 | 100%
[5 empty] | 44.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34675.0483 | 559884.9748 | 44.18 | 100%
[5 empty] | 44.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34697.8096 | 560252.4943 | 44.2 | 100%
[5 empty] | 44.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34720.571 | 560620.0138 | 44.22 | 100%
[5 empty] | 44.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34743.3324 | 560987.5333 | 44.24 | 100%
[5 empty] | 44.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34766.0938 | 561355.0529 | 44.26 | 100%
[5 empty] | 44.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34788.8552 | 561722.5724 | 44.28 | 100%
[5 empty] | 44.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34811.6166 | 562090.0919 | 44.3 | 100%
[5 empty] | 44.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34834.3779 | 562457.6114 | 44.32 | 100%
[5 empty] | 44.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34857.1393 | 562825.1309 | 44.34 | 100%
[5 empty] | 44.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34879.9007 | 563192.6505 | 44.36 | 100%
[5 empty] | 44.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34902.6621 | 563560.17 | 44.38 | 100%
[5 empty] | 44.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34925.4235 | 563927.6895 | 44.4 | 100%
[5 empty] | 44.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34948.1849 | 564295.209 | 44.42 | 100%
[5 empty] | 44.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34970.9462 | 564662.7285 | 44.44 | 100%
[5 empty] | 44.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 34993.7076 | 565030.2481 | 44.46 | 100%
[5 empty] | 44.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35016.469 | 565397.7676 | 44.48 | 100%
[5 empty] | 44.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35039.2304 | 565765.2871 | 44.5 | 100%
[5 empty] | 44.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35061.9918 | 566132.8066 | 44.52 | 100%
[5 empty] | 44.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35084.7532 | 566500.3261 | 44.54 | 100%
[5 empty] | 44.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35107.5146 | 566867.8457 | 44.56 | 100%
[5 empty] | 44.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35130.2759 | 567235.3652 | 44.58 | 100%
[5 empty] | 44.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35153.0373 | 567602.8847 | 44.6 | 100%
[5 empty] | 44.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35175.7987 | 567970.4042 | 44.62 | 100%
[5 empty] | 44.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35198.5601 | 568337.9237 | 44.64 | 100%
[5 empty] | 44.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35221.3215 | 568705.4433 | 44.66 | 100%
[5 empty] | 44.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35244.0829 | 569072.9628 | 44.68 | 100%
[5 empty] | 44.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35266.8442 | 569440.4823 | 44.7 | 100%
[5 empty] | 44.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35289.6056 | 569808.0018 | 44.72 | 100%
[5 empty] | 44.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35312.367 | 570175.5213 | 44.74 | 100%
[5 empty] | 44.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35335.1284 | 570543.0409 | 44.76 | 100%
[5 empty] | 44.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35357.8898 | 570910.5604 | 44.78 | 100%
[5 empty] | 44.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35380.6512 | 571278.0799 | 44.8 | 100%
[5 empty] | 44.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35403.4125 | 571645.5994 | 44.82 | 100%
[5 empty] | 44.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35426.1739 | 572013.1189 | 44.84 | 100%
[5 empty] | 44.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35448.9353 | 572380.6385 | 44.86 | 100%
[5 empty] | 44.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35471.6967 | 572748.158 | 44.88 | 100%
[5 empty] | 44.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35494.4581 | 573115.6775 | 44.9 | 100%
[5 empty] | 44.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35517.2195 | 573483.197 | 44.92 | 100%
[5 empty] | 44.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35539.9809 | 573850.7165 | 44.94 | 100%
[5 empty] | 44.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35562.7422 | 574218.2361 | 44.96 | 100%
[5 empty] | 44.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35585.5036 | 574585.7556 | 44.98 | 100%
[5 empty] | 45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35608.265 | 574953.2751 | 45 | 100%
[5 empty] | 45.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35631.0264 | 575320.7946 | 45.02 | 100%
[5 empty] | 45.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35653.7878 | 575688.3141 | 45.04 | 100%
[5 empty] | 45.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35676.5492 | 576055.8337 | 45.06 | 100%
[5 empty] | 45.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35699.3105 | 576423.3532 | 45.08 | 100%
[5 empty] | 45.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35722.0719 | 576790.8727 | 45.1 | 100%
[5 empty] | 45.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35744.8333 | 577158.3922 | 45.12 | 100%
[5 empty] | 45.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35767.5947 | 577525.9117 | 45.14 | 100%
[5 empty] | 45.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35790.3561 | 577893.4313 | 45.16 | 100%
[5 empty] | 45.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35813.1175 | 578260.9508 | 45.18 | 100%
[5 empty] | 45.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35835.8789 | 578628.4703 | 45.2 | 100%
[5 empty] | 45.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35858.6402 | 578995.9898 | 45.22 | 100%
[5 empty] | 45.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35881.4016 | 579363.5093 | 45.24 | 100%
[5 empty] | 45.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35904.163 | 579731.0289 | 45.26 | 100%
[5 empty] | 45.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35926.9244 | 580098.5484 | 45.28 | 100%
[5 empty] | 45.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35949.6858 | 580466.0679 | 45.3 | 100%
[5 empty] | 45.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35972.4472 | 580833.5874 | 45.32 | 100%
[5 empty] | 45.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 35995.2085 | 581201.1069 | 45.34 | 100%
[5 empty] | 45.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36017.9699 | 581568.6265 | 45.36 | 100%
[5 empty] | 45.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36040.7313 | 581936.146 | 45.38 | 100%
[5 empty] | 45.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36063.4927 | 582303.6655 | 45.4 | 100%
[5 empty] | 45.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36086.2541 | 582671.185 | 45.42 | 100%
[5 empty] | 45.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36109.0155 | 583038.7045 | 45.44 | 100%
[5 empty] | 45.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36131.7768 | 583406.2241 | 45.46 | 100%
[5 empty] | 45.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36154.5382 | 583773.7436 | 45.48 | 100%
[5 empty] | 45.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36177.2996 | 584141.2631 | 45.5 | 100%
[5 empty] | 45.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36200.061 | 584508.7826 | 45.52 | 100%
[5 empty] | 45.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36222.8224 | 584876.3021 | 45.54 | 100%
[5 empty] | 45.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36245.5838 | 585243.8217 | 45.56 | 100%
[5 empty] | 45.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36268.3452 | 585611.3412 | 45.58 | 100%
[5 empty] | 45.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36291.1065 | 585978.8607 | 45.6 | 100%
[5 empty] | 45.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36313.8679 | 586346.3802 | 45.62 | 100%
[5 empty] | 45.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36336.6293 | 586713.8997 | 45.64 | 100%
[5 empty] | 45.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36359.3907 | 587081.4193 | 45.66 | 100%
[5 empty] | 45.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36382.1521 | 587448.9388 | 45.68 | 100%
[5 empty] | 45.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36404.9135 | 587816.4583 | 45.7 | 100%
[5 empty] | 45.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36427.6748 | 588183.9778 | 45.72 | 100%
[5 empty] | 45.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36450.4362 | 588551.4973 | 45.74 | 100%
[5 empty] | 45.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36473.1976 | 588919.0169 | 45.76 | 100%
[5 empty] | 45.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36495.959 | 589286.5364 | 45.78 | 100%
[5 empty] | 45.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36518.7204 | 589654.0559 | 45.8 | 100%
[5 empty] | 45.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36541.4818 | 590021.5754 | 45.82 | 100%
[5 empty] | 45.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36564.2431 | 590389.0949 | 45.84 | 100%
[5 empty] | 45.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36587.0045 | 590756.6145 | 45.86 | 100%
[5 empty] | 45.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36609.7659 | 591124.134 | 45.88 | 100%
[5 empty] | 45.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36632.5273 | 591491.6535 | 45.9 | 100%
[5 empty] | 45.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36655.2887 | 591859.173 | 45.92 | 100%
[5 empty] | 45.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36678.0501 | 592226.6925 | 45.94 | 100%
[5 empty] | 45.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36700.8115 | 592594.2121 | 45.96 | 100%
[5 empty] | 45.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36723.5728 | 592961.7316 | 45.98 | 100%
[5 empty] | 46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36746.3342 | 593329.2511 | 46 | 100%
[5 empty] | 46.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36769.0956 | 593696.7706 | 46.02 | 100%
[5 empty] | 46.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36791.857 | 594064.2901 | 46.04 | 100%
[5 empty] | 46.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36814.6184 | 594431.8097 | 46.06 | 100%
[5 empty] | 46.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36837.3798 | 594799.3292 | 46.08 | 100%
[5 empty] | 46.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36860.1411 | 595166.8487 | 46.1 | 100%
[5 empty] | 46.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36882.9025 | 595534.3682 | 46.12 | 100%
[5 empty] | 46.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36905.6639 | 595901.8877 | 46.14 | 100%
[5 empty] | 46.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36928.4253 | 596269.4073 | 46.16 | 100%
[5 empty] | 46.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36951.1867 | 596636.9268 | 46.18 | 100%
[5 empty] | 46.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36973.9481 | 597004.4463 | 46.2 | 100%
[5 empty] | 46.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 36996.7095 | 597371.9658 | 46.22 | 100%
[5 empty] | 46.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37019.4708 | 597739.4853 | 46.24 | 100%
[5 empty] | 46.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37042.2322 | 598107.0049 | 46.26 | 100%
[5 empty] | 46.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37064.9936 | 598474.5244 | 46.28 | 100%
[5 empty] | 46.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37087.755 | 598842.0439 | 46.3 | 100%
[5 empty] | 46.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37110.5164 | 599209.5634 | 46.32 | 100%
[5 empty] | 46.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37133.2778 | 599577.0829 | 46.34 | 100%
[5 empty] | 46.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37156.0391 | 599944.6025 | 46.36 | 100%
[5 empty] | 46.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37178.8005 | 600312.122 | 46.38 | 100%
[5 empty] | 46.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37201.5619 | 600679.6415 | 46.4 | 100%
[5 empty] | 46.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37224.3233 | 601047.161 | 46.42 | 100%
[5 empty] | 46.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37247.0847 | 601414.6805 | 46.44 | 100%
[5 empty] | 46.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37269.8461 | 601782.2001 | 46.46 | 100%
[5 empty] | 46.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37292.6074 | 602149.7196 | 46.48 | 100%
[5 empty] | 46.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37315.3688 | 602517.2391 | 46.5 | 100%
[5 empty] | 46.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37338.1302 | 602884.7586 | 46.52 | 100%
[5 empty] | 46.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37360.8916 | 603252.2781 | 46.54 | 100%
[5 empty] | 46.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37383.653 | 603619.7977 | 46.56 | 100%
[5 empty] | 46.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37406.4144 | 603987.3172 | 46.58 | 100%
[5 empty] | 46.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37429.1758 | 604354.8367 | 46.6 | 100%
[5 empty] | 46.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37451.9371 | 604722.3562 | 46.62 | 100%
[5 empty] | 46.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37474.6985 | 605089.8757 | 46.64 | 100%
[5 empty] | 46.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37497.4599 | 605457.3953 | 46.66 | 100%
[5 empty] | 46.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37520.2213 | 605824.9148 | 46.68 | 100%
[5 empty] | 46.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37542.9827 | 606192.4343 | 46.7 | 100%
[5 empty] | 46.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37565.7441 | 606559.9538 | 46.72 | 100%
[5 empty] | 46.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37588.5054 | 606927.4733 | 46.74 | 100%
[5 empty] | 46.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37611.2668 | 607294.9929 | 46.76 | 100%
[5 empty] | 46.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37634.0282 | 607662.5124 | 46.78 | 100%
[5 empty] | 46.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37656.7896 | 608030.0319 | 46.8 | 100%
[5 empty] | 46.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37679.551 | 608397.5514 | 46.82 | 100%
[5 empty] | 46.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37702.3124 | 608765.0709 | 46.84 | 100%
[5 empty] | 46.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37725.0738 | 609132.5905 | 46.86 | 100%
[5 empty] | 46.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37747.8351 | 609500.11 | 46.88 | 100%
[5 empty] | 46.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37770.5965 | 609867.6295 | 46.9 | 100%
[5 empty] | 46.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37793.3579 | 610235.149 | 46.92 | 100%
[5 empty] | 46.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37816.1193 | 610602.6685 | 46.94 | 100%
[5 empty] | 46.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37838.8807 | 610970.1881 | 46.96 | 100%
[5 empty] | 46.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37861.6421 | 611337.7076 | 46.98 | 100%
[5 empty] | 47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37884.4034 | 611705.2271 | 47 | 100%
[5 empty] | 47.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37907.1648 | 612072.7466 | 47.02 | 100%
[5 empty] | 47.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37929.9262 | 612440.2661 | 47.04 | 100%
[5 empty] | 47.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37952.6876 | 612807.7857 | 47.06 | 100%
[5 empty] | 47.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37975.449 | 613175.3052 | 47.08 | 100%
[5 empty] | 47.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 37998.2104 | 613542.8247 | 47.1 | 100%
[5 empty] | 47.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38020.9717 | 613910.3442 | 47.12 | 100%
[5 empty] | 47.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38043.7331 | 614277.8637 | 47.14 | 100%
[5 empty] | 47.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38066.4945 | 614645.3833 | 47.16 | 100%
[5 empty] | 47.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38089.2559 | 615012.9028 | 47.18 | 100%
[5 empty] | 47.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38112.0173 | 615380.4223 | 47.2 | 100%
[5 empty] | 47.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38134.7787 | 615747.9418 | 47.22 | 100%
[5 empty] | 47.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38157.5401 | 616115.4613 | 47.24 | 100%
[5 empty] | 47.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38180.3014 | 616482.9809 | 47.26 | 100%
[5 empty] | 47.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38203.0628 | 616850.5004 | 47.28 | 100%
[5 empty] | 47.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38225.8242 | 617218.0199 | 47.3 | 100%
[5 empty] | 47.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38248.5856 | 617585.5394 | 47.32 | 100%
[5 empty] | 47.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38271.347 | 617953.0589 | 47.34 | 100%
[5 empty] | 47.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38294.1084 | 618320.5785 | 47.36 | 100%
[5 empty] | 47.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38316.8697 | 618688.098 | 47.38 | 100%
[5 empty] | 47.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38339.6311 | 619055.6175 | 47.4 | 100%
[5 empty] | 47.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38362.3925 | 619423.137 | 47.42 | 100%
[5 empty] | 47.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38385.1539 | 619790.6565 | 47.44 | 100%
[5 empty] | 47.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38407.9153 | 620158.1761 | 47.46 | 100%
[5 empty] | 47.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38430.6767 | 620525.6956 | 47.48 | 100%
[5 empty] | 47.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38453.438 | 620893.2151 | 47.5 | 100%
[5 empty] | 47.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38476.1994 | 621260.7346 | 47.52 | 100%
[5 empty] | 47.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38498.9608 | 621628.2541 | 47.54 | 100%
[5 empty] | 47.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38521.7222 | 621995.7737 | 47.56 | 100%
[5 empty] | 47.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38544.4836 | 622363.2932 | 47.58 | 100%
[5 empty] | 47.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38567.245 | 622730.8127 | 47.6 | 100%
[5 empty] | 47.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38590.0064 | 623098.3322 | 47.62 | 100%
[5 empty] | 47.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38612.7677 | 623465.8517 | 47.64 | 100%
[5 empty] | 47.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38635.5291 | 623833.3713 | 47.66 | 100%
[5 empty] | 47.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38658.2905 | 624200.8908 | 47.68 | 100%
[5 empty] | 47.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38681.0519 | 624568.4103 | 47.7 | 100%
[5 empty] | 47.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38703.8133 | 624935.9298 | 47.72 | 100%
[5 empty] | 47.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38726.5747 | 625303.4493 | 47.74 | 100%
[5 empty] | 47.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38749.336 | 625670.9689 | 47.76 | 100%
[5 empty] | 47.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38772.0974 | 626038.4884 | 47.78 | 100%
[5 empty] | 47.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38794.8588 | 626406.0079 | 47.8 | 100%
[5 empty] | 47.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38817.6202 | 626773.5274 | 47.82 | 100%
[5 empty] | 47.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38840.3816 | 627141.0469 | 47.84 | 100%
[5 empty] | 47.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38863.143 | 627508.5665 | 47.86 | 100%
[5 empty] | 47.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38885.9044 | 627876.086 | 47.88 | 100%
[5 empty] | 47.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38908.6657 | 628243.6055 | 47.9 | 100%
[5 empty] | 47.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38931.4271 | 628611.125 | 47.92 | 100%
[5 empty] | 47.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38954.1885 | 628978.6445 | 47.94 | 100%
[5 empty] | 47.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38976.9499 | 629346.1641 | 47.96 | 100%
[5 empty] | 47.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 38999.7113 | 629713.6836 | 47.98 | 100%
[5 empty] | 48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39022.4727 | 630081.2031 | 48 | 100%
[5 empty] | 48.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39045.234 | 630448.7226 | 48.02 | 100%
[5 empty] | 48.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39067.9954 | 630816.2421 | 48.04 | 100%
[5 empty] | 48.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39090.7568 | 631183.7617 | 48.06 | 100%
[5 empty] | 48.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39113.5182 | 631551.2812 | 48.08 | 100%
[5 empty] | 48.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39136.2796 | 631918.8007 | 48.1 | 100%
[5 empty] | 48.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39159.041 | 632286.3202 | 48.12 | 100%
[5 empty] | 48.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39181.8023 | 632653.8397 | 48.14 | 100%
[5 empty] | 48.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39204.5637 | 633021.3593 | 48.16 | 100%
[5 empty] | 48.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39227.3251 | 633388.8788 | 48.18 | 100%
[5 empty] | 48.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39250.0865 | 633756.3983 | 48.2 | 100%
[5 empty] | 48.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39272.8479 | 634123.9178 | 48.22 | 100%
[5 empty] | 48.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39295.6093 | 634491.4373 | 48.24 | 100%
[5 empty] | 48.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39318.3707 | 634858.9569 | 48.26 | 100%
[5 empty] | 48.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39341.132 | 635226.4764 | 48.28 | 100%
[5 empty] | 48.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39363.8934 | 635593.9959 | 48.3 | 100%
[5 empty] | 48.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39386.6548 | 635961.5154 | 48.32 | 100%
[5 empty] | 48.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39409.4162 | 636329.0349 | 48.34 | 100%
[5 empty] | 48.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39432.1776 | 636696.5545 | 48.36 | 100%
[5 empty] | 48.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39454.939 | 637064.074 | 48.38 | 100%
[5 empty] | 48.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39477.7003 | 637431.5935 | 48.4 | 100%
[5 empty] | 48.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39500.4617 | 637799.113 | 48.42 | 100%
[5 empty] | 48.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39523.2231 | 638166.6325 | 48.44 | 100%
[5 empty] | 48.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39545.9845 | 638534.1521 | 48.46 | 100%
[5 empty] | 48.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39568.7459 | 638901.6716 | 48.48 | 100%
[5 empty] | 48.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39591.5073 | 639269.1911 | 48.5 | 100%
[5 empty] | 48.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39614.2686 | 639636.7106 | 48.52 | 100%
[5 empty] | 48.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39637.03 | 640004.2301 | 48.54 | 100%
[5 empty] | 48.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39659.7914 | 640371.7497 | 48.56 | 100%
[5 empty] | 48.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39682.5528 | 640739.2692 | 48.58 | 100%
[5 empty] | 48.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39705.3142 | 641106.7887 | 48.6 | 100%
[5 empty] | 48.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39728.0756 | 641474.3082 | 48.62 | 100%
[5 empty] | 48.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39750.837 | 641841.8277 | 48.64 | 100%
[5 empty] | 48.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39773.5983 | 642209.3473 | 48.66 | 100%
[5 empty] | 48.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39796.3597 | 642576.8668 | 48.68 | 100%
[5 empty] | 48.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39819.1211 | 642944.3863 | 48.7 | 100%
[5 empty] | 48.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39841.8825 | 643311.9058 | 48.72 | 100%
[5 empty] | 48.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39864.6439 | 643679.4253 | 48.74 | 100%
[5 empty] | 48.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39887.4053 | 644046.9449 | 48.76 | 100%
[5 empty] | 48.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39910.1666 | 644414.4644 | 48.78 | 100%
[5 empty] | 48.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39932.928 | 644781.9839 | 48.8 | 100%
[5 empty] | 48.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39955.6894 | 645149.5034 | 48.82 | 100%
[5 empty] | 48.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 39978.4508 | 645517.0229 | 48.84 | 100%
[5 empty] | 48.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40001.2122 | 645884.5425 | 48.86 | 100%
[5 empty] | 48.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40023.9736 | 646252.062 | 48.88 | 100%
[5 empty] | 48.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40046.735 | 646619.5815 | 48.9 | 100%
[5 empty] | 48.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40069.4963 | 646987.101 | 48.92 | 100%
[5 empty] | 48.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40092.2577 | 647354.6205 | 48.94 | 100%
[5 empty] | 48.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40115.0191 | 647722.1401 | 48.96 | 100%
[5 empty] | 48.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40137.7805 | 648089.6596 | 48.98 | 100%
[5 empty] | 49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40160.5419 | 648457.1791 | 49 | 100%
[5 empty] | 49.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40183.3033 | 648824.6986 | 49.02 | 100%
[5 empty] | 49.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40206.0646 | 649192.2181 | 49.04 | 100%
[5 empty] | 49.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40228.826 | 649559.7377 | 49.06 | 100%
[5 empty] | 49.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40251.5874 | 649927.2572 | 49.08 | 100%
[5 empty] | 49.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40274.3488 | 650294.7767 | 49.1 | 100%
[5 empty] | 49.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40297.1102 | 650662.2962 | 49.12 | 100%
[5 empty] | 49.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40319.8716 | 651029.8157 | 49.14 | 100%
[5 empty] | 49.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40342.6329 | 651397.3353 | 49.16 | 100%
[5 empty] | 49.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40365.3943 | 651764.8548 | 49.18 | 100%
[5 empty] | 49.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40388.1557 | 652132.3743 | 49.2 | 100%
[5 empty] | 49.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40410.9171 | 652499.8938 | 49.22 | 100%
[5 empty] | 49.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40433.6785 | 652867.4133 | 49.24 | 100%
[5 empty] | 49.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40456.4399 | 653234.9329 | 49.26 | 100%
[5 empty] | 49.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40479.2013 | 653602.4524 | 49.28 | 100%
[5 empty] | 49.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40501.9626 | 653969.9719 | 49.3 | 100%
[5 empty] | 49.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40524.724 | 654337.4914 | 49.32 | 100%
[5 empty] | 49.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40547.4854 | 654705.0109 | 49.34 | 100%
[5 empty] | 49.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40570.2468 | 655072.5305 | 49.36 | 100%
[5 empty] | 49.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40593.0082 | 655440.05 | 49.38 | 100%
[5 empty] | 49.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40615.7696 | 655807.5695 | 49.4 | 100%
[5 empty] | 49.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40638.5309 | 656175.089 | 49.42 | 100%
[5 empty] | 49.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40661.2923 | 656542.6085 | 49.44 | 100%
[5 empty] | 49.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40684.0537 | 656910.1281 | 49.46 | 100%
[5 empty] | 49.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40706.8151 | 657277.6476 | 49.48 | 100%
[5 empty] | 49.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40729.5765 | 657645.1671 | 49.5 | 100%
[5 empty] | 49.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40752.3379 | 658012.6866 | 49.52 | 100%
[5 empty] | 49.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40775.0992 | 658380.2061 | 49.54 | 100%
[5 empty] | 49.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40797.8606 | 658747.7257 | 49.56 | 100%
[5 empty] | 49.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40820.622 | 659115.2452 | 49.58 | 100%
[5 empty] | 49.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40843.3834 | 659482.7647 | 49.6 | 100%
[5 empty] | 49.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40866.1448 | 659850.2842 | 49.62 | 100%
[5 empty] | 49.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40888.9062 | 660217.8037 | 49.64 | 100%
[5 empty] | 49.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40911.6676 | 660585.3233 | 49.66 | 100%
[5 empty] | 49.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40934.4289 | 660952.8428 | 49.68 | 100%
[5 empty] | 49.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40957.1903 | 661320.3623 | 49.7 | 100%
[5 empty] | 49.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 40979.9517 | 661687.8818 | 49.72 | 100%
[5 empty] | 49.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41002.7131 | 662055.4013 | 49.74 | 100%
[5 empty] | 49.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41025.4745 | 662422.9209 | 49.76 | 100%
[5 empty] | 49.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41048.2359 | 662790.4404 | 49.78 | 100%
[5 empty] | 49.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41070.9972 | 663157.9599 | 49.8 | 100%
[5 empty] | 49.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41093.7586 | 663525.4794 | 49.82 | 100%
[5 empty] | 49.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41116.52 | 663892.9989 | 49.84 | 100%
[5 empty] | 49.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41139.2814 | 664260.5185 | 49.86 | 100%
[5 empty] | 49.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41162.0428 | 664628.038 | 49.88 | 100%
[5 empty] | 49.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41184.8042 | 664995.5575 | 49.9 | 100%
[5 empty] | 49.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41207.5656 | 665363.077 | 49.92 | 100%
[5 empty] | 49.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41230.3269 | 665730.5965 | 49.94 | 100%
[5 empty] | 49.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41253.0883 | 666098.1161 | 49.96 | 100%
[5 empty] | 49.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41275.8497 | 666465.6356 | 49.98 | 100%
[5 empty] | 50 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41298.6111 | 666833.1551 | 50 | 100%
[5 empty] | 50.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41321.3725 | 667200.6746 | 50.02 | 100%
[5 empty] | 50.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41344.1339 | 667568.1941 | 50.04 | 100%
[5 empty] | 50.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41366.8952 | 667935.7137 | 50.06 | 100%
[5 empty] | 50.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41389.6566 | 668303.2332 | 50.08 | 100%
[5 empty] | 50.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41412.418 | 668670.7527 | 50.1 | 100%
[5 empty] | 50.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41435.1794 | 669038.2722 | 50.12 | 100%
[5 empty] | 50.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41457.9408 | 669405.7917 | 50.14 | 100%
[5 empty] | 50.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41480.7022 | 669773.3113 | 50.16 | 100%
[5 empty] | 50.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41503.4635 | 670140.8308 | 50.18 | 100%
[5 empty] | 50.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41526.2249 | 670508.3503 | 50.2 | 100%
[5 empty] | 50.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41548.9863 | 670875.8698 | 50.22 | 100%
[5 empty] | 50.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41571.7477 | 671243.3893 | 50.24 | 100%
[5 empty] | 50.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41594.5091 | 671610.9089 | 50.26 | 100%
[5 empty] | 50.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41617.2705 | 671978.4284 | 50.28 | 100%
[5 empty] | 50.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41640.0319 | 672345.9479 | 50.3 | 100%
[5 empty] | 50.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41662.7932 | 672713.4674 | 50.32 | 100%
[5 empty] | 50.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41685.5546 | 673080.9869 | 50.34 | 100%
[5 empty] | 50.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41708.316 | 673448.5065 | 50.36 | 100%
[5 empty] | 50.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41731.0774 | 673816.026 | 50.38 | 100%
[5 empty] | 50.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41753.8388 | 674183.5455 | 50.4 | 100%
[5 empty] | 50.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41776.6002 | 674551.065 | 50.42 | 100%
[5 empty] | 50.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41799.3615 | 674918.5845 | 50.44 | 100%
[5 empty] | 50.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41822.1229 | 675286.1041 | 50.46 | 100%
[5 empty] | 50.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41844.8843 | 675653.6236 | 50.48 | 100%
[5 empty] | 50.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41867.6457 | 676021.1431 | 50.5 | 100%
[5 empty] | 50.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41890.4071 | 676388.6626 | 50.52 | 100%
[5 empty] | 50.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41913.1685 | 676756.1821 | 50.54 | 100%
[5 empty] | 50.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41935.9299 | 677123.7017 | 50.56 | 100%
[5 empty] | 50.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41958.6912 | 677491.2212 | 50.58 | 100%
[5 empty] | 50.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 41981.4526 | 677858.7407 | 50.6 | 100%
[5 empty] | 50.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42004.214 | 678226.2602 | 50.62 | 100%
[5 empty] | 50.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42026.9754 | 678593.7797 | 50.64 | 100%
[5 empty] | 50.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42049.7368 | 678961.2993 | 50.66 | 100%
[5 empty] | 50.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42072.4982 | 679328.8188 | 50.68 | 100%
[5 empty] | 50.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42095.2595 | 679696.3383 | 50.7 | 100%
[5 empty] | 50.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42118.0209 | 680063.8578 | 50.72 | 100%
[5 empty] | 50.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42140.7823 | 680431.3773 | 50.74 | 100%
[5 empty] | 50.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42163.5437 | 680798.8969 | 50.76 | 100%
[5 empty] | 50.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42186.3051 | 681166.4164 | 50.78 | 100%
[5 empty] | 50.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42209.0665 | 681533.9359 | 50.8 | 100%
[5 empty] | 50.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42231.8278 | 681901.4554 | 50.82 | 100%
[5 empty] | 50.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42254.5892 | 682268.9749 | 50.84 | 100%
[5 empty] | 50.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42277.3506 | 682636.4945 | 50.86 | 100%
[5 empty] | 50.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42300.112 | 683004.014 | 50.88 | 100%
[5 empty] | 50.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42322.8734 | 683371.5335 | 50.9 | 100%
[5 empty] | 50.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42345.6348 | 683739.053 | 50.92 | 100%
[5 empty] | 50.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42368.3962 | 684106.5725 | 50.94 | 100%
[5 empty] | 50.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42391.1575 | 684474.0921 | 50.96 | 100%
[5 empty] | 50.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42413.9189 | 684841.6116 | 50.98 | 100%
[5 empty] | 51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42436.6803 | 685209.1311 | 51 | 100%
[5 empty] | 51.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42459.4417 | 685576.6506 | 51.02 | 100%
[5 empty] | 51.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42482.2031 | 685944.1701 | 51.04 | 100%
[5 empty] | 51.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42504.9645 | 686311.6897 | 51.06 | 100%
[5 empty] | 51.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42527.7258 | 686679.2092 | 51.08 | 100%
[5 empty] | 51.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42550.4872 | 687046.7287 | 51.1 | 100%
[5 empty] | 51.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42573.2486 | 687414.2482 | 51.12 | 100%
[5 empty] | 51.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42596.01 | 687781.7677 | 51.14 | 100%
[5 empty] | 51.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42618.7714 | 688149.2873 | 51.16 | 100%
[5 empty] | 51.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42641.5328 | 688516.8068 | 51.18 | 100%
[5 empty] | 51.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42664.2941 | 688884.3263 | 51.2 | 100%
[5 empty] | 51.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42687.0555 | 689251.8458 | 51.22 | 100%
[5 empty] | 51.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42709.8169 | 689619.3653 | 51.24 | 100%
[5 empty] | 51.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42732.5783 | 689986.8849 | 51.26 | 100%
[5 empty] | 51.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42755.3397 | 690354.4044 | 51.28 | 100%
[5 empty] | 51.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42778.1011 | 690721.9239 | 51.3 | 100%
[5 empty] | 51.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42800.8625 | 691089.4434 | 51.32 | 100%
[5 empty] | 51.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42823.6238 | 691456.9629 | 51.34 | 100%
[5 empty] | 51.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42846.3852 | 691824.4825 | 51.36 | 100%
[5 empty] | 51.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42869.1466 | 692192.002 | 51.38 | 100%
[5 empty] | 51.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42891.908 | 692559.5215 | 51.4 | 100%
[5 empty] | 51.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42914.6694 | 692927.041 | 51.42 | 100%
[5 empty] | 51.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42937.4308 | 693294.5605 | 51.44 | 100%
[5 empty] | 51.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42960.1921 | 693662.0801 | 51.46 | 100%
[5 empty] | 51.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 42982.9535 | 694029.5996 | 51.48 | 100%
[5 empty] | 51.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43005.7149 | 694397.1191 | 51.5 | 100%
[5 empty] | 51.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43028.4763 | 694764.6386 | 51.52 | 100%
[5 empty] | 51.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43051.2377 | 695132.1581 | 51.54 | 100%
[5 empty] | 51.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43073.9991 | 695499.6777 | 51.56 | 100%
[5 empty] | 51.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43096.7605 | 695867.1972 | 51.58 | 100%
[5 empty] | 51.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43119.5218 | 696234.7167 | 51.6 | 100%
[5 empty] | 51.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43142.2832 | 696602.2362 | 51.62 | 100%
[5 empty] | 51.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43165.0446 | 696969.7557 | 51.64 | 100%
[5 empty] | 51.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43187.806 | 697337.2753 | 51.66 | 100%
[5 empty] | 51.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43210.5674 | 697704.7948 | 51.68 | 100%
[5 empty] | 51.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43233.3288 | 698072.3143 | 51.7 | 100%
[5 empty] | 51.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43256.0901 | 698439.8338 | 51.72 | 100%
[5 empty] | 51.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43278.8515 | 698807.3533 | 51.74 | 100%
[5 empty] | 51.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43301.6129 | 699174.8729 | 51.76 | 100%
[5 empty] | 51.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43324.3743 | 699542.3924 | 51.78 | 100%
[5 empty] | 51.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43347.1357 | 699909.9119 | 51.8 | 100%
[5 empty] | 51.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43369.8971 | 700277.4314 | 51.82 | 100%
[5 empty] | 51.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43392.6584 | 700644.9509 | 51.84 | 100%
[5 empty] | 51.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43415.4198 | 701012.4705 | 51.86 | 100%
[5 empty] | 51.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43438.1812 | 701379.99 | 51.88 | 100%
[5 empty] | 51.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43460.9426 | 701747.5095 | 51.9 | 100%
[5 empty] | 51.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43483.704 | 702115.029 | 51.92 | 100%
[5 empty] | 51.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43506.4654 | 702482.5485 | 51.94 | 100%
[5 empty] | 51.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43529.2268 | 702850.0681 | 51.96 | 100%
[5 empty] | 51.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43551.9881 | 703217.5876 | 51.98 | 100%
[5 empty] | 52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43574.7495 | 703585.1071 | 52 | 100%
[5 empty] | 52.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43597.5109 | 703952.6266 | 52.02 | 100%
[5 empty] | 52.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43620.2723 | 704320.1461 | 52.04 | 100%
[5 empty] | 52.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43643.0337 | 704687.6657 | 52.06 | 100%
[5 empty] | 52.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43665.7951 | 705055.1852 | 52.08 | 100%
[5 empty] | 52.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43688.5564 | 705422.7047 | 52.1 | 100%
[5 empty] | 52.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43711.3178 | 705790.2242 | 52.12 | 100%
[5 empty] | 52.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43734.0792 | 706157.7437 | 52.14 | 100%
[5 empty] | 52.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43756.8406 | 706525.2633 | 52.16 | 100%
[5 empty] | 52.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43779.602 | 706892.7828 | 52.18 | 100%
[5 empty] | 52.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43802.3634 | 707260.3023 | 52.2 | 100%
[5 empty] | 52.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43825.1247 | 707627.8218 | 52.22 | 100%
[5 empty] | 52.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43847.8861 | 707995.3413 | 52.24 | 100%
[5 empty] | 52.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43870.6475 | 708362.8609 | 52.26 | 100%
[5 empty] | 52.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43893.4089 | 708730.3804 | 52.28 | 100%
[5 empty] | 52.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43916.1703 | 709097.8999 | 52.3 | 100%
[5 empty] | 52.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43938.9317 | 709465.4194 | 52.32 | 100%
[5 empty] | 52.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43961.6931 | 709832.9389 | 52.34 | 100%
[5 empty] | 52.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 43984.4544 | 710200.4585 | 52.36 | 100%
[5 empty] | 52.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44007.2158 | 710567.978 | 52.38 | 100%
[5 empty] | 52.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44029.9772 | 710935.4975 | 52.4 | 100%
[5 empty] | 52.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44052.7386 | 711303.017 | 52.42 | 100%
[5 empty] | 52.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44075.5 | 711670.5365 | 52.44 | 100%
[5 empty] | 52.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44098.2614 | 712038.0561 | 52.46 | 100%
[5 empty] | 52.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44121.0227 | 712405.5756 | 52.48 | 100%
[5 empty] | 52.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44143.7841 | 712773.0951 | 52.5 | 100%
[5 empty] | 52.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44166.5455 | 713140.6146 | 52.52 | 100%
[5 empty] | 52.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44189.3069 | 713508.1341 | 52.54 | 100%
[5 empty] | 52.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44212.0683 | 713875.6537 | 52.56 | 100%
[5 empty] | 52.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44234.8297 | 714243.1732 | 52.58 | 100%
[5 empty] | 52.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44257.5911 | 714610.6927 | 52.6 | 100%
[5 empty] | 52.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44280.3524 | 714978.2122 | 52.62 | 100%
[5 empty] | 52.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44303.1138 | 715345.7317 | 52.64 | 100%
[5 empty] | 52.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44325.8752 | 715713.2513 | 52.66 | 100%
[5 empty] | 52.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44348.6366 | 716080.7708 | 52.68 | 100%
[5 empty] | 52.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44371.398 | 716448.2903 | 52.7 | 100%
[5 empty] | 52.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44394.1594 | 716815.8098 | 52.72 | 100%
[5 empty] | 52.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44416.9207 | 717183.3293 | 52.74 | 100%
[5 empty] | 52.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44439.6821 | 717550.8489 | 52.76 | 100%
[5 empty] | 52.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44462.4435 | 717918.3684 | 52.78 | 100%
[5 empty] | 52.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44485.2049 | 718285.8879 | 52.8 | 100%
[5 empty] | 52.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44507.9663 | 718653.4074 | 52.82 | 100%
[5 empty] | 52.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44530.7277 | 719020.9269 | 52.84 | 100%
[5 empty] | 52.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44553.489 | 719388.4465 | 52.86 | 100%
[5 empty] | 52.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44576.2504 | 719755.966 | 52.88 | 100%
[5 empty] | 52.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44599.0118 | 720123.4855 | 52.9 | 100%
[5 empty] | 52.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44621.7732 | 720491.005 | 52.92 | 100%
[5 empty] | 52.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44644.5346 | 720858.5245 | 52.94 | 100%
[5 empty] | 52.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44667.296 | 721226.0441 | 52.96 | 100%
[5 empty] | 52.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44690.0574 | 721593.5636 | 52.98 | 100%
[5 empty] | 53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44712.8187 | 721961.0831 | 53 | 100%
[5 empty] | 53.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44735.5801 | 722328.6026 | 53.02 | 100%
[5 empty] | 53.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44758.3415 | 722696.1221 | 53.04 | 100%
[5 empty] | 53.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44781.1029 | 723063.6417 | 53.06 | 100%
[5 empty] | 53.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44803.8643 | 723431.1612 | 53.08 | 100%
[5 empty] | 53.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44826.6257 | 723798.6807 | 53.1 | 100%
[5 empty] | 53.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44849.387 | 724166.2002 | 53.12 | 100%
[5 empty] | 53.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44872.1484 | 724533.7197 | 53.14 | 100%
[5 empty] | 53.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44894.9098 | 724901.2393 | 53.16 | 100%
[5 empty] | 53.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44917.6712 | 725268.7588 | 53.18 | 100%
[5 empty] | 53.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44940.4326 | 725636.2783 | 53.2 | 100%
[5 empty] | 53.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44963.194 | 726003.7978 | 53.22 | 100%
[5 empty] | 53.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 44985.9553 | 726371.3173 | 53.24 | 100%
[5 empty] | 53.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45008.7167 | 726738.8369 | 53.26 | 100%
[5 empty] | 53.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45031.4781 | 727106.3564 | 53.28 | 100%
[5 empty] | 53.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45054.2395 | 727473.8759 | 53.3 | 100%
[5 empty] | 53.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45077.0009 | 727841.3954 | 53.32 | 100%
[5 empty] | 53.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45099.7623 | 728208.9149 | 53.34 | 100%
[5 empty] | 53.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45122.5237 | 728576.4345 | 53.36 | 100%
[5 empty] | 53.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45145.285 | 728943.954 | 53.38 | 100%
[5 empty] | 53.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45168.0464 | 729311.4735 | 53.4 | 100%
[5 empty] | 53.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45190.8078 | 729678.993 | 53.42 | 100%
[5 empty] | 53.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45213.5692 | 730046.5125 | 53.44 | 100%
[5 empty] | 53.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45236.3306 | 730414.0321 | 53.46 | 100%
[5 empty] | 53.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45259.092 | 730781.5516 | 53.48 | 100%
[5 empty] | 53.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45281.8533 | 731149.0711 | 53.5 | 100%
[5 empty] | 53.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45304.6147 | 731516.5906 | 53.52 | 100%
[5 empty] | 53.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45327.3761 | 731884.1101 | 53.54 | 100%
[5 empty] | 53.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45350.1375 | 732251.6297 | 53.56 | 100%
[5 empty] | 53.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45372.8989 | 732619.1492 | 53.58 | 100%
[5 empty] | 53.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45395.6603 | 732986.6687 | 53.6 | 100%
[5 empty] | 53.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45418.4217 | 733354.1882 | 53.62 | 100%
[5 empty] | 53.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45441.183 | 733721.7077 | 53.64 | 100%
[5 empty] | 53.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45463.9444 | 734089.2273 | 53.66 | 100%
[5 empty] | 53.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45486.7058 | 734456.7468 | 53.68 | 100%
[5 empty] | 53.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45509.4672 | 734824.2663 | 53.7 | 100%
[5 empty] | 53.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45532.2286 | 735191.7858 | 53.72 | 100%
[5 empty] | 53.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45554.99 | 735559.3053 | 53.74 | 100%
[5 empty] | 53.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45577.7513 | 735926.8249 | 53.76 | 100%
[5 empty] | 53.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45600.5127 | 736294.3444 | 53.78 | 100%
[5 empty] | 53.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45623.2741 | 736661.8639 | 53.8 | 100%
[5 empty] | 53.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45646.0355 | 737029.3834 | 53.82 | 100%
[5 empty] | 53.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45668.7969 | 737396.9029 | 53.84 | 100%
[5 empty] | 53.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45691.5583 | 737764.4225 | 53.86 | 100%
[5 empty] | 53.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45714.3196 | 738131.942 | 53.88 | 100%
[5 empty] | 53.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45737.081 | 738499.4615 | 53.9 | 100%
[5 empty] | 53.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45759.8424 | 738866.981 | 53.92 | 100%
[5 empty] | 53.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45782.6038 | 739234.5005 | 53.94 | 100%
[5 empty] | 53.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45805.3652 | 739602.0201 | 53.96 | 100%
[5 empty] | 53.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45828.1266 | 739969.5396 | 53.98 | 100%
[5 empty] | 54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45850.888 | 740337.0591 | 54 | 100%
[5 empty] | 54.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45873.6493 | 740704.5786 | 54.02 | 100%
[5 empty] | 54.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45896.4107 | 741072.0981 | 54.04 | 100%
[5 empty] | 54.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45919.1721 | 741439.6177 | 54.06 | 100%
[5 empty] | 54.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45941.9335 | 741807.1372 | 54.08 | 100%
[5 empty] | 54.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45964.6949 | 742174.6567 | 54.1 | 100%
[5 empty] | 54.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 45987.4563 | 742542.1762 | 54.12 | 100%
[5 empty] | 54.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46010.2176 | 742909.6957 | 54.14 | 100%
[5 empty] | 54.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46032.979 | 743277.2153 | 54.16 | 100%
[5 empty] | 54.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46055.7404 | 743644.7348 | 54.18 | 100%
[5 empty] | 54.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46078.5018 | 744012.2543 | 54.2 | 100%
[5 empty] | 54.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46101.2632 | 744379.7738 | 54.22 | 100%
[5 empty] | 54.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46124.0246 | 744747.2933 | 54.24 | 100%
[5 empty] | 54.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46146.786 | 745114.8129 | 54.26 | 100%
[5 empty] | 54.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46169.5473 | 745482.3324 | 54.28 | 100%
[5 empty] | 54.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46192.3087 | 745849.8519 | 54.3 | 100%
[5 empty] | 54.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46215.0701 | 746217.3714 | 54.32 | 100%
[5 empty] | 54.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46237.8315 | 746584.8909 | 54.34 | 100%
[5 empty] | 54.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46260.5929 | 746952.4105 | 54.36 | 100%
[5 empty] | 54.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46283.3543 | 747319.93 | 54.38 | 100%
[5 empty] | 54.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46306.1156 | 747687.4495 | 54.4 | 100%
[5 empty] | 54.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46328.877 | 748054.969 | 54.42 | 100%
[5 empty] | 54.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46351.6384 | 748422.4885 | 54.44 | 100%
[5 empty] | 54.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46374.3998 | 748790.0081 | 54.46 | 100%
[5 empty] | 54.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46397.1612 | 749157.5276 | 54.48 | 100%
[5 empty] | 54.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46419.9226 | 749525.0471 | 54.5 | 100%
[5 empty] | 54.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46442.6839 | 749892.5666 | 54.52 | 100%
[5 empty] | 54.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46465.4453 | 750260.0861 | 54.54 | 100%
[5 empty] | 54.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46488.2067 | 750627.6057 | 54.56 | 100%
[5 empty] | 54.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46510.9681 | 750995.1252 | 54.58 | 100%
[5 empty] | 54.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46533.7295 | 751362.6447 | 54.6 | 100%
[5 empty] | 54.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46556.4909 | 751730.1642 | 54.62 | 100%
[5 empty] | 54.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46579.2523 | 752097.6837 | 54.64 | 100%
[5 empty] | 54.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46602.0136 | 752465.2033 | 54.66 | 100%
[5 empty] | 54.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46624.775 | 752832.7228 | 54.68 | 100%
[5 empty] | 54.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46647.5364 | 753200.2423 | 54.7 | 100%
[5 empty] | 54.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46670.2978 | 753567.7618 | 54.72 | 100%
[5 empty] | 54.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46693.0592 | 753935.2813 | 54.74 | 100%
[5 empty] | 54.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46715.8206 | 754302.8009 | 54.76 | 100%
[5 empty] | 54.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46738.5819 | 754670.3204 | 54.78 | 100%
[5 empty] | 54.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46761.3433 | 755037.8399 | 54.8 | 100%
[5 empty] | 54.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46784.1047 | 755405.3594 | 54.82 | 100%
[5 empty] | 54.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46806.8661 | 755772.8789 | 54.84 | 100%
[5 empty] | 54.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46829.6275 | 756140.3985 | 54.86 | 100%
[5 empty] | 54.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46852.3889 | 756507.918 | 54.88 | 100%
[5 empty] | 54.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46875.1502 | 756875.4375 | 54.9 | 100%
[5 empty] | 54.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46897.9116 | 757242.957 | 54.92 | 100%
[5 empty] | 54.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46920.673 | 757610.4765 | 54.94 | 100%
[5 empty] | 54.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46943.4344 | 757977.9961 | 54.96 | 100%
[5 empty] | 54.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46966.1958 | 758345.5156 | 54.98 | 100%
[5 empty] | 55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 46988.9572 | 758713.0351 | 55 | 100%
[5 empty] | 55.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47011.7186 | 759080.5546 | 55.02 | 100%
[5 empty] | 55.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47034.4799 | 759448.0741 | 55.04 | 100%
[5 empty] | 55.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47057.2413 | 759815.5937 | 55.06 | 100%
[5 empty] | 55.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47080.0027 | 760183.1132 | 55.08 | 100%
[5 empty] | 55.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47102.7641 | 760550.6327 | 55.1 | 100%
[5 empty] | 55.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47125.5255 | 760918.1522 | 55.12 | 100%
[5 empty] | 55.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47148.2869 | 761285.6717 | 55.14 | 100%
[5 empty] | 55.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47171.0482 | 761653.1913 | 55.16 | 100%
[5 empty] | 55.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47193.8096 | 762020.7108 | 55.18 | 100%
[5 empty] | 55.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47216.571 | 762388.2303 | 55.2 | 100%
[5 empty] | 55.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47239.3324 | 762755.7498 | 55.22 | 100%
[5 empty] | 55.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47262.0938 | 763123.2693 | 55.24 | 100%
[5 empty] | 55.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47284.8552 | 763490.7889 | 55.26 | 100%
[5 empty] | 55.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47307.6166 | 763858.3084 | 55.28 | 100%
[5 empty] | 55.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47330.3779 | 764225.8279 | 55.3 | 100%
[5 empty] | 55.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47353.1393 | 764593.3474 | 55.32 | 100%
[5 empty] | 55.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47375.9007 | 764960.8669 | 55.34 | 100%
[5 empty] | 55.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47398.6621 | 765328.3865 | 55.36 | 100%
[5 empty] | 55.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47421.4235 | 765695.906 | 55.38 | 100%
[5 empty] | 55.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47444.1849 | 766063.4255 | 55.4 | 100%
[5 empty] | 55.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47466.9462 | 766430.945 | 55.42 | 100%
[5 empty] | 55.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47489.7076 | 766798.4645 | 55.44 | 100%
[5 empty] | 55.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47512.469 | 767165.9841 | 55.46 | 100%
[5 empty] | 55.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47535.2304 | 767533.5036 | 55.48 | 100%
[5 empty] | 55.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47557.9918 | 767901.0231 | 55.5 | 100%
[5 empty] | 55.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47580.7532 | 768268.5426 | 55.52 | 100%
[5 empty] | 55.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47603.5145 | 768636.0621 | 55.54 | 100%
[5 empty] | 55.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47626.2759 | 769003.5817 | 55.56 | 100%
[5 empty] | 55.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47649.0373 | 769371.1012 | 55.58 | 100%
[5 empty] | 55.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47671.7987 | 769738.6207 | 55.6 | 100%
[5 empty] | 55.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47694.5601 | 770106.1402 | 55.62 | 100%
[5 empty] | 55.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47717.3215 | 770473.6597 | 55.64 | 100%
[5 empty] | 55.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47740.0829 | 770841.1793 | 55.66 | 100%
[5 empty] | 55.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47762.8442 | 771208.6988 | 55.68 | 100%
[5 empty] | 55.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47785.6056 | 771576.2183 | 55.7 | 100%
[5 empty] | 55.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47808.367 | 771943.7378 | 55.72 | 100%
[5 empty] | 55.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47831.1284 | 772311.2573 | 55.74 | 100%
[5 empty] | 55.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47853.8898 | 772678.7769 | 55.76 | 100%
[5 empty] | 55.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47876.6512 | 773046.2964 | 55.78 | 100%
[5 empty] | 55.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47899.4125 | 773413.8159 | 55.8 | 100%
[5 empty] | 55.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47922.1739 | 773781.3354 | 55.82 | 100%
[5 empty] | 55.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47944.9353 | 774148.8549 | 55.84 | 100%
[5 empty] | 55.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47967.6967 | 774516.3745 | 55.86 | 100%
[5 empty] | 55.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 47990.4581 | 774883.894 | 55.88 | 100%
[5 empty] | 55.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48013.2195 | 775251.4135 | 55.9 | 100%
[5 empty] | 55.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48035.9808 | 775618.933 | 55.92 | 100%
[5 empty] | 55.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48058.7422 | 775986.4525 | 55.94 | 100%
[5 empty] | 55.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48081.5036 | 776353.9721 | 55.96 | 100%
[5 empty] | 55.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48104.265 | 776721.4916 | 55.98 | 100%
[5 empty] | 56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48127.0264 | 777089.0111 | 56 | 100%
[5 empty] | 56.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48149.7878 | 777456.5306 | 56.02 | 100%
[5 empty] | 56.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48172.5492 | 777824.0501 | 56.04 | 100%
[5 empty] | 56.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48195.3105 | 778191.5697 | 56.06 | 100%
[5 empty] | 56.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48218.0719 | 778559.0892 | 56.08 | 100%
[5 empty] | 56.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48240.8333 | 778926.6087 | 56.1 | 100%
[5 empty] | 56.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48263.5947 | 779294.1282 | 56.12 | 100%
[5 empty] | 56.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48286.3561 | 779661.6477 | 56.14 | 100%
[5 empty] | 56.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48309.1175 | 780029.1673 | 56.16 | 100%
[5 empty] | 56.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48331.8788 | 780396.6868 | 56.18 | 100%
[5 empty] | 56.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48354.6402 | 780764.2063 | 56.2 | 100%
[5 empty] | 56.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48377.4016 | 781131.7258 | 56.22 | 100%
[5 empty] | 56.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48400.163 | 781499.2453 | 56.24 | 100%
[5 empty] | 56.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48422.9244 | 781866.7649 | 56.26 | 100%
[5 empty] | 56.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48445.6858 | 782234.2844 | 56.28 | 100%
[5 empty] | 56.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48468.4472 | 782601.8039 | 56.3 | 100%
[5 empty] | 56.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48491.2085 | 782969.3234 | 56.32 | 100%
[5 empty] | 56.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48513.9699 | 783336.8429 | 56.34 | 100%
[5 empty] | 56.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48536.7313 | 783704.3625 | 56.36 | 100%
[5 empty] | 56.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48559.4927 | 784071.882 | 56.38 | 100%
[5 empty] | 56.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48582.2541 | 784439.4015 | 56.4 | 100%
[5 empty] | 56.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48605.0155 | 784806.921 | 56.42 | 100%
[5 empty] | 56.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48627.7768 | 785174.4405 | 56.44 | 100%
[5 empty] | 56.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48650.5382 | 785541.9601 | 56.46 | 100%
[5 empty] | 56.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48673.2996 | 785909.4796 | 56.48 | 100%
[5 empty] | 56.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48696.061 | 786276.9991 | 56.5 | 100%
[5 empty] | 56.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48718.8224 | 786644.5186 | 56.52 | 100%
[5 empty] | 56.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48741.5838 | 787012.0381 | 56.54 | 100%
[5 empty] | 56.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48764.3451 | 787379.5577 | 56.56 | 100%
[5 empty] | 56.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48787.1065 | 787747.0772 | 56.58 | 100%
[5 empty] | 56.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48809.8679 | 788114.5967 | 56.6 | 100%
[5 empty] | 56.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48832.6293 | 788482.1162 | 56.62 | 100%
[5 empty] | 56.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48855.3907 | 788849.6357 | 56.64 | 100%
[5 empty] | 56.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48878.1521 | 789217.1553 | 56.66 | 100%
[5 empty] | 56.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48900.9135 | 789584.6748 | 56.68 | 100%
[5 empty] | 56.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48923.6748 | 789952.1943 | 56.7 | 100%
[5 empty] | 56.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48946.4362 | 790319.7138 | 56.72 | 100%
[5 empty] | 56.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48969.1976 | 790687.2333 | 56.74 | 100%
[5 empty] | 56.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 48991.959 | 791054.7529 | 56.76 | 100%
[5 empty] | 56.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49014.7204 | 791422.2724 | 56.78 | 100%
[5 empty] | 56.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49037.4818 | 791789.7919 | 56.8 | 100%
[5 empty] | 56.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49060.2431 | 792157.3114 | 56.82 | 100%
[5 empty] | 56.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49083.0045 | 792524.8309 | 56.84 | 100%
[5 empty] | 56.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49105.7659 | 792892.3505 | 56.86 | 100%
[5 empty] | 56.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49128.5273 | 793259.87 | 56.88 | 100%
[5 empty] | 56.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49151.2887 | 793627.3895 | 56.9 | 100%
[5 empty] | 56.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49174.0501 | 793994.909 | 56.92 | 100%
[5 empty] | 56.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49196.8115 | 794362.4285 | 56.94 | 100%
[5 empty] | 56.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49219.5728 | 794729.9481 | 56.96 | 100%
[5 empty] | 56.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49242.3342 | 795097.4676 | 56.98 | 100%
[5 empty] | 57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49265.0956 | 795464.9871 | 57 | 100%
[5 empty] | 57.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49287.857 | 795832.5066 | 57.02 | 100%
[5 empty] | 57.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49310.6184 | 796200.0261 | 57.04 | 100%
[5 empty] | 57.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49333.3798 | 796567.5457 | 57.06 | 100%
[5 empty] | 57.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49356.1411 | 796935.0652 | 57.08 | 100%
[5 empty] | 57.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49378.9025 | 797302.5847 | 57.1 | 100%
[5 empty] | 57.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49401.6639 | 797670.1042 | 57.12 | 100%
[5 empty] | 57.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49424.4253 | 798037.6237 | 57.14 | 100%
[5 empty] | 57.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49447.1867 | 798405.1433 | 57.16 | 100%
[5 empty] | 57.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49469.9481 | 798772.6628 | 57.18 | 100%
[5 empty] | 57.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49492.7094 | 799140.1823 | 57.2 | 100%
[5 empty] | 57.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49515.4708 | 799507.7018 | 57.22 | 100%
[5 empty] | 57.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49538.2322 | 799875.2213 | 57.24 | 100%
[5 empty] | 57.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49560.9936 | 800242.7409 | 57.26 | 100%
[5 empty] | 57.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49583.755 | 800610.2604 | 57.28 | 100%
[5 empty] | 57.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49606.5164 | 800977.7799 | 57.3 | 100%
[5 empty] | 57.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49629.2778 | 801345.2994 | 57.32 | 100%
[5 empty] | 57.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49652.0391 | 801712.8189 | 57.34 | 100%
[5 empty] | 57.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49674.8005 | 802080.3385 | 57.36 | 100%
[5 empty] | 57.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49697.5619 | 802447.858 | 57.38 | 100%
[5 empty] | 57.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49720.3233 | 802815.3775 | 57.4 | 100%
[5 empty] | 57.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49743.0847 | 803182.897 | 57.42 | 100%
[5 empty] | 57.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49765.8461 | 803550.4165 | 57.44 | 100%
[5 empty] | 57.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49788.6074 | 803917.9361 | 57.46 | 100%
[5 empty] | 57.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49811.3688 | 804285.4556 | 57.48 | 100%
[5 empty] | 57.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49834.1302 | 804652.9751 | 57.5 | 100%
[5 empty] | 57.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49856.8916 | 805020.4946 | 57.52 | 100%
[5 empty] | 57.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49879.653 | 805388.0141 | 57.54 | 100%
[5 empty] | 57.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49902.4144 | 805755.5337 | 57.56 | 100%
[5 empty] | 57.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49925.1757 | 806123.0532 | 57.58 | 100%
[5 empty] | 57.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49947.9371 | 806490.5727 | 57.6 | 100%
[5 empty] | 57.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49970.6985 | 806858.0922 | 57.62 | 100%
[5 empty] | 57.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 49993.4599 | 807225.6117 | 57.64 | 100%
[5 empty] | 57.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50016.2213 | 807593.1313 | 57.66 | 100%
[5 empty] | 57.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50038.9827 | 807960.6508 | 57.68 | 100%
[5 empty] | 57.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50061.7441 | 808328.1703 | 57.7 | 100%
[5 empty] | 57.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50084.5054 | 808695.6898 | 57.72 | 100%
[5 empty] | 57.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50107.2668 | 809063.2093 | 57.74 | 100%
[5 empty] | 57.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50130.0282 | 809430.7289 | 57.76 | 100%
[5 empty] | 57.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50152.7896 | 809798.2484 | 57.78 | 100%
[5 empty] | 57.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50175.551 | 810165.7679 | 57.8 | 100%
[5 empty] | 57.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50198.3124 | 810533.2874 | 57.82 | 100%
[5 empty] | 57.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50221.0737 | 810900.8069 | 57.84 | 100%
[5 empty] | 57.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50243.8351 | 811268.3265 | 57.86 | 100%
[5 empty] | 57.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50266.5965 | 811635.846 | 57.88 | 100%
[5 empty] | 57.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50289.3579 | 812003.3655 | 57.9 | 100%
[5 empty] | 57.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50312.1193 | 812370.885 | 57.92 | 100%
[5 empty] | 57.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50334.8807 | 812738.4045 | 57.94 | 100%
[5 empty] | 57.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50357.6421 | 813105.9241 | 57.96 | 100%
[5 empty] | 57.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50380.4034 | 813473.4436 | 57.98 | 100%
[5 empty] | 58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50403.1648 | 813840.9631 | 58 | 100%
[5 empty] | 58.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50425.9262 | 814208.4826 | 58.02 | 100%
[5 empty] | 58.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50448.6876 | 814576.0021 | 58.04 | 100%
[5 empty] | 58.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50471.449 | 814943.5217 | 58.06 | 100%
[5 empty] | 58.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50494.2104 | 815311.0412 | 58.08 | 100%
[5 empty] | 58.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50516.9717 | 815678.5607 | 58.1 | 100%
[5 empty] | 58.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50539.7331 | 816046.0802 | 58.12 | 100%
[5 empty] | 58.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50562.4945 | 816413.5997 | 58.14 | 100%
[5 empty] | 58.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50585.2559 | 816781.1193 | 58.16 | 100%
[5 empty] | 58.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50608.0173 | 817148.6388 | 58.18 | 100%
[5 empty] | 58.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50630.7787 | 817516.1583 | 58.2 | 100%
[5 empty] | 58.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50653.54 | 817883.6778 | 58.22 | 100%
[5 empty] | 58.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50676.3014 | 818251.1973 | 58.24 | 100%
[5 empty] | 58.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50699.0628 | 818618.7169 | 58.26 | 100%
[5 empty] | 58.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50721.8242 | 818986.2364 | 58.28 | 100%
[5 empty] | 58.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50744.5856 | 819353.7559 | 58.3 | 100%
[5 empty] | 58.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50767.347 | 819721.2754 | 58.32 | 100%
[5 empty] | 58.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50790.1084 | 820088.7949 | 58.34 | 100%
[5 empty] | 58.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50812.8697 | 820456.3145 | 58.36 | 100%
[5 empty] | 58.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50835.6311 | 820823.834 | 58.38 | 100%
[5 empty] | 58.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50858.3925 | 821191.3535 | 58.4 | 100%
[5 empty] | 58.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50881.1539 | 821558.873 | 58.42 | 100%
[5 empty] | 58.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50903.9153 | 821926.3925 | 58.44 | 100%
[5 empty] | 58.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50926.6767 | 822293.9121 | 58.46 | 100%
[5 empty] | 58.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50949.438 | 822661.4316 | 58.48 | 100%
[5 empty] | 58.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50972.1994 | 823028.9511 | 58.5 | 100%
[5 empty] | 58.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 50994.9608 | 823396.4706 | 58.52 | 100%
[5 empty] | 58.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51017.7222 | 823763.9901 | 58.54 | 100%
[5 empty] | 58.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51040.4836 | 824131.5097 | 58.56 | 100%
[5 empty] | 58.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51063.245 | 824499.0292 | 58.58 | 100%
[5 empty] | 58.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51086.0063 | 824866.5487 | 58.6 | 100%
[5 empty] | 58.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51108.7677 | 825234.0682 | 58.62 | 100%
[5 empty] | 58.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51131.5291 | 825601.5877 | 58.64 | 100%
[5 empty] | 58.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51154.2905 | 825969.1073 | 58.66 | 100%
[5 empty] | 58.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51177.0519 | 826336.6268 | 58.68 | 100%
[5 empty] | 58.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51199.8133 | 826704.1463 | 58.7 | 100%
[5 empty] | 58.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51222.5747 | 827071.6658 | 58.72 | 100%
[5 empty] | 58.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51245.336 | 827439.1853 | 58.74 | 100%
[5 empty] | 58.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51268.0974 | 827806.7049 | 58.76 | 100%
[5 empty] | 58.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51290.8588 | 828174.2244 | 58.78 | 100%
[5 empty] | 58.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51313.6202 | 828541.7439 | 58.8 | 100%
[5 empty] | 58.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51336.3816 | 828909.2634 | 58.82 | 100%
[5 empty] | 58.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51359.143 | 829276.7829 | 58.84 | 100%
[5 empty] | 58.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51381.9043 | 829644.3025 | 58.86 | 100%
[5 empty] | 58.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51404.6657 | 830011.822 | 58.88 | 100%
[5 empty] | 58.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51427.4271 | 830379.3415 | 58.9 | 100%
[5 empty] | 58.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51450.1885 | 830746.861 | 58.92 | 100%
[5 empty] | 58.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51472.9499 | 831114.3805 | 58.94 | 100%
[5 empty] | 58.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51495.7113 | 831481.9001 | 58.96 | 100%
[5 empty] | 58.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51518.4727 | 831849.4196 | 58.98 | 100%
[5 empty] | 59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51541.234 | 832216.9391 | 59 | 100%
[5 empty] | 59.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51563.9954 | 832584.4586 | 59.02 | 100%
[5 empty] | 59.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51586.7568 | 832951.9781 | 59.04 | 100%
[5 empty] | 59.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51609.5182 | 833319.4977 | 59.06 | 100%
[5 empty] | 59.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51632.2796 | 833687.0172 | 59.08 | 100%
[5 empty] | 59.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51655.041 | 834054.5367 | 59.1 | 100%
[5 empty] | 59.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51677.8023 | 834422.0562 | 59.12 | 100%
[5 empty] | 59.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51700.5637 | 834789.5757 | 59.14 | 100%
[5 empty] | 59.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51723.3251 | 835157.0953 | 59.16 | 100%
[5 empty] | 59.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51746.0865 | 835524.6148 | 59.18 | 100%
[5 empty] | 59.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51768.8479 | 835892.1343 | 59.2 | 100%
[5 empty] | 59.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51791.6093 | 836259.6538 | 59.22 | 100%
[5 empty] | 59.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51814.3706 | 836627.1733 | 59.24 | 100%
[5 empty] | 59.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51837.132 | 836994.6929 | 59.26 | 100%
[5 empty] | 59.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51859.8934 | 837362.2124 | 59.28 | 100%
[5 empty] | 59.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51882.6548 | 837729.7319 | 59.3 | 100%
[5 empty] | 59.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51905.4162 | 838097.2514 | 59.32 | 100%
[5 empty] | 59.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51928.1776 | 838464.7709 | 59.34 | 100%
[5 empty] | 59.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51950.939 | 838832.2905 | 59.36 | 100%
[5 empty] | 59.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51973.7003 | 839199.81 | 59.38 | 100%
[5 empty] | 59.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 51996.4617 | 839567.3295 | 59.4 | 100%
[5 empty] | 59.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52019.2231 | 839934.849 | 59.42 | 100%
[5 empty] | 59.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52041.9845 | 840302.3685 | 59.44 | 100%
[5 empty] | 59.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52064.7459 | 840669.8881 | 59.46 | 100%
[5 empty] | 59.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52087.5073 | 841037.4076 | 59.48 | 100%
[5 empty] | 59.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52110.2686 | 841404.9271 | 59.5 | 100%
[5 empty] | 59.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52133.03 | 841772.4466 | 59.52 | 100%
[5 empty] | 59.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52155.7914 | 842139.9661 | 59.54 | 100%
[5 empty] | 59.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52178.5528 | 842507.4857 | 59.56 | 100%
[5 empty] | 59.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52201.3142 | 842875.0052 | 59.58 | 100%
[5 empty] | 59.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52224.0756 | 843242.5247 | 59.6 | 100%
[5 empty] | 59.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52246.8369 | 843610.0442 | 59.62 | 100%
[5 empty] | 59.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52269.5983 | 843977.5637 | 59.64 | 100%
[5 empty] | 59.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52292.3597 | 844345.0833 | 59.66 | 100%
[5 empty] | 59.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52315.1211 | 844712.6028 | 59.68 | 100%
[5 empty] | 59.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52337.8825 | 845080.1223 | 59.7 | 100%
[5 empty] | 59.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52360.6439 | 845447.6418 | 59.72 | 100%
[5 empty] | 59.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52383.4053 | 845815.1613 | 59.74 | 100%
[5 empty] | 59.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52406.1666 | 846182.6809 | 59.76 | 100%
[5 empty] | 59.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52428.928 | 846550.2004 | 59.78 | 100%
[5 empty] | 59.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52451.6894 | 846917.7199 | 59.8 | 100%
[5 empty] | 59.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52474.4508 | 847285.2394 | 59.82 | 100%
[5 empty] | 59.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52497.2122 | 847652.7589 | 59.84 | 100%
[5 empty] | 59.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52519.9736 | 848020.2785 | 59.86 | 100%
[5 empty] | 59.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52542.7349 | 848387.798 | 59.88 | 100%
[5 empty] | 59.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52565.4963 | 848755.3175 | 59.9 | 100%
[5 empty] | 59.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52588.2577 | 849122.837 | 59.92 | 100%
[5 empty] | 59.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52611.0191 | 849490.3565 | 59.94 | 100%
[5 empty] | 59.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52633.7805 | 849857.8761 | 59.96 | 100%
[5 empty] | 59.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52656.5419 | 850225.3956 | 59.98 | 100%
[5 empty] | 60 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52679.3033 | 850592.9151 | 60 | 100%
[5 empty] | 60.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52702.0646 | 850960.4346 | 60.02 | 100%
[5 empty] | 60.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52724.826 | 851327.9541 | 60.04 | 100%
[5 empty] | 60.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52747.5874 | 851695.4737 | 60.06 | 100%
[5 empty] | 60.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52770.3488 | 852062.9932 | 60.08 | 100%
[5 empty] | 60.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52793.1102 | 852430.5127 | 60.1 | 100%
[5 empty] | 60.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52815.8716 | 852798.0322 | 60.12 | 100%
[5 empty] | 60.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52838.6329 | 853165.5517 | 60.14 | 100%
[5 empty] | 60.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52861.3943 | 853533.0713 | 60.16 | 100%
[5 empty] | 60.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52884.1557 | 853900.5908 | 60.18 | 100%
[5 empty] | 60.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52906.9171 | 854268.1103 | 60.2 | 100%
[5 empty] | 60.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52929.6785 | 854635.6298 | 60.22 | 100%
[5 empty] | 60.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52952.4399 | 855003.1493 | 60.24 | 100%
[5 empty] | 60.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52975.2012 | 855370.6689 | 60.26 | 100%
[5 empty] | 60.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 52997.9626 | 855738.1884 | 60.28 | 100%
[5 empty] | 60.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53020.724 | 856105.7079 | 60.3 | 100%
[5 empty] | 60.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53043.4854 | 856473.2274 | 60.32 | 100%
[5 empty] | 60.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53066.2468 | 856840.7469 | 60.34 | 100%
[5 empty] | 60.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53089.0082 | 857208.2665 | 60.36 | 100%
[5 empty] | 60.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53111.7696 | 857575.786 | 60.38 | 100%
[5 empty] | 60.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53134.5309 | 857943.3055 | 60.4 | 100%
[5 empty] | 60.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53157.2923 | 858310.825 | 60.42 | 100%
[5 empty] | 60.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53180.0537 | 858678.3445 | 60.44 | 100%
[5 empty] | 60.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53202.8151 | 859045.8641 | 60.46 | 100%
[5 empty] | 60.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53225.5765 | 859413.3836 | 60.48 | 100%
[5 empty] | 60.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53248.3379 | 859780.9031 | 60.5 | 100%
[5 empty] | 60.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53271.0992 | 860148.4226 | 60.52 | 100%
[5 empty] | 60.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53293.8606 | 860515.9421 | 60.54 | 100%
[5 empty] | 60.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53316.622 | 860883.4617 | 60.56 | 100%
[5 empty] | 60.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53339.3834 | 861250.9812 | 60.58 | 100%
[5 empty] | 60.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53362.1448 | 861618.5007 | 60.6 | 100%
[5 empty] | 60.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53384.9062 | 861986.0202 | 60.62 | 100%
[5 empty] | 60.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53407.6676 | 862353.5397 | 60.64 | 100%
[5 empty] | 60.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53430.4289 | 862721.0593 | 60.66 | 100%
[5 empty] | 60.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53453.1903 | 863088.5788 | 60.68 | 100%
[5 empty] | 60.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53475.9517 | 863456.0983 | 60.7 | 100%
[5 empty] | 60.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53498.7131 | 863823.6178 | 60.72 | 100%
[5 empty] | 60.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53521.4745 | 864191.1373 | 60.74 | 100%
[5 empty] | 60.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53544.2359 | 864558.6569 | 60.76 | 100%
[5 empty] | 60.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53566.9972 | 864926.1764 | 60.78 | 100%
[5 empty] | 60.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53589.7586 | 865293.6959 | 60.8 | 100%
[5 empty] | 60.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53612.52 | 865661.2154 | 60.82 | 100%
[5 empty] | 60.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53635.2814 | 866028.7349 | 60.84 | 100%
[5 empty] | 60.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53658.0428 | 866396.2545 | 60.86 | 100%
[5 empty] | 60.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53680.8042 | 866763.774 | 60.88 | 100%
[5 empty] | 60.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53703.5655 | 867131.2935 | 60.9 | 100%
[5 empty] | 60.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53726.3269 | 867498.813 | 60.92 | 100%
[5 empty] | 60.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53749.0883 | 867866.3325 | 60.94 | 100%
[5 empty] | 60.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53771.8497 | 868233.8521 | 60.96 | 100%
[5 empty] | 60.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53794.6111 | 868601.3716 | 60.98 | 100%
[5 empty] | 61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53817.3725 | 868968.8911 | 61 | 100%
[5 empty] | 61.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53840.1339 | 869336.4106 | 61.02 | 100%
[5 empty] | 61.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53862.8952 | 869703.9301 | 61.04 | 100%
[5 empty] | 61.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53885.6566 | 870071.4497 | 61.06 | 100%
[5 empty] | 61.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53908.418 | 870438.9692 | 61.08 | 100%
[5 empty] | 61.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53931.1794 | 870806.4887 | 61.1 | 100%
[5 empty] | 61.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53953.9408 | 871174.0082 | 61.12 | 100%
[5 empty] | 61.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53976.7022 | 871541.5277 | 61.14 | 100%
[5 empty] | 61.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 53999.4635 | 871909.0473 | 61.16 | 100%
[5 empty] | 61.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54022.2249 | 872276.5668 | 61.18 | 100%
[5 empty] | 61.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54044.9863 | 872644.0863 | 61.2 | 100%
[5 empty] | 61.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54067.7477 | 873011.6058 | 61.22 | 100%
[5 empty] | 61.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54090.5091 | 873379.1253 | 61.24 | 100%
[5 empty] | 61.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54113.2705 | 873746.6449 | 61.26 | 100%
[5 empty] | 61.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54136.0318 | 874114.1644 | 61.28 | 100%
[5 empty] | 61.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54158.7932 | 874481.6839 | 61.3 | 100%
[5 empty] | 61.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54181.5546 | 874849.2034 | 61.32 | 100%
[5 empty] | 61.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54204.316 | 875216.7229 | 61.34 | 100%
[5 empty] | 61.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54227.0774 | 875584.2425 | 61.36 | 100%
[5 empty] | 61.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54249.8388 | 875951.762 | 61.38 | 100%
[5 empty] | 61.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54272.6002 | 876319.2815 | 61.4 | 100%
[5 empty] | 61.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54295.3615 | 876686.801 | 61.42 | 100%
[5 empty] | 61.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54318.1229 | 877054.3205 | 61.44 | 100%
[5 empty] | 61.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54340.8843 | 877421.8401 | 61.46 | 100%
[5 empty] | 61.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54363.6457 | 877789.3596 | 61.48 | 100%
[5 empty] | 61.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54386.4071 | 878156.8791 | 61.5 | 100%
[5 empty] | 61.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54409.1685 | 878524.3986 | 61.52 | 100%
[5 empty] | 61.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54431.9298 | 878891.9181 | 61.54 | 100%
[5 empty] | 61.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54454.6912 | 879259.4377 | 61.56 | 100%
[5 empty] | 61.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54477.4526 | 879626.9572 | 61.58 | 100%
[5 empty] | 61.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54500.214 | 879994.4767 | 61.6 | 100%
[5 empty] | 61.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54522.9754 | 880361.9962 | 61.62 | 100%
[5 empty] | 61.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54545.7368 | 880729.5157 | 61.64 | 100%
[5 empty] | 61.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54568.4982 | 881097.0353 | 61.66 | 100%
[5 empty] | 61.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54591.2595 | 881464.5548 | 61.68 | 100%
[5 empty] | 61.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54614.0209 | 881832.0743 | 61.7 | 100%
[5 empty] | 61.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54636.7823 | 882199.5938 | 61.72 | 100%
[5 empty] | 61.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54659.5437 | 882567.1133 | 61.74 | 100%
[5 empty] | 61.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54682.3051 | 882934.6329 | 61.76 | 100%
[5 empty] | 61.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54705.0665 | 883302.1524 | 61.78 | 100%
[5 empty] | 61.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54727.8278 | 883669.6719 | 61.8 | 100%
[5 empty] | 61.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54750.5892 | 884037.1914 | 61.82 | 100%
[5 empty] | 61.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54773.3506 | 884404.7109 | 61.84 | 100%
[5 empty] | 61.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54796.112 | 884772.2305 | 61.86 | 100%
[5 empty] | 61.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54818.8734 | 885139.75 | 61.88 | 100%
[5 empty] | 61.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54841.6348 | 885507.2695 | 61.9 | 100%
[5 empty] | 61.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54864.3961 | 885874.789 | 61.92 | 100%
[5 empty] | 61.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54887.1575 | 886242.3085 | 61.94 | 100%
[5 empty] | 61.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54909.9189 | 886609.8281 | 61.96 | 100%
[5 empty] | 61.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54932.6803 | 886977.3476 | 61.98 | 100%
[5 empty] | 62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54955.4417 | 887344.8671 | 62 | 100%
[5 empty] | 62.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 54978.2031 | 887712.3866 | 62.02 | 100%
[5 empty] | 62.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55000.9645 | 888079.9061 | 62.04 | 100%
[5 empty] | 62.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55023.7258 | 888447.4257 | 62.06 | 100%
[5 empty] | 62.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55046.4872 | 888814.9452 | 62.08 | 100%
[5 empty] | 62.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55069.2486 | 889182.4647 | 62.1 | 100%
[5 empty] | 62.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55092.01 | 889549.9842 | 62.12 | 100%
[5 empty] | 62.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55114.7714 | 889917.5037 | 62.14 | 100%
[5 empty] | 62.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55137.5328 | 890285.0233 | 62.16 | 100%
[5 empty] | 62.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55160.2941 | 890652.5428 | 62.18 | 100%
[5 empty] | 62.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55183.0555 | 891020.0623 | 62.2 | 100%
[5 empty] | 62.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55205.8169 | 891387.5818 | 62.22 | 100%
[5 empty] | 62.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55228.5783 | 891755.1013 | 62.24 | 100%
[5 empty] | 62.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55251.3397 | 892122.6209 | 62.26 | 100%
[5 empty] | 62.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55274.1011 | 892490.1404 | 62.28 | 100%
[5 empty] | 62.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55296.8624 | 892857.6599 | 62.3 | 100%
[5 empty] | 62.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55319.6238 | 893225.1794 | 62.32 | 100%
[5 empty] | 62.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55342.3852 | 893592.6989 | 62.34 | 100%
[5 empty] | 62.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55365.1466 | 893960.2185 | 62.36 | 100%
[5 empty] | 62.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55387.908 | 894327.738 | 62.38 | 100%
[5 empty] | 62.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55410.6694 | 894695.2575 | 62.4 | 100%
[5 empty] | 62.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55433.4308 | 895062.777 | 62.42 | 100%
[5 empty] | 62.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55456.1921 | 895430.2965 | 62.44 | 100%
[5 empty] | 62.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55478.9535 | 895797.8161 | 62.46 | 100%
[5 empty] | 62.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55501.7149 | 896165.3356 | 62.48 | 100%
[5 empty] | 62.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55524.4763 | 896532.8551 | 62.5 | 100%
[5 empty] | 62.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55547.2377 | 896900.3746 | 62.52 | 100%
[5 empty] | 62.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55569.9991 | 897267.8941 | 62.54 | 100%
[5 empty] | 62.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55592.7604 | 897635.4137 | 62.56 | 100%
[5 empty] | 62.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55615.5218 | 898002.9332 | 62.58 | 100%
[5 empty] | 62.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55638.2832 | 898370.4527 | 62.6 | 100%
[5 empty] | 62.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55661.0446 | 898737.9722 | 62.62 | 100%
[5 empty] | 62.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55683.806 | 899105.4917 | 62.64 | 100%
[5 empty] | 62.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55706.5674 | 899473.0113 | 62.66 | 100%
[5 empty] | 62.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55729.3288 | 899840.5308 | 62.68 | 100%
[5 empty] | 62.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55752.0901 | 900208.0503 | 62.7 | 100%
[5 empty] | 62.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55774.8515 | 900575.5698 | 62.72 | 100%
[5 empty] | 62.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55797.6129 | 900943.0893 | 62.74 | 100%
[5 empty] | 62.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55820.3743 | 901310.6089 | 62.76 | 100%
[5 empty] | 62.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55843.1357 | 901678.1284 | 62.78 | 100%
[5 empty] | 62.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55865.8971 | 902045.6479 | 62.8 | 100%
[5 empty] | 62.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55888.6584 | 902413.1674 | 62.82 | 100%
[5 empty] | 62.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55911.4198 | 902780.6869 | 62.84 | 100%
[5 empty] | 62.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55934.1812 | 903148.2065 | 62.86 | 100%
[5 empty] | 62.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55956.9426 | 903515.726 | 62.88 | 100%
[5 empty] | 62.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 55979.704 | 903883.2455 | 62.9 | 100%
[5 empty] | 62.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56002.4654 | 904250.765 | 62.92 | 100%
[5 empty] | 62.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56025.2267 | 904618.2845 | 62.94 | 100%
[5 empty] | 62.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56047.9881 | 904985.8041 | 62.96 | 100%
[5 empty] | 62.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56070.7495 | 905353.3236 | 62.98 | 100%
[5 empty] | 63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56093.5109 | 905720.8431 | 63 | 100%
[5 empty] | 63.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56116.2723 | 906088.3626 | 63.02 | 100%
[5 empty] | 63.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56139.0337 | 906455.8821 | 63.04 | 100%
[5 empty] | 63.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56161.7951 | 906823.4017 | 63.06 | 100%
[5 empty] | 63.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56184.5564 | 907190.9212 | 63.08 | 100%
[5 empty] | 63.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56207.3178 | 907558.4407 | 63.1 | 100%
[5 empty] | 63.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56230.0792 | 907925.9602 | 63.12 | 100%
[5 empty] | 63.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56252.8406 | 908293.4797 | 63.14 | 100%
[5 empty] | 63.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56275.602 | 908660.9993 | 63.16 | 100%
[5 empty] | 63.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56298.3634 | 909028.5188 | 63.18 | 100%
[5 empty] | 63.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56321.1247 | 909396.0383 | 63.2 | 100%
[5 empty] | 63.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56343.8861 | 909763.5578 | 63.22 | 100%
[5 empty] | 63.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56366.6475 | 910131.0773 | 63.24 | 100%
[5 empty] | 63.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56389.4089 | 910498.5969 | 63.26 | 100%
[5 empty] | 63.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56412.1703 | 910866.1164 | 63.28 | 100%
[5 empty] | 63.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56434.9317 | 911233.6359 | 63.3 | 100%
[5 empty] | 63.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56457.693 | 911601.1554 | 63.32 | 100%
[5 empty] | 63.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56480.4544 | 911968.6749 | 63.34 | 100%
[5 empty] | 63.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56503.2158 | 912336.1945 | 63.36 | 100%
[5 empty] | 63.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56525.9772 | 912703.714 | 63.38 | 100%
[5 empty] | 63.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56548.7386 | 913071.2335 | 63.4 | 100%
[5 empty] | 63.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56571.5 | 913438.753 | 63.42 | 100%
[5 empty] | 63.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56594.2614 | 913806.2725 | 63.44 | 100%
[5 empty] | 63.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56617.0227 | 914173.7921 | 63.46 | 100%
[5 empty] | 63.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56639.7841 | 914541.3116 | 63.48 | 100%
[5 empty] | 63.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56662.5455 | 914908.8311 | 63.5 | 100%
[5 empty] | 63.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56685.3069 | 915276.3506 | 63.52 | 100%
[5 empty] | 63.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56708.0683 | 915643.8701 | 63.54 | 100%
[5 empty] | 63.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56730.8297 | 916011.3897 | 63.56 | 100%
[5 empty] | 63.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56753.591 | 916378.9092 | 63.58 | 100%
[5 empty] | 63.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56776.3524 | 916746.4287 | 63.6 | 100%
[5 empty] | 63.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56799.1138 | 917113.9482 | 63.62 | 100%
[5 empty] | 63.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56821.8752 | 917481.4677 | 63.64 | 100%
[5 empty] | 63.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56844.6366 | 917848.9873 | 63.66 | 100%
[5 empty] | 63.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56867.398 | 918216.5068 | 63.68 | 100%
[5 empty] | 63.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56890.1594 | 918584.0263 | 63.7 | 100%
[5 empty] | 63.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56912.9207 | 918951.5458 | 63.72 | 100%
[5 empty] | 63.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56935.6821 | 919319.0653 | 63.74 | 100%
[5 empty] | 63.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56958.4435 | 919686.5849 | 63.76 | 100%
[5 empty] | 63.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 56981.2049 | 920054.1044 | 63.78 | 100%
[5 empty] | 63.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57003.9663 | 920421.6239 | 63.8 | 100%
[5 empty] | 63.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57026.7277 | 920789.1434 | 63.82 | 100%
[5 empty] | 63.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57049.489 | 921156.6629 | 63.84 | 100%
[5 empty] | 63.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57072.2504 | 921524.1825 | 63.86 | 100%
[5 empty] | 63.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57095.0118 | 921891.702 | 63.88 | 100%
[5 empty] | 63.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57117.7732 | 922259.2215 | 63.9 | 100%
[5 empty] | 63.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57140.5346 | 922626.741 | 63.92 | 100%
[5 empty] | 63.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57163.296 | 922994.2605 | 63.94 | 100%
[5 empty] | 63.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57186.0573 | 923361.7801 | 63.96 | 100%
[5 empty] | 63.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57208.8187 | 923729.2996 | 63.98 | 100%
[5 empty] | 64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57231.5801 | 924096.8191 | 64 | 100%
[5 empty] | 64.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57254.3415 | 924464.3386 | 64.02 | 100%
[5 empty] | 64.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57277.1029 | 924831.8581 | 64.04 | 100%
[5 empty] | 64.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57299.8643 | 925199.3777 | 64.06 | 100%
[5 empty] | 64.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57322.6257 | 925566.8972 | 64.08 | 100%
[5 empty] | 64.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57345.387 | 925934.4167 | 64.1 | 100%
[5 empty] | 64.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57368.1484 | 926301.9362 | 64.12 | 100%
[5 empty] | 64.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57390.9098 | 926669.4557 | 64.14 | 100%
[5 empty] | 64.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57413.6712 | 927036.9753 | 64.16 | 100%
[5 empty] | 64.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57436.4326 | 927404.4948 | 64.18 | 100%
[5 empty] | 64.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57459.194 | 927772.0143 | 64.2 | 100%
[5 empty] | 64.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57481.9553 | 928139.5338 | 64.22 | 100%
[5 empty] | 64.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57504.7167 | 928507.0533 | 64.24 | 100%
[5 empty] | 64.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57527.4781 | 928874.5729 | 64.26 | 100%
[5 empty] | 64.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57550.2395 | 929242.0924 | 64.28 | 100%
[5 empty] | 64.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57573.0009 | 929609.6119 | 64.3 | 100%
[5 empty] | 64.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57595.7623 | 929977.1314 | 64.32 | 100%
[5 empty] | 64.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57618.5237 | 930344.6509 | 64.34 | 100%
[5 empty] | 64.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57641.285 | 930712.1705 | 64.36 | 100%
[5 empty] | 64.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57664.0464 | 931079.69 | 64.38 | 100%
[5 empty] | 64.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57686.8078 | 931447.2095 | 64.4 | 100%
[5 empty] | 64.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57709.5692 | 931814.729 | 64.42 | 100%
[5 empty] | 64.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57732.3306 | 932182.2485 | 64.44 | 100%
[5 empty] | 64.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57755.092 | 932549.7681 | 64.46 | 100%
[5 empty] | 64.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57777.8533 | 932917.2876 | 64.48 | 100%
[5 empty] | 64.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57800.6147 | 933284.8071 | 64.5 | 100%
[5 empty] | 64.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57823.3761 | 933652.3266 | 64.52 | 100%
[5 empty] | 64.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57846.1375 | 934019.8461 | 64.54 | 100%
[5 empty] | 64.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57868.8989 | 934387.3657 | 64.56 | 100%
[5 empty] | 64.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57891.6603 | 934754.8852 | 64.58 | 100%
[5 empty] | 64.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57914.4216 | 935122.4047 | 64.6 | 100%
[5 empty] | 64.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57937.183 | 935489.9242 | 64.62 | 100%
[5 empty] | 64.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57959.9444 | 935857.4437 | 64.64 | 100%
[5 empty] | 64.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 57982.7058 | 936224.9633 | 64.66 | 100%
[5 empty] | 64.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58005.4672 | 936592.4828 | 64.68 | 100%
[5 empty] | 64.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58028.2286 | 936960.0023 | 64.7 | 100%
[5 empty] | 64.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58050.99 | 937327.5218 | 64.72 | 100%
[5 empty] | 64.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58073.7513 | 937695.0413 | 64.74 | 100%
[5 empty] | 64.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58096.5127 | 938062.5609 | 64.76 | 100%
[5 empty] | 64.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58119.2741 | 938430.0804 | 64.78 | 100%
[5 empty] | 64.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58142.0355 | 938797.5999 | 64.8 | 100%
[5 empty] | 64.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58164.7969 | 939165.1194 | 64.82 | 100%
[5 empty] | 64.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58187.5583 | 939532.6389 | 64.84 | 100%
[5 empty] | 64.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58210.3196 | 939900.1585 | 64.86 | 100%
[5 empty] | 64.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58233.081 | 940267.678 | 64.88 | 100%
[5 empty] | 64.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58255.8424 | 940635.1975 | 64.9 | 100%
[5 empty] | 64.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58278.6038 | 941002.717 | 64.92 | 100%
[5 empty] | 64.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58301.3652 | 941370.2365 | 64.94 | 100%
[5 empty] | 64.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58324.1266 | 941737.7561 | 64.96 | 100%
[5 empty] | 64.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58346.8879 | 942105.2756 | 64.98 | 100%
[5 empty] | 65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58369.6493 | 942472.7951 | 65 | 100%
[5 empty] | 65.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58392.4107 | 942840.3146 | 65.02 | 100%
[5 empty] | 65.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58415.1721 | 943207.8341 | 65.04 | 100%
[5 empty] | 65.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58437.9335 | 943575.3537 | 65.06 | 100%
[5 empty] | 65.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58460.6949 | 943942.8732 | 65.08 | 100%
[5 empty] | 65.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58483.4563 | 944310.3927 | 65.1 | 100%
[5 empty] | 65.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58506.2176 | 944677.9122 | 65.12 | 100%
[5 empty] | 65.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58528.979 | 945045.4317 | 65.14 | 100%
[5 empty] | 65.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58551.7404 | 945412.9513 | 65.16 | 100%
[5 empty] | 65.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58574.5018 | 945780.4708 | 65.18 | 100%
[5 empty] | 65.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58597.2632 | 946147.9903 | 65.2 | 100%
[5 empty] | 65.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58620.0246 | 946515.5098 | 65.22 | 100%
[5 empty] | 65.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58642.7859 | 946883.0293 | 65.24 | 100%
[5 empty] | 65.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58665.5473 | 947250.5489 | 65.26 | 100%
[5 empty] | 65.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58688.3087 | 947618.0684 | 65.28 | 100%
[5 empty] | 65.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58711.0701 | 947985.5879 | 65.3 | 100%
[5 empty] | 65.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58733.8315 | 948353.1074 | 65.32 | 100%
[5 empty] | 65.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58756.5929 | 948720.6269 | 65.34 | 100%
[5 empty] | 65.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58779.3543 | 949088.1465 | 65.36 | 100%
[5 empty] | 65.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58802.1156 | 949455.666 | 65.38 | 100%
[5 empty] | 65.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58824.877 | 949823.1855 | 65.4 | 100%
[5 empty] | 65.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58847.6384 | 950190.705 | 65.42 | 100%
[5 empty] | 65.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58870.3998 | 950558.2245 | 65.44 | 100%
[5 empty] | 65.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58893.1612 | 950925.7441 | 65.46 | 100%
[5 empty] | 65.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58915.9226 | 951293.2636 | 65.48 | 100%
[5 empty] | 65.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58938.6839 | 951660.7831 | 65.5 | 100%
[5 empty] | 65.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58961.4453 | 952028.3026 | 65.52 | 100%
[5 empty] | 65.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 58984.2067 | 952395.8221 | 65.54 | 100%
[5 empty] | 65.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59006.9681 | 952763.3417 | 65.56 | 100%
[5 empty] | 65.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59029.7295 | 953130.8612 | 65.58 | 100%
[5 empty] | 65.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59052.4909 | 953498.3807 | 65.6 | 100%
[5 empty] | 65.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59075.2522 | 953865.9002 | 65.62 | 100%
[5 empty] | 65.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59098.0136 | 954233.4197 | 65.64 | 100%
[5 empty] | 65.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59120.775 | 954600.9393 | 65.66 | 100%
[5 empty] | 65.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59143.5364 | 954968.4588 | 65.68 | 100%
[5 empty] | 65.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59166.2978 | 955335.9783 | 65.7 | 100%
[5 empty] | 65.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59189.0592 | 955703.4978 | 65.72 | 100%
[5 empty] | 65.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59211.8206 | 956071.0173 | 65.74 | 100%
[5 empty] | 65.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59234.5819 | 956438.5369 | 65.76 | 100%
[5 empty] | 65.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59257.3433 | 956806.0564 | 65.78 | 100%
[5 empty] | 65.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59280.1047 | 957173.5759 | 65.8 | 100%
[5 empty] | 65.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59302.8661 | 957541.0954 | 65.82 | 100%
[5 empty] | 65.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59325.6275 | 957908.6149 | 65.84 | 100%
[5 empty] | 65.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59348.3889 | 958276.1345 | 65.86 | 100%
[5 empty] | 65.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59371.1502 | 958643.654 | 65.88 | 100%
[5 empty] | 65.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59393.9116 | 959011.1735 | 65.9 | 100%
[5 empty] | 65.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59416.673 | 959378.693 | 65.92 | 100%
[5 empty] | 65.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59439.4344 | 959746.2125 | 65.94 | 100%
[5 empty] | 65.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59462.1958 | 960113.7321 | 65.96 | 100%
[5 empty] | 65.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59484.9572 | 960481.2516 | 65.98 | 100%
[5 empty] | 66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59507.7185 | 960848.7711 | 66 | 100%
[5 empty] | 66.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59530.4799 | 961216.2906 | 66.02 | 100%
[5 empty] | 66.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59553.2413 | 961583.8101 | 66.04 | 100%
[5 empty] | 66.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59576.0027 | 961951.3297 | 66.06 | 100%
[5 empty] | 66.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59598.7641 | 962318.8492 | 66.08 | 100%
[5 empty] | 66.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59621.5255 | 962686.3687 | 66.1 | 100%
[5 empty] | 66.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59644.2869 | 963053.8882 | 66.12 | 100%
[5 empty] | 66.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59667.0482 | 963421.4077 | 66.14 | 100%
[5 empty] | 66.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59689.8096 | 963788.9273 | 66.16 | 100%
[5 empty] | 66.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59712.571 | 964156.4468 | 66.18 | 100%
[5 empty] | 66.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59735.3324 | 964523.9663 | 66.2 | 100%
[5 empty] | 66.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59758.0938 | 964891.4858 | 66.22 | 100%
[5 empty] | 66.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59780.8552 | 965259.0053 | 66.24 | 100%
[5 empty] | 66.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59803.6165 | 965626.5249 | 66.26 | 100%
[5 empty] | 66.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59826.3779 | 965994.0444 | 66.28 | 100%
[5 empty] | 66.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59849.1393 | 966361.5639 | 66.3 | 100%
[5 empty] | 66.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59871.9007 | 966729.0834 | 66.32 | 100%
[5 empty] | 66.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59894.6621 | 967096.6029 | 66.34 | 100%
[5 empty] | 66.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59917.4235 | 967464.1225 | 66.36 | 100%
[5 empty] | 66.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59940.1849 | 967831.642 | 66.38 | 100%
[5 empty] | 66.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59962.9462 | 968199.1615 | 66.4 | 100%
[5 empty] | 66.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 59985.7076 | 968566.681 | 66.42 | 100%
[5 empty] | 66.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60008.469 | 968934.2005 | 66.44 | 100%
[5 empty] | 66.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60031.2304 | 969301.7201 | 66.46 | 100%
[5 empty] | 66.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60053.9918 | 969669.2396 | 66.48 | 100%
[5 empty] | 66.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60076.7532 | 970036.7591 | 66.5 | 100%
[5 empty] | 66.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60099.5145 | 970404.2786 | 66.52 | 100%
[5 empty] | 66.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60122.2759 | 970771.7981 | 66.54 | 100%
[5 empty] | 66.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60145.0373 | 971139.3177 | 66.56 | 100%
[5 empty] | 66.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60167.7987 | 971506.8372 | 66.58 | 100%
[5 empty] | 66.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60190.5601 | 971874.3567 | 66.6 | 100%
[5 empty] | 66.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60213.3215 | 972241.8762 | 66.62 | 100%
[5 empty] | 66.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60236.0828 | 972609.3957 | 66.64 | 100%
[5 empty] | 66.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60258.8442 | 972976.9153 | 66.66 | 100%
[5 empty] | 66.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60281.6056 | 973344.4348 | 66.68 | 100%
[5 empty] | 66.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60304.367 | 973711.9543 | 66.7 | 100%
[5 empty] | 66.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60327.1284 | 974079.4738 | 66.72 | 100%
[5 empty] | 66.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60349.8898 | 974446.9933 | 66.74 | 100%
[5 empty] | 66.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60372.6512 | 974814.5129 | 66.76 | 100%
[5 empty] | 66.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60395.4125 | 975182.0324 | 66.78 | 100%
[5 empty] | 66.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60418.1739 | 975549.5519 | 66.8 | 100%
[5 empty] | 66.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60440.9353 | 975917.0714 | 66.82 | 100%
[5 empty] | 66.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60463.6967 | 976284.5909 | 66.84 | 100%
[5 empty] | 66.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60486.4581 | 976652.1105 | 66.86 | 100%
[5 empty] | 66.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60509.2195 | 977019.63 | 66.88 | 100%
[5 empty] | 66.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60531.9808 | 977387.1495 | 66.9 | 100%
[5 empty] | 66.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60554.7422 | 977754.669 | 66.92 | 100%
[5 empty] | 66.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60577.5036 | 978122.1885 | 66.94 | 100%
[5 empty] | 66.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60600.265 | 978489.7081 | 66.96 | 100%
[5 empty] | 66.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60623.0264 | 978857.2276 | 66.98 | 100%
[5 empty] | 67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60645.7878 | 979224.7471 | 67 | 100%
[5 empty] | 67.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60668.5491 | 979592.2666 | 67.02 | 100%
[5 empty] | 67.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60691.3105 | 979959.7861 | 67.04 | 100%
[5 empty] | 67.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60714.0719 | 980327.3057 | 67.06 | 100%
[5 empty] | 67.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60736.8333 | 980694.8252 | 67.08 | 100%
[5 empty] | 67.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60759.5947 | 981062.3447 | 67.1 | 100%
[5 empty] | 67.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60782.3561 | 981429.8642 | 67.12 | 100%
[5 empty] | 67.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60805.1175 | 981797.3837 | 67.14 | 100%
[5 empty] | 67.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60827.8788 | 982164.9033 | 67.16 | 100%
[5 empty] | 67.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60850.6402 | 982532.4228 | 67.18 | 100%
[5 empty] | 67.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60873.4016 | 982899.9423 | 67.2 | 100%
[5 empty] | 67.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60896.163 | 983267.4618 | 67.22 | 100%
[5 empty] | 67.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60918.9244 | 983634.9813 | 67.24 | 100%
[5 empty] | 67.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60941.6858 | 984002.5009 | 67.26 | 100%
[5 empty] | 67.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60964.4471 | 984370.0204 | 67.28 | 100%
[5 empty] | 67.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 60987.2085 | 984737.5399 | 67.3 | 100%
[5 empty] | 67.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61009.9699 | 985105.0594 | 67.32 | 100%
[5 empty] | 67.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61032.7313 | 985472.5789 | 67.34 | 100%
[5 empty] | 67.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61055.4927 | 985840.0985 | 67.36 | 100%
[5 empty] | 67.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61078.2541 | 986207.618 | 67.38 | 100%
[5 empty] | 67.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61101.0155 | 986575.1375 | 67.4 | 100%
[5 empty] | 67.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61123.7768 | 986942.657 | 67.42 | 100%
[5 empty] | 67.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61146.5382 | 987310.1765 | 67.44 | 100%
[5 empty] | 67.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61169.2996 | 987677.6961 | 67.46 | 100%
[5 empty] | 67.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61192.061 | 988045.2156 | 67.48 | 100%
[5 empty] | 67.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61214.8224 | 988412.7351 | 67.5 | 100%
[5 empty] | 67.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61237.5838 | 988780.2546 | 67.52 | 100%
[5 empty] | 67.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61260.3451 | 989147.7741 | 67.54 | 100%
[5 empty] | 67.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61283.1065 | 989515.2937 | 67.56 | 100%
[5 empty] | 67.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61305.8679 | 989882.8132 | 67.58 | 100%
[5 empty] | 67.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61328.6293 | 990250.3327 | 67.6 | 100%
[5 empty] | 67.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61351.3907 | 990617.8522 | 67.62 | 100%
[5 empty] | 67.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61374.1521 | 990985.3717 | 67.64 | 100%
[5 empty] | 67.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61396.9134 | 991352.8913 | 67.66 | 100%
[5 empty] | 67.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61419.6748 | 991720.4108 | 67.68 | 100%
[5 empty] | 67.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61442.4362 | 992087.9303 | 67.7 | 100%
[5 empty] | 67.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61465.1976 | 992455.4498 | 67.72 | 100%
[5 empty] | 67.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61487.959 | 992822.9693 | 67.74 | 100%
[5 empty] | 67.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61510.7204 | 993190.4889 | 67.76 | 100%
[5 empty] | 67.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61533.4818 | 993558.0084 | 67.78 | 100%
[5 empty] | 67.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61556.2431 | 993925.5279 | 67.8 | 100%
[5 empty] | 67.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61579.0045 | 994293.0474 | 67.82 | 100%
[5 empty] | 67.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61601.7659 | 994660.5669 | 67.84 | 100%
[5 empty] | 67.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61624.5273 | 995028.0865 | 67.86 | 100%
[5 empty] | 67.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61647.2887 | 995395.606 | 67.88 | 100%
[5 empty] | 67.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61670.0501 | 995763.1255 | 67.9 | 100%
[5 empty] | 67.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61692.8114 | 996130.645 | 67.92 | 100%
[5 empty] | 67.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61715.5728 | 996498.1645 | 67.94 | 100%
[5 empty] | 67.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61738.3342 | 996865.6841 | 67.96 | 100%
[5 empty] | 67.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61761.0956 | 997233.2036 | 67.98 | 100%
[5 empty] | 68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61783.857 | 997600.7231 | 68 | 100%
[5 empty] | 68.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61806.6184 | 997968.2426 | 68.02 | 100%
[5 empty] | 68.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61829.3798 | 998335.7621 | 68.04 | 100%
[5 empty] | 68.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61852.1411 | 998703.2817 | 68.06 | 100%
[5 empty] | 68.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61874.9025 | 999070.8012 | 68.08 | 100%
[5 empty] | 68.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61897.6639 | 999438.3207 | 68.1 | 100%
[5 empty] | 68.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61920.4253 | 999805.8402 | 68.12 | 100%
[5 empty] | 68.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61943.1867 | 1000173.3597 | 68.14 | 100%
[5 empty] | 68.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61965.9481 | 1000540.8793 | 68.16 | 100%
[5 empty] | 68.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 61988.7094 | 1000908.3988 | 68.18 | 100%
[5 empty] | 68.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62011.4708 | 1001275.9183 | 68.2 | 100%
[5 empty] | 68.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62034.2322 | 1001643.4378 | 68.22 | 100%
[5 empty] | 68.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62056.9936 | 1002010.9573 | 68.24 | 100%
[5 empty] | 68.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62079.755 | 1002378.4769 | 68.26 | 100%
[5 empty] | 68.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62102.5164 | 1002745.9964 | 68.28 | 100%
[5 empty] | 68.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62125.2777 | 1003113.5159 | 68.3 | 100%
[5 empty] | 68.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62148.0391 | 1003481.0354 | 68.32 | 100%
[5 empty] | 68.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62170.8005 | 1003848.5549 | 68.34 | 100%
[5 empty] | 68.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62193.5619 | 1004216.0745 | 68.36 | 100%
[5 empty] | 68.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62216.3233 | 1004583.594 | 68.38 | 100%
[5 empty] | 68.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62239.0847 | 1004951.1135 | 68.4 | 100%
[5 empty] | 68.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62261.8461 | 1005318.633 | 68.42 | 100%
[5 empty] | 68.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62284.6074 | 1005686.1525 | 68.44 | 100%
[5 empty] | 68.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62307.3688 | 1006053.6721 | 68.46 | 100%
[5 empty] | 68.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62330.1302 | 1006421.1916 | 68.48 | 100%
[5 empty] | 68.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62352.8916 | 1006788.7111 | 68.5 | 100%
[5 empty] | 68.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62375.653 | 1007156.2306 | 68.52 | 100%
[5 empty] | 68.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62398.4144 | 1007523.7501 | 68.54 | 100%
[5 empty] | 68.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62421.1757 | 1007891.2697 | 68.56 | 100%
[5 empty] | 68.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62443.9371 | 1008258.7892 | 68.58 | 100%
[5 empty] | 68.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62466.6985 | 1008626.3087 | 68.6 | 100%
[5 empty] | 68.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62489.4599 | 1008993.8282 | 68.62 | 100%
[5 empty] | 68.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62512.2213 | 1009361.3477 | 68.64 | 100%
[5 empty] | 68.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62534.9827 | 1009728.8673 | 68.66 | 100%
[5 empty] | 68.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62557.744 | 1010096.3868 | 68.68 | 100%
[5 empty] | 68.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62580.5054 | 1010463.9063 | 68.7 | 100%
[5 empty] | 68.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62603.2668 | 1010831.4258 | 68.72 | 100%
[5 empty] | 68.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62626.0282 | 1011198.9453 | 68.74 | 100%
[5 empty] | 68.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62648.7896 | 1011566.4649 | 68.76 | 100%
[5 empty] | 68.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62671.551 | 1011933.9844 | 68.78 | 100%
[5 empty] | 68.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62694.3124 | 1012301.5039 | 68.8 | 100%
[5 empty] | 68.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62717.0737 | 1012669.0234 | 68.82 | 100%
[5 empty] | 68.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62739.8351 | 1013036.5429 | 68.84 | 100%
[5 empty] | 68.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62762.5965 | 1013404.0625 | 68.86 | 100%
[5 empty] | 68.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62785.3579 | 1013771.582 | 68.88 | 100%
[5 empty] | 68.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62808.1193 | 1014139.1015 | 68.9 | 100%
[5 empty] | 68.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62830.8807 | 1014506.621 | 68.92 | 100%
[5 empty] | 68.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62853.642 | 1014874.1405 | 68.94 | 100%
[5 empty] | 68.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62876.4034 | 1015241.6601 | 68.96 | 100%
[5 empty] | 68.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62899.1648 | 1015609.1796 | 68.98 | 100%
[5 empty] | 69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62921.9262 | 1015976.6991 | 69 | 100%
[5 empty] | 69.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62944.6876 | 1016344.2186 | 69.02 | 100%
[5 empty] | 69.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62967.449 | 1016711.7381 | 69.04 | 100%
[5 empty] | 69.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 62990.2104 | 1017079.2577 | 69.06 | 100%
[5 empty] | 69.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63012.9717 | 1017446.7772 | 69.08 | 100%
[5 empty] | 69.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63035.7331 | 1017814.2967 | 69.1 | 100%
[5 empty] | 69.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63058.4945 | 1018181.8162 | 69.12 | 100%
[5 empty] | 69.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63081.2559 | 1018549.3357 | 69.14 | 100%
[5 empty] | 69.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63104.0173 | 1018916.8553 | 69.16 | 100%
[5 empty] | 69.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63126.7787 | 1019284.3748 | 69.18 | 100%
[5 empty] | 69.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63149.54 | 1019651.8943 | 69.2 | 100%
[5 empty] | 69.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63172.3014 | 1020019.4138 | 69.22 | 100%
[5 empty] | 69.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63195.0628 | 1020386.9333 | 69.24 | 100%
[5 empty] | 69.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63217.8242 | 1020754.4529 | 69.26 | 100%
[5 empty] | 69.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63240.5856 | 1021121.9724 | 69.28 | 100%
[5 empty] | 69.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63263.347 | 1021489.4919 | 69.3 | 100%
[5 empty] | 69.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63286.1083 | 1021857.0114 | 69.32 | 100%
[5 empty] | 69.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63308.8697 | 1022224.5309 | 69.34 | 100%
[5 empty] | 69.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63331.6311 | 1022592.0505 | 69.36 | 100%
[5 empty] | 69.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63354.3925 | 1022959.57 | 69.38 | 100%
[5 empty] | 69.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63377.1539 | 1023327.0895 | 69.4 | 100%
[5 empty] | 69.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63399.9153 | 1023694.609 | 69.42 | 100%
[5 empty] | 69.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63422.6767 | 1024062.1285 | 69.44 | 100%
[5 empty] | 69.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63445.438 | 1024429.6481 | 69.46 | 100%
[5 empty] | 69.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63468.1994 | 1024797.1676 | 69.48 | 100%
[5 empty] | 69.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63490.9608 | 1025164.6871 | 69.5 | 100%
[5 empty] | 69.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63513.7222 | 1025532.2066 | 69.52 | 100%
[5 empty] | 69.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63536.4836 | 1025899.7261 | 69.54 | 100%
[5 empty] | 69.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63559.245 | 1026267.2457 | 69.56 | 100%
[5 empty] | 69.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63582.0063 | 1026634.7652 | 69.58 | 100%
[5 empty] | 69.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63604.7677 | 1027002.2847 | 69.6 | 100%
[5 empty] | 69.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63627.5291 | 1027369.8042 | 69.62 | 100%
[5 empty] | 69.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63650.2905 | 1027737.3237 | 69.64 | 100%
[5 empty] | 69.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63673.0519 | 1028104.8433 | 69.66 | 100%
[5 empty] | 69.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63695.8133 | 1028472.3628 | 69.68 | 100%
[5 empty] | 69.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63718.5746 | 1028839.8823 | 69.7 | 100%
[5 empty] | 69.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63741.336 | 1029207.4018 | 69.72 | 100%
[5 empty] | 69.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63764.0974 | 1029574.9213 | 69.74 | 100%
[5 empty] | 69.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63786.8588 | 1029942.4409 | 69.76 | 100%
[5 empty] | 69.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63809.6202 | 1030309.9604 | 69.78 | 100%
[5 empty] | 69.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63832.3816 | 1030677.4799 | 69.8 | 100%
[5 empty] | 69.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63855.143 | 1031044.9994 | 69.82 | 100%
[5 empty] | 69.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63877.9043 | 1031412.5189 | 69.84 | 100%
[5 empty] | 69.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63900.6657 | 1031780.0385 | 69.86 | 100%
[5 empty] | 69.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63923.4271 | 1032147.558 | 69.88 | 100%
[5 empty] | 69.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63946.1885 | 1032515.0775 | 69.9 | 100%
[5 empty] | 69.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63968.9499 | 1032882.597 | 69.92 | 100%
[5 empty] | 69.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 63991.7113 | 1033250.1165 | 69.94 | 100%
[5 empty] | 69.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64014.4726 | 1033617.6361 | 69.96 | 100%
[5 empty] | 69.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64037.234 | 1033985.1556 | 69.98 | 100%
[5 empty] | 70 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64059.9954 | 1034352.6751 | 70 | 100%
[5 empty] | 70.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64082.7568 | 1034720.1946 | 70.02 | 100%
[5 empty] | 70.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64105.5182 | 1035087.7141 | 70.04 | 100%
[5 empty] | 70.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64128.2796 | 1035455.2337 | 70.06 | 100%
[5 empty] | 70.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64151.041 | 1035822.7532 | 70.08 | 100%
[5 empty] | 70.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64173.8023 | 1036190.2727 | 70.1 | 100%
[5 empty] | 70.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64196.5637 | 1036557.7922 | 70.12 | 100%
[5 empty] | 70.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64219.3251 | 1036925.3117 | 70.14 | 100%
[5 empty] | 70.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64242.0865 | 1037292.8313 | 70.16 | 100%
[5 empty] | 70.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64264.8479 | 1037660.3508 | 70.18 | 100%
[5 empty] | 70.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64287.6093 | 1038027.8703 | 70.2 | 100%
[5 empty] | 70.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64310.3706 | 1038395.3898 | 70.22 | 100%
[5 empty] | 70.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64333.132 | 1038762.9093 | 70.24 | 100%
[5 empty] | 70.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64355.8934 | 1039130.4289 | 70.26 | 100%
[5 empty] | 70.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64378.6548 | 1039497.9484 | 70.28 | 100%
[5 empty] | 70.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64401.4162 | 1039865.4679 | 70.3 | 100%
[5 empty] | 70.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64424.1776 | 1040232.9874 | 70.32 | 100%
[5 empty] | 70.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64446.9389 | 1040600.5069 | 70.34 | 100%
[5 empty] | 70.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64469.7003 | 1040968.0265 | 70.36 | 100%
[5 empty] | 70.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64492.4617 | 1041335.546 | 70.38 | 100%
[5 empty] | 70.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64515.2231 | 1041703.0655 | 70.4 | 100%
[5 empty] | 70.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64537.9845 | 1042070.585 | 70.42 | 100%
[5 empty] | 70.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64560.7459 | 1042438.1045 | 70.44 | 100%
[5 empty] | 70.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64583.5073 | 1042805.6241 | 70.46 | 100%
[5 empty] | 70.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64606.2686 | 1043173.1436 | 70.48 | 100%
[5 empty] | 70.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64629.03 | 1043540.6631 | 70.5 | 100%
[5 empty] | 70.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64651.7914 | 1043908.1826 | 70.52 | 100%
[5 empty] | 70.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64674.5528 | 1044275.7021 | 70.54 | 100%
[5 empty] | 70.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64697.3142 | 1044643.2217 | 70.56 | 100%
[5 empty] | 70.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64720.0756 | 1045010.7412 | 70.58 | 100%
[5 empty] | 70.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64742.8369 | 1045378.2607 | 70.6 | 100%
[5 empty] | 70.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64765.5983 | 1045745.7802 | 70.62 | 100%
[5 empty] | 70.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64788.3597 | 1046113.2997 | 70.64 | 100%
[5 empty] | 70.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64811.1211 | 1046480.8193 | 70.66 | 100%
[5 empty] | 70.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64833.8825 | 1046848.3388 | 70.68 | 100%
[5 empty] | 70.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64856.6439 | 1047215.8583 | 70.7 | 100%
[5 empty] | 70.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64879.4053 | 1047583.3778 | 70.72 | 100%
[5 empty] | 70.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64902.1666 | 1047950.8973 | 70.74 | 100%
[5 empty] | 70.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64924.928 | 1048318.4169 | 70.76 | 100%
[5 empty] | 70.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64947.6894 | 1048685.9364 | 70.78 | 100%
[5 empty] | 70.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64970.4508 | 1049053.4559 | 70.8 | 100%
[5 empty] | 70.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 64993.2122 | 1049420.9754 | 70.82 | 100%
[5 empty] | 70.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65015.9736 | 1049788.4949 | 70.84 | 100%
[5 empty] | 70.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65038.7349 | 1050156.0145 | 70.86 | 100%
[5 empty] | 70.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65061.4963 | 1050523.534 | 70.88 | 100%
[5 empty] | 70.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65084.2577 | 1050891.0535 | 70.9 | 100%
[5 empty] | 70.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65107.0191 | 1051258.573 | 70.92 | 100%
[5 empty] | 70.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65129.7805 | 1051626.0925 | 70.94 | 100%
[5 empty] | 70.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65152.5419 | 1051993.6121 | 70.96 | 100%
[5 empty] | 70.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65175.3032 | 1052361.1316 | 70.98 | 100%
[5 empty] | 71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65198.0646 | 1052728.6511 | 71 | 100%
[5 empty] | 71.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65220.826 | 1053096.1706 | 71.02 | 100%
[5 empty] | 71.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65243.5874 | 1053463.6901 | 71.04 | 100%
[5 empty] | 71.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65266.3488 | 1053831.2097 | 71.06 | 100%
[5 empty] | 71.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65289.1102 | 1054198.7292 | 71.08 | 100%
[5 empty] | 71.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65311.8716 | 1054566.2487 | 71.1 | 100%
[5 empty] | 71.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65334.6329 | 1054933.7682 | 71.12 | 100%
[5 empty] | 71.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65357.3943 | 1055301.2877 | 71.14 | 100%
[5 empty] | 71.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65380.1557 | 1055668.8073 | 71.16 | 100%
[5 empty] | 71.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65402.9171 | 1056036.3268 | 71.18 | 100%
[5 empty] | 71.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65425.6785 | 1056403.8463 | 71.2 | 100%
[5 empty] | 71.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65448.4399 | 1056771.3658 | 71.22 | 100%
[5 empty] | 71.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65471.2012 | 1057138.8853 | 71.24 | 100%
[5 empty] | 71.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65493.9626 | 1057506.4049 | 71.26 | 100%
[5 empty] | 71.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65516.724 | 1057873.9244 | 71.28 | 100%
[5 empty] | 71.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65539.4854 | 1058241.4439 | 71.3 | 100%
[5 empty] | 71.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65562.2468 | 1058608.9634 | 71.32 | 100%
[5 empty] | 71.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65585.0082 | 1058976.4829 | 71.34 | 100%
[5 empty] | 71.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65607.7695 | 1059344.0025 | 71.36 | 100%
[5 empty] | 71.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65630.5309 | 1059711.522 | 71.38 | 100%
[5 empty] | 71.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65653.2923 | 1060079.0415 | 71.4 | 100%
[5 empty] | 71.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65676.0537 | 1060446.561 | 71.42 | 100%
[5 empty] | 71.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65698.8151 | 1060814.0805 | 71.44 | 100%
[5 empty] | 71.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65721.5765 | 1061181.6001 | 71.46 | 100%
[5 empty] | 71.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65744.3379 | 1061549.1196 | 71.48 | 100%
[5 empty] | 71.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65767.0992 | 1061916.6391 | 71.5 | 100%
[5 empty] | 71.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65789.8606 | 1062284.1586 | 71.52 | 100%
[5 empty] | 71.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65812.622 | 1062651.6781 | 71.54 | 100%
[5 empty] | 71.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65835.3834 | 1063019.1977 | 71.56 | 100%
[5 empty] | 71.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65858.1448 | 1063386.7172 | 71.58 | 100%
[5 empty] | 71.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65880.9062 | 1063754.2367 | 71.6 | 100%
[5 empty] | 71.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65903.6675 | 1064121.7562 | 71.62 | 100%
[5 empty] | 71.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65926.4289 | 1064489.2757 | 71.64 | 100%
[5 empty] | 71.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65949.1903 | 1064856.7953 | 71.66 | 100%
[5 empty] | 71.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65971.9517 | 1065224.3148 | 71.68 | 100%
[5 empty] | 71.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 65994.7131 | 1065591.8343 | 71.7 | 100%
[5 empty] | 71.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66017.4745 | 1065959.3538 | 71.72 | 100%
[5 empty] | 71.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66040.2359 | 1066326.8733 | 71.74 | 100%
[5 empty] | 71.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66062.9972 | 1066694.3929 | 71.76 | 100%
[5 empty] | 71.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66085.7586 | 1067061.9124 | 71.78 | 100%
[5 empty] | 71.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66108.52 | 1067429.4319 | 71.8 | 100%
[5 empty] | 71.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66131.2814 | 1067796.9514 | 71.82 | 100%
[5 empty] | 71.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66154.0428 | 1068164.4709 | 71.84 | 100%
[5 empty] | 71.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66176.8042 | 1068531.9905 | 71.86 | 100%
[5 empty] | 71.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66199.5655 | 1068899.51 | 71.88 | 100%
[5 empty] | 71.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66222.3269 | 1069267.0295 | 71.9 | 100%
[5 empty] | 71.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66245.0883 | 1069634.549 | 71.92 | 100%
[5 empty] | 71.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66267.8497 | 1070002.0685 | 71.94 | 100%
[5 empty] | 71.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66290.6111 | 1070369.5881 | 71.96 | 100%
[5 empty] | 71.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66313.3725 | 1070737.1076 | 71.98 | 100%
[5 empty] | 72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66336.1338 | 1071104.6271 | 72 | 100%
[5 empty] | 72.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66358.8952 | 1071472.1466 | 72.02 | 100%
[5 empty] | 72.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66381.6566 | 1071839.6661 | 72.04 | 100%
[5 empty] | 72.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66404.418 | 1072207.1857 | 72.06 | 100%
[5 empty] | 72.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66427.1794 | 1072574.7052 | 72.08 | 100%
[5 empty] | 72.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66449.9408 | 1072942.2247 | 72.1 | 100%
[5 empty] | 72.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66472.7022 | 1073309.7442 | 72.12 | 100%
[5 empty] | 72.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66495.4635 | 1073677.2637 | 72.14 | 100%
[5 empty] | 72.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66518.2249 | 1074044.7833 | 72.16 | 100%
[5 empty] | 72.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66540.9863 | 1074412.3028 | 72.18 | 100%
[5 empty] | 72.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66563.7477 | 1074779.8223 | 72.2 | 100%
[5 empty] | 72.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66586.5091 | 1075147.3418 | 72.22 | 100%
[5 empty] | 72.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66609.2705 | 1075514.8613 | 72.24 | 100%
[5 empty] | 72.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66632.0318 | 1075882.3809 | 72.26 | 100%
[5 empty] | 72.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66654.7932 | 1076249.9004 | 72.28 | 100%
[5 empty] | 72.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66677.5546 | 1076617.4199 | 72.3 | 100%
[5 empty] | 72.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66700.316 | 1076984.9394 | 72.32 | 100%
[5 empty] | 72.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66723.0774 | 1077352.4589 | 72.34 | 100%
[5 empty] | 72.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66745.8388 | 1077719.9785 | 72.36 | 100%
[5 empty] | 72.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66768.6001 | 1078087.498 | 72.38 | 100%
[5 empty] | 72.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66791.3615 | 1078455.0175 | 72.4 | 100%
[5 empty] | 72.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66814.1229 | 1078822.537 | 72.42 | 100%
[5 empty] | 72.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66836.8843 | 1079190.0565 | 72.44 | 100%
[5 empty] | 72.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66859.6457 | 1079557.5761 | 72.46 | 100%
[5 empty] | 72.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66882.4071 | 1079925.0956 | 72.48 | 100%
[5 empty] | 72.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66905.1685 | 1080292.6151 | 72.5 | 100%
[5 empty] | 72.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66927.9298 | 1080660.1346 | 72.52 | 100%
[5 empty] | 72.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66950.6912 | 1081027.6541 | 72.54 | 100%
[5 empty] | 72.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66973.4526 | 1081395.1737 | 72.56 | 100%
[5 empty] | 72.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 66996.214 | 1081762.6932 | 72.58 | 100%
[5 empty] | 72.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67018.9754 | 1082130.2127 | 72.6 | 100%
[5 empty] | 72.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67041.7368 | 1082497.7322 | 72.62 | 100%
[5 empty] | 72.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67064.4981 | 1082865.2517 | 72.64 | 100%
[5 empty] | 72.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67087.2595 | 1083232.7713 | 72.66 | 100%
[5 empty] | 72.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67110.0209 | 1083600.2908 | 72.68 | 100%
[5 empty] | 72.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67132.7823 | 1083967.8103 | 72.7 | 100%
[5 empty] | 72.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67155.5437 | 1084335.3298 | 72.72 | 100%
[5 empty] | 72.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67178.3051 | 1084702.8493 | 72.74 | 100%
[5 empty] | 72.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67201.0665 | 1085070.3689 | 72.76 | 100%
[5 empty] | 72.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67223.8278 | 1085437.8884 | 72.78 | 100%
[5 empty] | 72.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67246.5892 | 1085805.4079 | 72.8 | 100%
[5 empty] | 72.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67269.3506 | 1086172.9274 | 72.82 | 100%
[5 empty] | 72.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67292.112 | 1086540.4469 | 72.84 | 100%
[5 empty] | 72.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67314.8734 | 1086907.9665 | 72.86 | 100%
[5 empty] | 72.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67337.6348 | 1087275.486 | 72.88 | 100%
[5 empty] | 72.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67360.3961 | 1087643.0055 | 72.9 | 100%
[5 empty] | 72.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67383.1575 | 1088010.525 | 72.92 | 100%
[5 empty] | 72.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67405.9189 | 1088378.0445 | 72.94 | 100%
[5 empty] | 72.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67428.6803 | 1088745.5641 | 72.96 | 100%
[5 empty] | 72.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67451.4417 | 1089113.0836 | 72.98 | 100%
[5 empty] | 73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67474.2031 | 1089480.6031 | 73 | 100%
[5 empty] | 73.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67496.9644 | 1089848.1226 | 73.02 | 100%
[5 empty] | 73.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67519.7258 | 1090215.6421 | 73.04 | 100%
[5 empty] | 73.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67542.4872 | 1090583.1617 | 73.06 | 100%
[5 empty] | 73.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67565.2486 | 1090950.6812 | 73.08 | 100%
[5 empty] | 73.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67588.01 | 1091318.2007 | 73.1 | 100%
[5 empty] | 73.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67610.7714 | 1091685.7202 | 73.12 | 100%
[5 empty] | 73.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67633.5328 | 1092053.2397 | 73.14 | 100%
[5 empty] | 73.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67656.2941 | 1092420.7593 | 73.16 | 100%
[5 empty] | 73.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67679.0555 | 1092788.2788 | 73.18 | 100%
[5 empty] | 73.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67701.8169 | 1093155.7983 | 73.2 | 100%
[5 empty] | 73.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67724.5783 | 1093523.3178 | 73.22 | 100%
[5 empty] | 73.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67747.3397 | 1093890.8373 | 73.24 | 100%
[5 empty] | 73.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67770.1011 | 1094258.3569 | 73.26 | 100%
[5 empty] | 73.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67792.8624 | 1094625.8764 | 73.28 | 100%
[5 empty] | 73.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67815.6238 | 1094993.3959 | 73.3 | 100%
[5 empty] | 73.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67838.3852 | 1095360.9154 | 73.32 | 100%
[5 empty] | 73.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67861.1466 | 1095728.4349 | 73.34 | 100%
[5 empty] | 73.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67883.908 | 1096095.9545 | 73.36 | 100%
[5 empty] | 73.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67906.6694 | 1096463.474 | 73.38 | 100%
[5 empty] | 73.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67929.4307 | 1096830.9935 | 73.4 | 100%
[5 empty] | 73.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67952.1921 | 1097198.513 | 73.42 | 100%
[5 empty] | 73.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67974.9535 | 1097566.0325 | 73.44 | 100%
[5 empty] | 73.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 67997.7149 | 1097933.5521 | 73.46 | 100%
[5 empty] | 73.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68020.4763 | 1098301.0716 | 73.48 | 100%
[5 empty] | 73.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68043.2377 | 1098668.5911 | 73.5 | 100%
[5 empty] | 73.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68065.9991 | 1099036.1106 | 73.52 | 100%
[5 empty] | 73.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68088.7604 | 1099403.6301 | 73.54 | 100%
[5 empty] | 73.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68111.5218 | 1099771.1497 | 73.56 | 100%
[5 empty] | 73.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68134.2832 | 1100138.6692 | 73.58 | 100%
[5 empty] | 73.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68157.0446 | 1100506.1887 | 73.6 | 100%
[5 empty] | 73.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68179.806 | 1100873.7082 | 73.62 | 100%
[5 empty] | 73.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68202.5674 | 1101241.2277 | 73.64 | 100%
[5 empty] | 73.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68225.3287 | 1101608.7473 | 73.66 | 100%
[5 empty] | 73.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68248.0901 | 1101976.2668 | 73.68 | 100%
[5 empty] | 73.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68270.8515 | 1102343.7863 | 73.7 | 100%
[5 empty] | 73.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68293.6129 | 1102711.3058 | 73.72 | 100%
[5 empty] | 73.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68316.3743 | 1103078.8253 | 73.74 | 100%
[5 empty] | 73.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68339.1357 | 1103446.3449 | 73.76 | 100%
[5 empty] | 73.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68361.8971 | 1103813.8644 | 73.78 | 100%
[5 empty] | 73.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68384.6584 | 1104181.3839 | 73.8 | 100%
[5 empty] | 73.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68407.4198 | 1104548.9034 | 73.82 | 100%
[5 empty] | 73.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68430.1812 | 1104916.4229 | 73.84 | 100%
[5 empty] | 73.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68452.9426 | 1105283.9425 | 73.86 | 100%
[5 empty] | 73.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68475.704 | 1105651.462 | 73.88 | 100%
[5 empty] | 73.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68498.4654 | 1106018.9815 | 73.9 | 100%
[5 empty] | 73.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68521.2267 | 1106386.501 | 73.92 | 100%
[5 empty] | 73.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68543.9881 | 1106754.0205 | 73.94 | 100%
[5 empty] | 73.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68566.7495 | 1107121.5401 | 73.96 | 100%
[5 empty] | 73.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68589.5109 | 1107489.0596 | 73.98 | 100%
[5 empty] | 74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68612.2723 | 1107856.5791 | 74 | 100%
[5 empty] | 74.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68635.0337 | 1108224.0986 | 74.02 | 100%
[5 empty] | 74.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68657.795 | 1108591.6181 | 74.04 | 100%
[5 empty] | 74.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68680.5564 | 1108959.1377 | 74.06 | 100%
[5 empty] | 74.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68703.3178 | 1109326.6572 | 74.08 | 100%
[5 empty] | 74.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68726.0792 | 1109694.1767 | 74.1 | 100%
[5 empty] | 74.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68748.8406 | 1110061.6962 | 74.12 | 100%
[5 empty] | 74.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68771.602 | 1110429.2157 | 74.14 | 100%
[5 empty] | 74.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68794.3634 | 1110796.7353 | 74.16 | 100%
[5 empty] | 74.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68817.1247 | 1111164.2548 | 74.18 | 100%
[5 empty] | 74.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68839.8861 | 1111531.7743 | 74.2 | 100%
[5 empty] | 74.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68862.6475 | 1111899.2938 | 74.22 | 100%
[5 empty] | 74.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68885.4089 | 1112266.8133 | 74.24 | 100%
[5 empty] | 74.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68908.1703 | 1112634.3329 | 74.26 | 100%
[5 empty] | 74.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68930.9317 | 1113001.8524 | 74.28 | 100%
[5 empty] | 74.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68953.693 | 1113369.3719 | 74.3 | 100%
[5 empty] | 74.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68976.4544 | 1113736.8914 | 74.32 | 100%
[5 empty] | 74.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 68999.2158 | 1114104.4109 | 74.34 | 100%
[5 empty] | 74.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69021.9772 | 1114471.9305 | 74.36 | 100%
[5 empty] | 74.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69044.7386 | 1114839.45 | 74.38 | 100%
[5 empty] | 74.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69067.5 | 1115206.9695 | 74.4 | 100%
[5 empty] | 74.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69090.2614 | 1115574.489 | 74.42 | 100%
[5 empty] | 74.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69113.0227 | 1115942.0085 | 74.44 | 100%
[5 empty] | 74.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69135.7841 | 1116309.5281 | 74.46 | 100%
[5 empty] | 74.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69158.5455 | 1116677.0476 | 74.48 | 100%
[5 empty] | 74.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69181.3069 | 1117044.5671 | 74.5 | 100%
[5 empty] | 74.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69204.0683 | 1117412.0866 | 74.52 | 100%
[5 empty] | 74.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69226.8297 | 1117779.6061 | 74.54 | 100%
[5 empty] | 74.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69249.591 | 1118147.1257 | 74.56 | 100%
[5 empty] | 74.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69272.3524 | 1118514.6452 | 74.58 | 100%
[5 empty] | 74.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69295.1138 | 1118882.1647 | 74.6 | 100%
[5 empty] | 74.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69317.8752 | 1119249.6842 | 74.62 | 100%
[5 empty] | 74.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69340.6366 | 1119617.2037 | 74.64 | 100%
[5 empty] | 74.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69363.398 | 1119984.7233 | 74.66 | 100%
[5 empty] | 74.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69386.1593 | 1120352.2428 | 74.68 | 100%
[5 empty] | 74.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69408.9207 | 1120719.7623 | 74.7 | 100%
[5 empty] | 74.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69431.6821 | 1121087.2818 | 74.72 | 100%
[5 empty] | 74.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69454.4435 | 1121454.8013 | 74.74 | 100%
[5 empty] | 74.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69477.2049 | 1121822.3209 | 74.76 | 100%
[5 empty] | 74.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69499.9663 | 1122189.8404 | 74.78 | 100%
[5 empty] | 74.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69522.7277 | 1122557.3599 | 74.8 | 100%
[5 empty] | 74.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69545.489 | 1122924.8794 | 74.82 | 100%
[5 empty] | 74.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69568.2504 | 1123292.3989 | 74.84 | 100%
[5 empty] | 74.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69591.0118 | 1123659.9185 | 74.86 | 100%
[5 empty] | 74.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69613.7732 | 1124027.438 | 74.88 | 100%
[5 empty] | 74.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69636.5346 | 1124394.9575 | 74.9 | 100%
[5 empty] | 74.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69659.296 | 1124762.477 | 74.92 | 100%
[5 empty] | 74.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69682.0573 | 1125129.9965 | 74.94 | 100%
[5 empty] | 74.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69704.8187 | 1125497.5161 | 74.96 | 100%
[5 empty] | 74.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69727.5801 | 1125865.0356 | 74.98 | 100%
[5 empty] | 75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69750.3415 | 1126232.5551 | 75 | 100%
[5 empty] | 75.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69773.1029 | 1126600.0746 | 75.02 | 100%
[5 empty] | 75.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69795.8643 | 1126967.5941 | 75.04 | 100%
[5 empty] | 75.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69818.6256 | 1127335.1137 | 75.06 | 100%
[5 empty] | 75.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69841.387 | 1127702.6332 | 75.08 | 100%
[5 empty] | 75.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69864.1484 | 1128070.1527 | 75.1 | 100%
[5 empty] | 75.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69886.9098 | 1128437.6722 | 75.12 | 100%
[5 empty] | 75.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69909.6712 | 1128805.1917 | 75.14 | 100%
[5 empty] | 75.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69932.4326 | 1129172.7113 | 75.16 | 100%
[5 empty] | 75.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69955.194 | 1129540.2308 | 75.18 | 100%
[5 empty] | 75.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 69977.9553 | 1129907.7503 | 75.2 | 100%
[5 empty] | 75.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70000.7167 | 1130275.2698 | 75.22 | 100%
[5 empty] | 75.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70023.4781 | 1130642.7893 | 75.24 | 100%
[5 empty] | 75.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70046.2395 | 1131010.3089 | 75.26 | 100%
[5 empty] | 75.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70069.0009 | 1131377.8284 | 75.28 | 100%
[5 empty] | 75.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70091.7623 | 1131745.3479 | 75.3 | 100%
[5 empty] | 75.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70114.5236 | 1132112.8674 | 75.32 | 100%
[5 empty] | 75.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70137.285 | 1132480.3869 | 75.34 | 100%
[5 empty] | 75.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70160.0464 | 1132847.9065 | 75.36 | 100%
[5 empty] | 75.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70182.8078 | 1133215.426 | 75.38 | 100%
[5 empty] | 75.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70205.5692 | 1133582.9455 | 75.4 | 100%
[5 empty] | 75.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70228.3306 | 1133950.465 | 75.42 | 100%
[5 empty] | 75.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70251.092 | 1134317.9845 | 75.44 | 100%
[5 empty] | 75.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70273.8533 | 1134685.5041 | 75.46 | 100%
[5 empty] | 75.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70296.6147 | 1135053.0236 | 75.48 | 100%
[5 empty] | 75.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70319.3761 | 1135420.5431 | 75.5 | 100%
[5 empty] | 75.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70342.1375 | 1135788.0626 | 75.52 | 100%
[5 empty] | 75.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70364.8989 | 1136155.5821 | 75.54 | 100%
[5 empty] | 75.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70387.6603 | 1136523.1017 | 75.56 | 100%
[5 empty] | 75.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70410.4216 | 1136890.6212 | 75.58 | 100%
[5 empty] | 75.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70433.183 | 1137258.1407 | 75.6 | 100%
[5 empty] | 75.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70455.9444 | 1137625.6602 | 75.62 | 100%
[5 empty] | 75.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70478.7058 | 1137993.1797 | 75.64 | 100%
[5 empty] | 75.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70501.4672 | 1138360.6993 | 75.66 | 100%
[5 empty] | 75.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70524.2286 | 1138728.2188 | 75.68 | 100%
[5 empty] | 75.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70546.9899 | 1139095.7383 | 75.7 | 100%
[5 empty] | 75.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70569.7513 | 1139463.2578 | 75.72 | 100%
[5 empty] | 75.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70592.5127 | 1139830.7773 | 75.74 | 100%
[5 empty] | 75.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70615.2741 | 1140198.2969 | 75.76 | 100%
[5 empty] | 75.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70638.0355 | 1140565.8164 | 75.78 | 100%
[5 empty] | 75.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70660.7969 | 1140933.3359 | 75.8 | 100%
[5 empty] | 75.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70683.5583 | 1141300.8554 | 75.82 | 100%
[5 empty] | 75.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70706.3196 | 1141668.3749 | 75.84 | 100%
[5 empty] | 75.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70729.081 | 1142035.8945 | 75.86 | 100%
[5 empty] | 75.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70751.8424 | 1142403.414 | 75.88 | 100%
[5 empty] | 75.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70774.6038 | 1142770.9335 | 75.9 | 100%
[5 empty] | 75.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70797.3652 | 1143138.453 | 75.92 | 100%
[5 empty] | 75.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70820.1266 | 1143505.9725 | 75.94 | 100%
[5 empty] | 75.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70842.8879 | 1143873.4921 | 75.96 | 100%
[5 empty] | 75.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70865.6493 | 1144241.0116 | 75.98 | 100%
[5 empty] | 76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70888.4107 | 1144608.5311 | 76 | 100%
[5 empty] | 76.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70911.1721 | 1144976.0506 | 76.02 | 100%
[5 empty] | 76.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70933.9335 | 1145343.5701 | 76.04 | 100%
[5 empty] | 76.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70956.6949 | 1145711.0897 | 76.06 | 100%
[5 empty] | 76.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 70979.4562 | 1146078.6092 | 76.08 | 100%
[5 empty] | 76.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71002.2176 | 1146446.1287 | 76.1 | 100%
[5 empty] | 76.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71024.979 | 1146813.6482 | 76.12 | 100%
[5 empty] | 76.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71047.7404 | 1147181.1677 | 76.14 | 100%
[5 empty] | 76.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71070.5018 | 1147548.6873 | 76.16 | 100%
[5 empty] | 76.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71093.2632 | 1147916.2068 | 76.18 | 100%
[5 empty] | 76.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71116.0246 | 1148283.7263 | 76.2 | 100%
[5 empty] | 76.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71138.7859 | 1148651.2458 | 76.22 | 100%
[5 empty] | 76.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71161.5473 | 1149018.7653 | 76.24 | 100%
[5 empty] | 76.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71184.3087 | 1149386.2849 | 76.26 | 100%
[5 empty] | 76.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71207.0701 | 1149753.8044 | 76.28 | 100%
[5 empty] | 76.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71229.8315 | 1150121.3239 | 76.3 | 100%
[5 empty] | 76.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71252.5929 | 1150488.8434 | 76.32 | 100%
[5 empty] | 76.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71275.3542 | 1150856.3629 | 76.34 | 100%
[5 empty] | 76.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71298.1156 | 1151223.8825 | 76.36 | 100%
[5 empty] | 76.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71320.877 | 1151591.402 | 76.38 | 100%
[5 empty] | 76.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71343.6384 | 1151958.9215 | 76.4 | 100%
[5 empty] | 76.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71366.3998 | 1152326.441 | 76.42 | 100%
[5 empty] | 76.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71389.1612 | 1152693.9605 | 76.44 | 100%
[5 empty] | 76.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71411.9226 | 1153061.4801 | 76.46 | 100%
[5 empty] | 76.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71434.6839 | 1153428.9996 | 76.48 | 100%
[5 empty] | 76.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71457.4453 | 1153796.5191 | 76.5 | 100%
[5 empty] | 76.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71480.2067 | 1154164.0386 | 76.52 | 100%
[5 empty] | 76.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71502.9681 | 1154531.5581 | 76.54 | 100%
[5 empty] | 76.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71525.7295 | 1154899.0777 | 76.56 | 100%
[5 empty] | 76.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71548.4909 | 1155266.5972 | 76.58 | 100%
[5 empty] | 76.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71571.2522 | 1155634.1167 | 76.6 | 100%
[5 empty] | 76.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71594.0136 | 1156001.6362 | 76.62 | 100%
[5 empty] | 76.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71616.775 | 1156369.1557 | 76.64 | 100%
[5 empty] | 76.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71639.5364 | 1156736.6753 | 76.66 | 100%
[5 empty] | 76.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71662.2978 | 1157104.1948 | 76.68 | 100%
[5 empty] | 76.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71685.0592 | 1157471.7143 | 76.7 | 100%
[5 empty] | 76.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71707.8205 | 1157839.2338 | 76.72 | 100%
[5 empty] | 76.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71730.5819 | 1158206.7533 | 76.74 | 100%
[5 empty] | 76.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71753.3433 | 1158574.2729 | 76.76 | 100%
[5 empty] | 76.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71776.1047 | 1158941.7924 | 76.78 | 100%
[5 empty] | 76.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71798.8661 | 1159309.3119 | 76.8 | 100%
[5 empty] | 76.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71821.6275 | 1159676.8314 | 76.82 | 100%
[5 empty] | 76.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71844.3889 | 1160044.3509 | 76.84 | 100%
[5 empty] | 76.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71867.1502 | 1160411.8705 | 76.86 | 100%
[5 empty] | 76.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71889.9116 | 1160779.39 | 76.88 | 100%
[5 empty] | 76.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71912.673 | 1161146.9095 | 76.9 | 100%
[5 empty] | 76.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71935.4344 | 1161514.429 | 76.92 | 100%
[5 empty] | 76.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71958.1958 | 1161881.9485 | 76.94 | 100%
[5 empty] | 76.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 71980.9572 | 1162249.4681 | 76.96 | 100%
[5 empty] | 76.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72003.7185 | 1162616.9876 | 76.98 | 100%
[5 empty] | 77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72026.4799 | 1162984.5071 | 77 | 100%
[5 empty] | 77.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72049.2413 | 1163352.0266 | 77.02 | 100%
[5 empty] | 77.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72072.0027 | 1163719.5461 | 77.04 | 100%
[5 empty] | 77.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72094.7641 | 1164087.0657 | 77.06 | 100%
[5 empty] | 77.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72117.5255 | 1164454.5852 | 77.08 | 100%
[5 empty] | 77.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72140.2868 | 1164822.1047 | 77.1 | 100%
[5 empty] | 77.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72163.0482 | 1165189.6242 | 77.12 | 100%
[5 empty] | 77.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72185.8096 | 1165557.1437 | 77.14 | 100%
[5 empty] | 77.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72208.571 | 1165924.6633 | 77.16 | 100%
[5 empty] | 77.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72231.3324 | 1166292.1828 | 77.18 | 100%
[5 empty] | 77.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72254.0938 | 1166659.7023 | 77.2 | 100%
[5 empty] | 77.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72276.8552 | 1167027.2218 | 77.22 | 100%
[5 empty] | 77.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72299.6165 | 1167394.7413 | 77.24 | 100%
[5 empty] | 77.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72322.3779 | 1167762.2609 | 77.26 | 100%
[5 empty] | 77.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72345.1393 | 1168129.7804 | 77.28 | 100%
[5 empty] | 77.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72367.9007 | 1168497.2999 | 77.3 | 100%
[5 empty] | 77.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72390.6621 | 1168864.8194 | 77.32 | 100%
[5 empty] | 77.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72413.4235 | 1169232.3389 | 77.34 | 100%
[5 empty] | 77.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72436.1848 | 1169599.8585 | 77.36 | 100%
[5 empty] | 77.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72458.9462 | 1169967.378 | 77.38 | 100%
[5 empty] | 77.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72481.7076 | 1170334.8975 | 77.4 | 100%
[5 empty] | 77.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72504.469 | 1170702.417 | 77.42 | 100%
[5 empty] | 77.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72527.2304 | 1171069.9365 | 77.44 | 100%
[5 empty] | 77.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72549.9918 | 1171437.4561 | 77.46 | 100%
[5 empty] | 77.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72572.7532 | 1171804.9756 | 77.48 | 100%
[5 empty] | 77.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72595.5145 | 1172172.4951 | 77.5 | 100%
[5 empty] | 77.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72618.2759 | 1172540.0146 | 77.52 | 100%
[5 empty] | 77.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72641.0373 | 1172907.5341 | 77.54 | 100%
[5 empty] | 77.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72663.7987 | 1173275.0537 | 77.56 | 100%
[5 empty] | 77.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72686.5601 | 1173642.5732 | 77.58 | 100%
[5 empty] | 77.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72709.3215 | 1174010.0927 | 77.6 | 100%
[5 empty] | 77.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72732.0828 | 1174377.6122 | 77.62 | 100%
[5 empty] | 77.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72754.8442 | 1174745.1317 | 77.64 | 100%
[5 empty] | 77.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72777.6056 | 1175112.6513 | 77.66 | 100%
[5 empty] | 77.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72800.367 | 1175480.1708 | 77.68 | 100%
[5 empty] | 77.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72823.1284 | 1175847.6903 | 77.7 | 100%
[5 empty] | 77.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72845.8898 | 1176215.2098 | 77.72 | 100%
[5 empty] | 77.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72868.6511 | 1176582.7293 | 77.74 | 100%
[5 empty] | 77.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72891.4125 | 1176950.2489 | 77.76 | 100%
[5 empty] | 77.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72914.1739 | 1177317.7684 | 77.78 | 100%
[5 empty] | 77.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72936.9353 | 1177685.2879 | 77.8 | 100%
[5 empty] | 77.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72959.6967 | 1178052.8074 | 77.82 | 100%
[5 empty] | 77.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 72982.4581 | 1178420.3269 | 77.84 | 100%
[5 empty] | 77.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73005.2195 | 1178787.8465 | 77.86 | 100%
[5 empty] | 77.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73027.9808 | 1179155.366 | 77.88 | 100%
[5 empty] | 77.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73050.7422 | 1179522.8855 | 77.9 | 100%
[5 empty] | 77.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73073.5036 | 1179890.405 | 77.92 | 100%
[5 empty] | 77.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73096.265 | 1180257.9245 | 77.94 | 100%
[5 empty] | 77.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73119.0264 | 1180625.4441 | 77.96 | 100%
[5 empty] | 77.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73141.7878 | 1180992.9636 | 77.98 | 100%
[5 empty] | 78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73164.5491 | 1181360.4831 | 78 | 100%
[5 empty] | 78.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73187.3105 | 1181728.0026 | 78.02 | 100%
[5 empty] | 78.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73210.0719 | 1182095.5221 | 78.04 | 100%
[5 empty] | 78.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73232.8333 | 1182463.0417 | 78.06 | 100%
[5 empty] | 78.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73255.5947 | 1182830.5612 | 78.08 | 100%
[5 empty] | 78.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73278.3561 | 1183198.0807 | 78.1 | 100%
[5 empty] | 78.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73301.1175 | 1183565.6002 | 78.12 | 100%
[5 empty] | 78.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73323.8788 | 1183933.1197 | 78.14 | 100%
[5 empty] | 78.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73346.6402 | 1184300.6393 | 78.16 | 100%
[5 empty] | 78.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73369.4016 | 1184668.1588 | 78.18 | 100%
[5 empty] | 78.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73392.163 | 1185035.6783 | 78.2 | 100%
[5 empty] | 78.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73414.9244 | 1185403.1978 | 78.22 | 100%
[5 empty] | 78.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73437.6858 | 1185770.7173 | 78.24 | 100%
[5 empty] | 78.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73460.4471 | 1186138.2369 | 78.26 | 100%
[5 empty] | 78.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73483.2085 | 1186505.7564 | 78.28 | 100%
[5 empty] | 78.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73505.9699 | 1186873.2759 | 78.3 | 100%
[5 empty] | 78.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73528.7313 | 1187240.7954 | 78.32 | 100%
[5 empty] | 78.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73551.4927 | 1187608.3149 | 78.34 | 100%
[5 empty] | 78.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73574.2541 | 1187975.8345 | 78.36 | 100%
[5 empty] | 78.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73597.0154 | 1188343.354 | 78.38 | 100%
[5 empty] | 78.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73619.7768 | 1188710.8735 | 78.4 | 100%
[5 empty] | 78.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73642.5382 | 1189078.393 | 78.42 | 100%
[5 empty] | 78.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73665.2996 | 1189445.9125 | 78.44 | 100%
[5 empty] | 78.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73688.061 | 1189813.4321 | 78.46 | 100%
[5 empty] | 78.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73710.8224 | 1190180.9516 | 78.48 | 100%
[5 empty] | 78.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73733.5838 | 1190548.4711 | 78.5 | 100%
[5 empty] | 78.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73756.3451 | 1190915.9906 | 78.52 | 100%
[5 empty] | 78.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73779.1065 | 1191283.5101 | 78.54 | 100%
[5 empty] | 78.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73801.8679 | 1191651.0297 | 78.56 | 100%
[5 empty] | 78.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73824.6293 | 1192018.5492 | 78.58 | 100%
[5 empty] | 78.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73847.3907 | 1192386.0687 | 78.6 | 100%
[5 empty] | 78.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73870.1521 | 1192753.5882 | 78.62 | 100%
[5 empty] | 78.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73892.9134 | 1193121.1077 | 78.64 | 100%
[5 empty] | 78.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73915.6748 | 1193488.6273 | 78.66 | 100%
[5 empty] | 78.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73938.4362 | 1193856.1468 | 78.68 | 100%
[5 empty] | 78.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73961.1976 | 1194223.6663 | 78.7 | 100%
[5 empty] | 78.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 73983.959 | 1194591.1858 | 78.72 | 100%
[5 empty] | 78.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74006.7204 | 1194958.7053 | 78.74 | 100%
[5 empty] | 78.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74029.4817 | 1195326.2249 | 78.76 | 100%
[5 empty] | 78.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74052.2431 | 1195693.7444 | 78.78 | 100%
[5 empty] | 78.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74075.0045 | 1196061.2639 | 78.8 | 100%
[5 empty] | 78.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74097.7659 | 1196428.7834 | 78.82 | 100%
[5 empty] | 78.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74120.5273 | 1196796.3029 | 78.84 | 100%
[5 empty] | 78.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74143.2887 | 1197163.8225 | 78.86 | 100%
[5 empty] | 78.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74166.0501 | 1197531.342 | 78.88 | 100%
[5 empty] | 78.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74188.8114 | 1197898.8615 | 78.9 | 100%
[5 empty] | 78.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74211.5728 | 1198266.381 | 78.92 | 100%
[5 empty] | 78.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74234.3342 | 1198633.9005 | 78.94 | 100%
[5 empty] | 78.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74257.0956 | 1199001.4201 | 78.96 | 100%
[5 empty] | 78.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74279.857 | 1199368.9396 | 78.98 | 100%
[5 empty] | 79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74302.6184 | 1199736.4591 | 79 | 100%
[5 empty] | 79.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74325.3797 | 1200103.9786 | 79.02 | 100%
[5 empty] | 79.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74348.1411 | 1200471.4981 | 79.04 | 100%
[5 empty] | 79.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74370.9025 | 1200839.0177 | 79.06 | 100%
[5 empty] | 79.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74393.6639 | 1201206.5372 | 79.08 | 100%
[5 empty] | 79.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74416.4253 | 1201574.0567 | 79.1 | 100%
[5 empty] | 79.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74439.1867 | 1201941.5762 | 79.12 | 100%
[5 empty] | 79.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74461.9481 | 1202309.0957 | 79.14 | 100%
[5 empty] | 79.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74484.7094 | 1202676.6153 | 79.16 | 100%
[5 empty] | 79.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74507.4708 | 1203044.1348 | 79.18 | 100%
[5 empty] | 79.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74530.2322 | 1203411.6543 | 79.2 | 100%
[5 empty] | 79.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74552.9936 | 1203779.1738 | 79.22 | 100%
[5 empty] | 79.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74575.755 | 1204146.6933 | 79.24 | 100%
[5 empty] | 79.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74598.5164 | 1204514.2129 | 79.26 | 100%
[5 empty] | 79.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74621.2777 | 1204881.7324 | 79.28 | 100%
[5 empty] | 79.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74644.0391 | 1205249.2519 | 79.3 | 100%
[5 empty] | 79.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74666.8005 | 1205616.7714 | 79.32 | 100%
[5 empty] | 79.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74689.5619 | 1205984.2909 | 79.34 | 100%
[5 empty] | 79.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74712.3233 | 1206351.8105 | 79.36 | 100%
[5 empty] | 79.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74735.0847 | 1206719.33 | 79.38 | 100%
[5 empty] | 79.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74757.846 | 1207086.8495 | 79.4 | 100%
[5 empty] | 79.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74780.6074 | 1207454.369 | 79.42 | 100%
[5 empty] | 79.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74803.3688 | 1207821.8885 | 79.44 | 100%
[5 empty] | 79.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74826.1302 | 1208189.4081 | 79.46 | 100%
[5 empty] | 79.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74848.8916 | 1208556.9276 | 79.48 | 100%
[5 empty] | 79.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74871.653 | 1208924.4471 | 79.5 | 100%
[5 empty] | 79.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74894.4144 | 1209291.9666 | 79.52 | 100%
[5 empty] | 79.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74917.1757 | 1209659.4861 | 79.54 | 100%
[5 empty] | 79.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74939.9371 | 1210027.0057 | 79.56 | 100%
[5 empty] | 79.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74962.6985 | 1210394.5252 | 79.58 | 100%
[5 empty] | 79.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 74985.4599 | 1210762.0447 | 79.6 | 100%
[5 empty] | 79.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75008.2213 | 1211129.5642 | 79.62 | 100%
[5 empty] | 79.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75030.9827 | 1211497.0837 | 79.64 | 100%
[5 empty] | 79.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75053.744 | 1211864.6033 | 79.66 | 100%
[5 empty] | 79.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75076.5054 | 1212232.1228 | 79.68 | 100%
[5 empty] | 79.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75099.2668 | 1212599.6423 | 79.7 | 100%
[5 empty] | 79.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75122.0282 | 1212967.1618 | 79.72 | 100%
[5 empty] | 79.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75144.7896 | 1213334.6813 | 79.74 | 100%
[5 empty] | 79.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75167.551 | 1213702.2009 | 79.76 | 100%
[5 empty] | 79.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75190.3123 | 1214069.7204 | 79.78 | 100%
[5 empty] | 79.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75213.0737 | 1214437.2399 | 79.8 | 100%
[5 empty] | 79.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75235.8351 | 1214804.7594 | 79.82 | 100%
[5 empty] | 79.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75258.5965 | 1215172.2789 | 79.84 | 100%
[5 empty] | 79.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75281.3579 | 1215539.7985 | 79.86 | 100%
[5 empty] | 79.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75304.1193 | 1215907.318 | 79.88 | 100%
[5 empty] | 79.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75326.8807 | 1216274.8375 | 79.9 | 100%
[5 empty] | 79.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75349.642 | 1216642.357 | 79.92 | 100%
[5 empty] | 79.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75372.4034 | 1217009.8765 | 79.94 | 100%
[5 empty] | 79.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75395.1648 | 1217377.3961 | 79.96 | 100%
[5 empty] | 79.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75417.9262 | 1217744.9156 | 79.98 | 100%
[5 empty] | 80 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75440.6876 | 1218112.4351 | 80 | 100%
[5 empty] | 80.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75463.449 | 1218479.9546 | 80.02 | 100%
[5 empty] | 80.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75486.2103 | 1218847.4741 | 80.04 | 100%
[5 empty] | 80.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75508.9717 | 1219214.9937 | 80.06 | 100%
[5 empty] | 80.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75531.7331 | 1219582.5132 | 80.08 | 100%
[5 empty] | 80.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75554.4945 | 1219950.0327 | 80.1 | 100%
[5 empty] | 80.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75577.2559 | 1220317.5522 | 80.12 | 100%
[5 empty] | 80.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75600.0173 | 1220685.0717 | 80.14 | 100%
[5 empty] | 80.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75622.7787 | 1221052.5913 | 80.16 | 100%
[5 empty] | 80.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75645.54 | 1221420.1108 | 80.18 | 100%
[5 empty] | 80.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75668.3014 | 1221787.6303 | 80.2 | 100%
[5 empty] | 80.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75691.0628 | 1222155.1498 | 80.22 | 100%
[5 empty] | 80.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75713.8242 | 1222522.6693 | 80.24 | 100%
[5 empty] | 80.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75736.5856 | 1222890.1889 | 80.26 | 100%
[5 empty] | 80.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75759.347 | 1223257.7084 | 80.28 | 100%
[5 empty] | 80.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75782.1083 | 1223625.2279 | 80.3 | 100%
[5 empty] | 80.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75804.8697 | 1223992.7474 | 80.32 | 100%
[5 empty] | 80.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75827.6311 | 1224360.2669 | 80.34 | 100%
[5 empty] | 80.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75850.3925 | 1224727.7865 | 80.36 | 100%
[5 empty] | 80.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75873.1539 | 1225095.306 | 80.38 | 100%
[5 empty] | 80.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75895.9153 | 1225462.8255 | 80.4 | 100%
[5 empty] | 80.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75918.6766 | 1225830.345 | 80.42 | 100%
[5 empty] | 80.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75941.438 | 1226197.8645 | 80.44 | 100%
[5 empty] | 80.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75964.1994 | 1226565.3841 | 80.46 | 100%
[5 empty] | 80.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 75986.9608 | 1226932.9036 | 80.48 | 100%
[5 empty] | 80.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76009.7222 | 1227300.4231 | 80.5 | 100%
[5 empty] | 80.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76032.4836 | 1227667.9426 | 80.52 | 100%
[5 empty] | 80.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76055.245 | 1228035.4621 | 80.54 | 100%
[5 empty] | 80.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76078.0063 | 1228402.9817 | 80.56 | 100%
[5 empty] | 80.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76100.7677 | 1228770.5012 | 80.58 | 100%
[5 empty] | 80.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76123.5291 | 1229138.0207 | 80.6 | 100%
[5 empty] | 80.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76146.2905 | 1229505.5402 | 80.62 | 100%
[5 empty] | 80.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76169.0519 | 1229873.0597 | 80.64 | 100%
[5 empty] | 80.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76191.8133 | 1230240.5793 | 80.66 | 100%
[5 empty] | 80.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76214.5746 | 1230608.0988 | 80.68 | 100%
[5 empty] | 80.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76237.336 | 1230975.6183 | 80.7 | 100%
[5 empty] | 80.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76260.0974 | 1231343.1378 | 80.72 | 100%
[5 empty] | 80.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76282.8588 | 1231710.6573 | 80.74 | 100%
[5 empty] | 80.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76305.6202 | 1232078.1769 | 80.76 | 100%
[5 empty] | 80.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76328.3816 | 1232445.6964 | 80.78 | 100%
[5 empty] | 80.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76351.143 | 1232813.2159 | 80.8 | 100%
[5 empty] | 80.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76373.9043 | 1233180.7354 | 80.82 | 100%
[5 empty] | 80.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76396.6657 | 1233548.2549 | 80.84 | 100%
[5 empty] | 80.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76419.4271 | 1233915.7745 | 80.86 | 100%
[5 empty] | 80.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76442.1885 | 1234283.294 | 80.88 | 100%
[5 empty] | 80.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76464.9499 | 1234650.8135 | 80.9 | 100%
[5 empty] | 80.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76487.7113 | 1235018.333 | 80.92 | 100%
[5 empty] | 80.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76510.4726 | 1235385.8525 | 80.94 | 100%
[5 empty] | 80.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76533.234 | 1235753.3721 | 80.96 | 100%
[5 empty] | 80.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76555.9954 | 1236120.8916 | 80.98 | 100%
[5 empty] | 81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76578.7568 | 1236488.4111 | 81 | 100%
[5 empty] | 81.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76601.5182 | 1236855.9306 | 81.02 | 100%
[5 empty] | 81.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76624.2796 | 1237223.4501 | 81.04 | 100%
[5 empty] | 81.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76647.0409 | 1237590.9697 | 81.06 | 100%
[5 empty] | 81.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76669.8023 | 1237958.4892 | 81.08 | 100%
[5 empty] | 81.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76692.5637 | 1238326.0087 | 81.1 | 100%
[5 empty] | 81.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76715.3251 | 1238693.5282 | 81.12 | 100%
[5 empty] | 81.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76738.0865 | 1239061.0477 | 81.14 | 100%
[5 empty] | 81.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76760.8479 | 1239428.5673 | 81.16 | 100%
[5 empty] | 81.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76783.6093 | 1239796.0868 | 81.18 | 100%
[5 empty] | 81.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76806.3706 | 1240163.6063 | 81.2 | 100%
[5 empty] | 81.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76829.132 | 1240531.1258 | 81.22 | 100%
[5 empty] | 81.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76851.8934 | 1240898.6453 | 81.24 | 100%
[5 empty] | 81.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76874.6548 | 1241266.1649 | 81.26 | 100%
[5 empty] | 81.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76897.4162 | 1241633.6844 | 81.28 | 100%
[5 empty] | 81.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76920.1776 | 1242001.2039 | 81.3 | 100%
[5 empty] | 81.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76942.9389 | 1242368.7234 | 81.32 | 100%
[5 empty] | 81.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76965.7003 | 1242736.2429 | 81.34 | 100%
[5 empty] | 81.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 76988.4617 | 1243103.7625 | 81.36 | 100%
[5 empty] | 81.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77011.2231 | 1243471.282 | 81.38 | 100%
[5 empty] | 81.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77033.9845 | 1243838.8015 | 81.4 | 100%
[5 empty] | 81.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77056.7459 | 1244206.321 | 81.42 | 100%
[5 empty] | 81.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77079.5072 | 1244573.8405 | 81.44 | 100%
[5 empty] | 81.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77102.2686 | 1244941.3601 | 81.46 | 100%
[5 empty] | 81.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77125.03 | 1245308.8796 | 81.48 | 100%
[5 empty] | 81.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77147.7914 | 1245676.3991 | 81.5 | 100%
[5 empty] | 81.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77170.5528 | 1246043.9186 | 81.52 | 100%
[5 empty] | 81.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77193.3142 | 1246411.4381 | 81.54 | 100%
[5 empty] | 81.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77216.0756 | 1246778.9577 | 81.56 | 100%
[5 empty] | 81.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77238.8369 | 1247146.4772 | 81.58 | 100%
[5 empty] | 81.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77261.5983 | 1247513.9967 | 81.6 | 100%
[5 empty] | 81.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77284.3597 | 1247881.5162 | 81.62 | 100%
[5 empty] | 81.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77307.1211 | 1248249.0357 | 81.64 | 100%
[5 empty] | 81.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77329.8825 | 1248616.5553 | 81.66 | 100%
[5 empty] | 81.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77352.6439 | 1248984.0748 | 81.68 | 100%
[5 empty] | 81.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77375.4052 | 1249351.5943 | 81.7 | 100%
[5 empty] | 81.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77398.1666 | 1249719.1138 | 81.72 | 100%
[5 empty] | 81.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77420.928 | 1250086.6333 | 81.74 | 100%
[5 empty] | 81.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77443.6894 | 1250454.1529 | 81.76 | 100%
[5 empty] | 81.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77466.4508 | 1250821.6724 | 81.78 | 100%
[5 empty] | 81.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77489.2122 | 1251189.1919 | 81.8 | 100%
[5 empty] | 81.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77511.9736 | 1251556.7114 | 81.82 | 100%
[5 empty] | 81.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77534.7349 | 1251924.2309 | 81.84 | 100%
[5 empty] | 81.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77557.4963 | 1252291.7505 | 81.86 | 100%
[5 empty] | 81.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77580.2577 | 1252659.27 | 81.88 | 100%
[5 empty] | 81.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77603.0191 | 1253026.7895 | 81.9 | 100%
[5 empty] | 81.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77625.7805 | 1253394.309 | 81.92 | 100%
[5 empty] | 81.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77648.5419 | 1253761.8285 | 81.94 | 100%
[5 empty] | 81.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77671.3032 | 1254129.3481 | 81.96 | 100%
[5 empty] | 81.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77694.0646 | 1254496.8676 | 81.98 | 100%
[5 empty] | 82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77716.826 | 1254864.3871 | 82 | 100%
[5 empty] | 82.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77739.5874 | 1255231.9066 | 82.02 | 100%
[5 empty] | 82.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77762.3488 | 1255599.4261 | 82.04 | 100%
[5 empty] | 82.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77785.1102 | 1255966.9457 | 82.06 | 100%
[5 empty] | 82.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77807.8715 | 1256334.4652 | 82.08 | 100%
[5 empty] | 82.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77830.6329 | 1256701.9847 | 82.1 | 100%
[5 empty] | 82.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77853.3943 | 1257069.5042 | 82.12 | 100%
[5 empty] | 82.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77876.1557 | 1257437.0237 | 82.14 | 100%
[5 empty] | 82.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77898.9171 | 1257804.5433 | 82.16 | 100%
[5 empty] | 82.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77921.6785 | 1258172.0628 | 82.18 | 100%
[5 empty] | 82.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77944.4399 | 1258539.5823 | 82.2 | 100%
[5 empty] | 82.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77967.2012 | 1258907.1018 | 82.22 | 100%
[5 empty] | 82.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 77989.9626 | 1259274.6213 | 82.24 | 100%
[5 empty] | 82.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78012.724 | 1259642.1409 | 82.26 | 100%
[5 empty] | 82.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78035.4854 | 1260009.6604 | 82.28 | 100%
[5 empty] | 82.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78058.2468 | 1260377.1799 | 82.3 | 100%
[5 empty] | 82.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78081.0082 | 1260744.6994 | 82.32 | 100%
[5 empty] | 82.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78103.7695 | 1261112.2189 | 82.34 | 100%
[5 empty] | 82.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78126.5309 | 1261479.7385 | 82.36 | 100%
[5 empty] | 82.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78149.2923 | 1261847.258 | 82.38 | 100%
[5 empty] | 82.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78172.0537 | 1262214.7775 | 82.4 | 100%
[5 empty] | 82.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78194.8151 | 1262582.297 | 82.42 | 100%
[5 empty] | 82.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78217.5765 | 1262949.8165 | 82.44 | 100%
[5 empty] | 82.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78240.3378 | 1263317.3361 | 82.46 | 100%
[5 empty] | 82.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78263.0992 | 1263684.8556 | 82.48 | 100%
[5 empty] | 82.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78285.8606 | 1264052.3751 | 82.5 | 100%
[5 empty] | 82.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78308.622 | 1264419.8946 | 82.52 | 100%
[5 empty] | 82.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78331.3834 | 1264787.4141 | 82.54 | 100%
[5 empty] | 82.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78354.1448 | 1265154.9337 | 82.56 | 100%
[5 empty] | 82.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78376.9062 | 1265522.4532 | 82.58 | 100%
[5 empty] | 82.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78399.6675 | 1265889.9727 | 82.6 | 100%
[5 empty] | 82.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78422.4289 | 1266257.4922 | 82.62 | 100%
[5 empty] | 82.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78445.1903 | 1266625.0117 | 82.64 | 100%
[5 empty] | 82.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78467.9517 | 1266992.5313 | 82.66 | 100%
[5 empty] | 82.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78490.7131 | 1267360.0508 | 82.68 | 100%
[5 empty] | 82.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78513.4745 | 1267727.5703 | 82.7 | 100%
[5 empty] | 82.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78536.2358 | 1268095.0898 | 82.72 | 100%
[5 empty] | 82.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78558.9972 | 1268462.6093 | 82.74 | 100%
[5 empty] | 82.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78581.7586 | 1268830.1289 | 82.76 | 100%
[5 empty] | 82.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78604.52 | 1269197.6484 | 82.78 | 100%
[5 empty] | 82.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78627.2814 | 1269565.1679 | 82.8 | 100%
[5 empty] | 82.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78650.0428 | 1269932.6874 | 82.82 | 100%
[5 empty] | 82.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78672.8042 | 1270300.2069 | 82.84 | 100%
[5 empty] | 82.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78695.5655 | 1270667.7265 | 82.86 | 100%
[5 empty] | 82.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78718.3269 | 1271035.246 | 82.88 | 100%
[5 empty] | 82.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78741.0883 | 1271402.7655 | 82.9 | 100%
[5 empty] | 82.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78763.8497 | 1271770.285 | 82.92 | 100%
[5 empty] | 82.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78786.6111 | 1272137.8045 | 82.94 | 100%
[5 empty] | 82.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78809.3725 | 1272505.3241 | 82.96 | 100%
[5 empty] | 82.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78832.1338 | 1272872.8436 | 82.98 | 100%
[5 empty] | 83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78854.8952 | 1273240.3631 | 83 | 100%
[5 empty] | 83.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78877.6566 | 1273607.8826 | 83.02 | 100%
[5 empty] | 83.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78900.418 | 1273975.4021 | 83.04 | 100%
[5 empty] | 83.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78923.1794 | 1274342.9217 | 83.06 | 100%
[5 empty] | 83.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78945.9408 | 1274710.4412 | 83.08 | 100%
[5 empty] | 83.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78968.7021 | 1275077.9607 | 83.1 | 100%
[5 empty] | 83.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 78991.4635 | 1275445.4802 | 83.12 | 100%
[5 empty] | 83.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79014.2249 | 1275812.9997 | 83.14 | 100%
[5 empty] | 83.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79036.9863 | 1276180.5193 | 83.16 | 100%
[5 empty] | 83.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79059.7477 | 1276548.0388 | 83.18 | 100%
[5 empty] | 83.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79082.5091 | 1276915.5583 | 83.2 | 100%
[5 empty] | 83.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79105.2705 | 1277283.0778 | 83.22 | 100%
[5 empty] | 83.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79128.0318 | 1277650.5973 | 83.24 | 100%
[5 empty] | 83.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79150.7932 | 1278018.1169 | 83.26 | 100%
[5 empty] | 83.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79173.5546 | 1278385.6364 | 83.28 | 100%
[5 empty] | 83.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79196.316 | 1278753.1559 | 83.3 | 100%
[5 empty] | 83.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79219.0774 | 1279120.6754 | 83.32 | 100%
[5 empty] | 83.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79241.8388 | 1279488.1949 | 83.34 | 100%
[5 empty] | 83.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79264.6001 | 1279855.7145 | 83.36 | 100%
[5 empty] | 83.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79287.3615 | 1280223.234 | 83.38 | 100%
[5 empty] | 83.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79310.1229 | 1280590.7535 | 83.4 | 100%
[5 empty] | 83.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79332.8843 | 1280958.273 | 83.42 | 100%
[5 empty] | 83.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79355.6457 | 1281325.7925 | 83.44 | 100%
[5 empty] | 83.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79378.4071 | 1281693.3121 | 83.46 | 100%
[5 empty] | 83.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79401.1684 | 1282060.8316 | 83.48 | 100%
[5 empty] | 83.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79423.9298 | 1282428.3511 | 83.5 | 100%
[5 empty] | 83.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79446.6912 | 1282795.8706 | 83.52 | 100%
[5 empty] | 83.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79469.4526 | 1283163.3901 | 83.54 | 100%
[5 empty] | 83.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79492.214 | 1283530.9097 | 83.56 | 100%
[5 empty] | 83.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79514.9754 | 1283898.4292 | 83.58 | 100%
[5 empty] | 83.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79537.7368 | 1284265.9487 | 83.6 | 100%
[5 empty] | 83.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79560.4981 | 1284633.4682 | 83.62 | 100%
[5 empty] | 83.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79583.2595 | 1285000.9877 | 83.64 | 100%
[5 empty] | 83.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79606.0209 | 1285368.5073 | 83.66 | 100%
[5 empty] | 83.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79628.7823 | 1285736.0268 | 83.68 | 100%
[5 empty] | 83.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79651.5437 | 1286103.5463 | 83.7 | 100%
[5 empty] | 83.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79674.3051 | 1286471.0658 | 83.72 | 100%
[5 empty] | 83.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79697.0664 | 1286838.5853 | 83.74 | 100%
[5 empty] | 83.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79719.8278 | 1287206.1049 | 83.76 | 100%
[5 empty] | 83.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79742.5892 | 1287573.6244 | 83.78 | 100%
[5 empty] | 83.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79765.3506 | 1287941.1439 | 83.8 | 100%
[5 empty] | 83.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79788.112 | 1288308.6634 | 83.82 | 100%
[5 empty] | 83.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79810.8734 | 1288676.1829 | 83.84 | 100%
[5 empty] | 83.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79833.6348 | 1289043.7025 | 83.86 | 100%
[5 empty] | 83.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79856.3961 | 1289411.222 | 83.88 | 100%
[5 empty] | 83.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79879.1575 | 1289778.7415 | 83.9 | 100%
[5 empty] | 83.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79901.9189 | 1290146.261 | 83.92 | 100%
[5 empty] | 83.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79924.6803 | 1290513.7805 | 83.94 | 100%
[5 empty] | 83.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79947.4417 | 1290881.3001 | 83.96 | 100%
[5 empty] | 83.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79970.2031 | 1291248.8196 | 83.98 | 100%
[5 empty] | 84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 79992.9644 | 1291616.3391 | 84 | 100%
[5 empty] | 84.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80015.7258 | 1291983.8586 | 84.02 | 100%
[5 empty] | 84.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80038.4872 | 1292351.3781 | 84.04 | 100%
[5 empty] | 84.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80061.2486 | 1292718.8977 | 84.06 | 100%
[5 empty] | 84.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80084.01 | 1293086.4172 | 84.08 | 100%
[5 empty] | 84.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80106.7714 | 1293453.9367 | 84.1 | 100%
[5 empty] | 84.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80129.5327 | 1293821.4562 | 84.12 | 100%
[5 empty] | 84.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80152.2941 | 1294188.9757 | 84.14 | 100%
[5 empty] | 84.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80175.0555 | 1294556.4953 | 84.16 | 100%
[5 empty] | 84.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80197.8169 | 1294924.0148 | 84.18 | 100%
[5 empty] | 84.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80220.5783 | 1295291.5343 | 84.2 | 100%
[5 empty] | 84.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80243.3397 | 1295659.0538 | 84.22 | 100%
[5 empty] | 84.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80266.1011 | 1296026.5733 | 84.24 | 100%
[5 empty] | 84.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80288.8624 | 1296394.0929 | 84.26 | 100%
[5 empty] | 84.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80311.6238 | 1296761.6124 | 84.28 | 100%
[5 empty] | 84.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80334.3852 | 1297129.1319 | 84.3 | 100%
[5 empty] | 84.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80357.1466 | 1297496.6514 | 84.32 | 100%
[5 empty] | 84.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80379.908 | 1297864.1709 | 84.34 | 100%
[5 empty] | 84.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80402.6694 | 1298231.6905 | 84.36 | 100%
[5 empty] | 84.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80425.4307 | 1298599.21 | 84.38 | 100%
[5 empty] | 84.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80448.1921 | 1298966.7295 | 84.4 | 100%
[5 empty] | 84.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80470.9535 | 1299334.249 | 84.42 | 100%
[5 empty] | 84.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80493.7149 | 1299701.7685 | 84.44 | 100%
[5 empty] | 84.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80516.4763 | 1300069.2881 | 84.46 | 100%
[5 empty] | 84.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80539.2377 | 1300436.8076 | 84.48 | 100%
[5 empty] | 84.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80561.9991 | 1300804.3271 | 84.5 | 100%
[5 empty] | 84.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80584.7604 | 1301171.8466 | 84.52 | 100%
[5 empty] | 84.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80607.5218 | 1301539.3661 | 84.54 | 100%
[5 empty] | 84.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80630.2832 | 1301906.8857 | 84.56 | 100%
[5 empty] | 84.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80653.0446 | 1302274.4052 | 84.58 | 100%
[5 empty] | 84.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80675.806 | 1302641.9247 | 84.6 | 100%
[5 empty] | 84.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80698.5674 | 1303009.4442 | 84.62 | 100%
[5 empty] | 84.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80721.3287 | 1303376.9637 | 84.64 | 100%
[5 empty] | 84.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80744.0901 | 1303744.4833 | 84.66 | 100%
[5 empty] | 84.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80766.8515 | 1304112.0028 | 84.68 | 100%
[5 empty] | 84.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80789.6129 | 1304479.5223 | 84.7 | 100%
[5 empty] | 84.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80812.3743 | 1304847.0418 | 84.72 | 100%
[5 empty] | 84.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80835.1357 | 1305214.5613 | 84.74 | 100%
[5 empty] | 84.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80857.897 | 1305582.0809 | 84.76 | 100%
[5 empty] | 84.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80880.6584 | 1305949.6004 | 84.78 | 100%
[5 empty] | 84.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80903.4198 | 1306317.1199 | 84.8 | 100%
[5 empty] | 84.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80926.1812 | 1306684.6394 | 84.82 | 100%
[5 empty] | 84.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80948.9426 | 1307052.1589 | 84.84 | 100%
[5 empty] | 84.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80971.704 | 1307419.6785 | 84.86 | 100%
[5 empty] | 84.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 80994.4654 | 1307787.198 | 84.88 | 100%
[5 empty] | 84.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81017.2267 | 1308154.7175 | 84.9 | 100%
[5 empty] | 84.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81039.9881 | 1308522.237 | 84.92 | 100%
[5 empty] | 84.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81062.7495 | 1308889.7565 | 84.94 | 100%
[5 empty] | 84.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81085.5109 | 1309257.2761 | 84.96 | 100%
[5 empty] | 84.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81108.2723 | 1309624.7956 | 84.98 | 100%
[5 empty] | 85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81131.0337 | 1309992.3151 | 85 | 100%
[5 empty] | 85.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81153.795 | 1310359.8346 | 85.02 | 100%
[5 empty] | 85.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81176.5564 | 1310727.3541 | 85.04 | 100%
[5 empty] | 85.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81199.3178 | 1311094.8737 | 85.06 | 100%
[5 empty] | 85.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81222.0792 | 1311462.3932 | 85.08 | 100%
[5 empty] | 85.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81244.8406 | 1311829.9127 | 85.1 | 100%
[5 empty] | 85.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81267.602 | 1312197.4322 | 85.12 | 100%
[5 empty] | 85.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81290.3633 | 1312564.9517 | 85.14 | 100%
[5 empty] | 85.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81313.1247 | 1312932.4713 | 85.16 | 100%
[5 empty] | 85.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81335.8861 | 1313299.9908 | 85.18 | 100%
[5 empty] | 85.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81358.6475 | 1313667.5103 | 85.2 | 100%
[5 empty] | 85.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81381.4089 | 1314035.0298 | 85.22 | 100%
[5 empty] | 85.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81404.1703 | 1314402.5493 | 85.24 | 100%
[5 empty] | 85.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81426.9317 | 1314770.0689 | 85.26 | 100%
[5 empty] | 85.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81449.693 | 1315137.5884 | 85.28 | 100%
[5 empty] | 85.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81472.4544 | 1315505.1079 | 85.3 | 100%
[5 empty] | 85.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81495.2158 | 1315872.6274 | 85.32 | 100%
[5 empty] | 85.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81517.9772 | 1316240.1469 | 85.34 | 100%
[5 empty] | 85.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81540.7386 | 1316607.6665 | 85.36 | 100%
[5 empty] | 85.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81563.5 | 1316975.186 | 85.38 | 100%
[5 empty] | 85.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81586.2613 | 1317342.7055 | 85.4 | 100%
[5 empty] | 85.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81609.0227 | 1317710.225 | 85.42 | 100%
[5 empty] | 85.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81631.7841 | 1318077.7445 | 85.44 | 100%
[5 empty] | 85.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81654.5455 | 1318445.2641 | 85.46 | 100%
[5 empty] | 85.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81677.3069 | 1318812.7836 | 85.48 | 100%
[5 empty] | 85.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81700.0683 | 1319180.3031 | 85.5 | 100%
[5 empty] | 85.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81722.8297 | 1319547.8226 | 85.52 | 100%
[5 empty] | 85.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81745.591 | 1319915.3421 | 85.54 | 100%
[5 empty] | 85.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81768.3524 | 1320282.8617 | 85.56 | 100%
[5 empty] | 85.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81791.1138 | 1320650.3812 | 85.58 | 100%
[5 empty] | 85.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81813.8752 | 1321017.9007 | 85.6 | 100%
[5 empty] | 85.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81836.6366 | 1321385.4202 | 85.62 | 100%
[5 empty] | 85.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81859.398 | 1321752.9397 | 85.64 | 100%
[5 empty] | 85.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81882.1593 | 1322120.4593 | 85.66 | 100%
[5 empty] | 85.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81904.9207 | 1322487.9788 | 85.68 | 100%
[5 empty] | 85.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81927.6821 | 1322855.4983 | 85.7 | 100%
[5 empty] | 85.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81950.4435 | 1323223.0178 | 85.72 | 100%
[5 empty] | 85.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81973.2049 | 1323590.5373 | 85.74 | 100%
[5 empty] | 85.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 81995.9663 | 1323958.0569 | 85.76 | 100%
[5 empty] | 85.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82018.7276 | 1324325.5764 | 85.78 | 100%
[5 empty] | 85.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82041.489 | 1324693.0959 | 85.8 | 100%
[5 empty] | 85.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82064.2504 | 1325060.6154 | 85.82 | 100%
[5 empty] | 85.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82087.0118 | 1325428.1349 | 85.84 | 100%
[5 empty] | 85.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82109.7732 | 1325795.6545 | 85.86 | 100%
[5 empty] | 85.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82132.5346 | 1326163.174 | 85.88 | 100%
[5 empty] | 85.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82155.296 | 1326530.6935 | 85.9 | 100%
[5 empty] | 85.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82178.0573 | 1326898.213 | 85.92 | 100%
[5 empty] | 85.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82200.8187 | 1327265.7325 | 85.94 | 100%
[5 empty] | 85.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82223.5801 | 1327633.2521 | 85.96 | 100%
[5 empty] | 85.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82246.3415 | 1328000.7716 | 85.98 | 100%
[5 empty] | 86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82269.1029 | 1328368.2911 | 86 | 100%
[5 empty] | 86.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82291.8643 | 1328735.8106 | 86.02 | 100%
[5 empty] | 86.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82314.6256 | 1329103.3301 | 86.04 | 100%
[5 empty] | 86.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82337.387 | 1329470.8497 | 86.06 | 100%
[5 empty] | 86.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82360.1484 | 1329838.3692 | 86.08 | 100%
[5 empty] | 86.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82382.9098 | 1330205.8887 | 86.1 | 100%
[5 empty] | 86.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82405.6712 | 1330573.4082 | 86.12 | 100%
[5 empty] | 86.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82428.4326 | 1330940.9277 | 86.14 | 100%
[5 empty] | 86.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82451.1939 | 1331308.4473 | 86.16 | 100%
[5 empty] | 86.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82473.9553 | 1331675.9668 | 86.18 | 100%
[5 empty] | 86.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82496.7167 | 1332043.4863 | 86.2 | 100%
[5 empty] | 86.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82519.4781 | 1332411.0058 | 86.22 | 100%
[5 empty] | 86.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82542.2395 | 1332778.5253 | 86.24 | 100%
[5 empty] | 86.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82565.0009 | 1333146.0449 | 86.26 | 100%
[5 empty] | 86.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82587.7623 | 1333513.5644 | 86.28 | 100%
[5 empty] | 86.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82610.5236 | 1333881.0839 | 86.3 | 100%
[5 empty] | 86.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82633.285 | 1334248.6034 | 86.32 | 100%
[5 empty] | 86.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82656.0464 | 1334616.1229 | 86.34 | 100%
[5 empty] | 86.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82678.8078 | 1334983.6425 | 86.36 | 100%
[5 empty] | 86.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82701.5692 | 1335351.162 | 86.38 | 100%
[5 empty] | 86.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82724.3306 | 1335718.6815 | 86.4 | 100%
[5 empty] | 86.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82747.0919 | 1336086.201 | 86.42 | 100%
[5 empty] | 86.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82769.8533 | 1336453.7205 | 86.44 | 100%
[5 empty] | 86.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82792.6147 | 1336821.2401 | 86.46 | 100%
[5 empty] | 86.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82815.3761 | 1337188.7596 | 86.48 | 100%
[5 empty] | 86.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82838.1375 | 1337556.2791 | 86.5 | 100%
[5 empty] | 86.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82860.8989 | 1337923.7986 | 86.52 | 100%
[5 empty] | 86.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82883.6603 | 1338291.3181 | 86.54 | 100%
[5 empty] | 86.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82906.4216 | 1338658.8377 | 86.56 | 100%
[5 empty] | 86.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82929.183 | 1339026.3572 | 86.58 | 100%
[5 empty] | 86.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82951.9444 | 1339393.8767 | 86.6 | 100%
[5 empty] | 86.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82974.7058 | 1339761.3962 | 86.62 | 100%
[5 empty] | 86.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 82997.4672 | 1340128.9157 | 86.64 | 100%
[5 empty] | 86.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83020.2286 | 1340496.4353 | 86.66 | 100%
[5 empty] | 86.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83042.9899 | 1340863.9548 | 86.68 | 100%
[5 empty] | 86.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83065.7513 | 1341231.4743 | 86.7 | 100%
[5 empty] | 86.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83088.5127 | 1341598.9938 | 86.72 | 100%
[5 empty] | 86.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83111.2741 | 1341966.5133 | 86.74 | 100%
[5 empty] | 86.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83134.0355 | 1342334.0329 | 86.76 | 100%
[5 empty] | 86.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83156.7969 | 1342701.5524 | 86.78 | 100%
[5 empty] | 86.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83179.5582 | 1343069.0719 | 86.8 | 100%
[5 empty] | 86.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83202.3196 | 1343436.5914 | 86.82 | 100%
[5 empty] | 86.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83225.081 | 1343804.1109 | 86.84 | 100%
[5 empty] | 86.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83247.8424 | 1344171.6305 | 86.86 | 100%
[5 empty] | 86.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83270.6038 | 1344539.15 | 86.88 | 100%
[5 empty] | 86.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83293.3652 | 1344906.6695 | 86.9 | 100%
[5 empty] | 86.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83316.1266 | 1345274.189 | 86.92 | 100%
[5 empty] | 86.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83338.8879 | 1345641.7085 | 86.94 | 100%
[5 empty] | 86.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83361.6493 | 1346009.2281 | 86.96 | 100%
[5 empty] | 86.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83384.4107 | 1346376.7476 | 86.98 | 100%
[5 empty] | 87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83407.1721 | 1346744.2671 | 87 | 100%
[5 empty] | 87.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83429.9335 | 1347111.7866 | 87.02 | 100%
[5 empty] | 87.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83452.6949 | 1347479.3061 | 87.04 | 100%
[5 empty] | 87.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83475.4562 | 1347846.8257 | 87.06 | 100%
[5 empty] | 87.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83498.2176 | 1348214.3452 | 87.08 | 100%
[5 empty] | 87.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83520.979 | 1348581.8647 | 87.1 | 100%
[5 empty] | 87.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83543.7404 | 1348949.3842 | 87.12 | 100%
[5 empty] | 87.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83566.5018 | 1349316.9037 | 87.14 | 100%
[5 empty] | 87.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83589.2632 | 1349684.4233 | 87.16 | 100%
[5 empty] | 87.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83612.0245 | 1350051.9428 | 87.18 | 100%
[5 empty] | 87.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83634.7859 | 1350419.4623 | 87.2 | 100%
[5 empty] | 87.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83657.5473 | 1350786.9818 | 87.22 | 100%
[5 empty] | 87.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83680.3087 | 1351154.5013 | 87.24 | 100%
[5 empty] | 87.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83703.0701 | 1351522.0209 | 87.26 | 100%
[5 empty] | 87.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83725.8315 | 1351889.5404 | 87.28 | 100%
[5 empty] | 87.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83748.5929 | 1352257.0599 | 87.3 | 100%
[5 empty] | 87.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83771.3542 | 1352624.5794 | 87.32 | 100%
[5 empty] | 87.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83794.1156 | 1352992.0989 | 87.34 | 100%
[5 empty] | 87.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83816.877 | 1353359.6185 | 87.36 | 100%
[5 empty] | 87.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83839.6384 | 1353727.138 | 87.38 | 100%
[5 empty] | 87.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83862.3998 | 1354094.6575 | 87.4 | 100%
[5 empty] | 87.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83885.1612 | 1354462.177 | 87.42 | 100%
[5 empty] | 87.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83907.9225 | 1354829.6965 | 87.44 | 100%
[5 empty] | 87.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83930.6839 | 1355197.2161 | 87.46 | 100%
[5 empty] | 87.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83953.4453 | 1355564.7356 | 87.48 | 100%
[5 empty] | 87.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83976.2067 | 1355932.2551 | 87.5 | 100%
[5 empty] | 87.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 83998.9681 | 1356299.7746 | 87.52 | 100%
[5 empty] | 87.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84021.7295 | 1356667.2941 | 87.54 | 100%
[5 empty] | 87.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84044.4909 | 1357034.8137 | 87.56 | 100%
[5 empty] | 87.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84067.2522 | 1357402.3332 | 87.58 | 100%
[5 empty] | 87.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84090.0136 | 1357769.8527 | 87.6 | 100%
[5 empty] | 87.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84112.775 | 1358137.3722 | 87.62 | 100%
[5 empty] | 87.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84135.5364 | 1358504.8917 | 87.64 | 100%
[5 empty] | 87.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84158.2978 | 1358872.4113 | 87.66 | 100%
[5 empty] | 87.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84181.0592 | 1359239.9308 | 87.68 | 100%
[5 empty] | 87.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84203.8205 | 1359607.4503 | 87.7 | 100%
[5 empty] | 87.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84226.5819 | 1359974.9698 | 87.72 | 100%
[5 empty] | 87.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84249.3433 | 1360342.4893 | 87.74 | 100%
[5 empty] | 87.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84272.1047 | 1360710.0089 | 87.76 | 100%
[5 empty] | 87.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84294.8661 | 1361077.5284 | 87.78 | 100%
[5 empty] | 87.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84317.6275 | 1361445.0479 | 87.8 | 100%
[5 empty] | 87.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84340.3888 | 1361812.5674 | 87.82 | 100%
[5 empty] | 87.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84363.1502 | 1362180.0869 | 87.84 | 100%
[5 empty] | 87.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84385.9116 | 1362547.6065 | 87.86 | 100%
[5 empty] | 87.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84408.673 | 1362915.126 | 87.88 | 100%
[5 empty] | 87.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84431.4344 | 1363282.6455 | 87.9 | 100%
[5 empty] | 87.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84454.1958 | 1363650.165 | 87.92 | 100%
[5 empty] | 87.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84476.9572 | 1364017.6845 | 87.94 | 100%
[5 empty] | 87.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84499.7185 | 1364385.2041 | 87.96 | 100%
[5 empty] | 87.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84522.4799 | 1364752.7236 | 87.98 | 100%
[5 empty] | 88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84545.2413 | 1365120.2431 | 88 | 100%
[5 empty] | 88.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84568.0027 | 1365487.7626 | 88.02 | 100%
[5 empty] | 88.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84590.7641 | 1365855.2821 | 88.04 | 100%
[5 empty] | 88.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84613.5255 | 1366222.8017 | 88.06 | 100%
[5 empty] | 88.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84636.2868 | 1366590.3212 | 88.08 | 100%
[5 empty] | 88.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84659.0482 | 1366957.8407 | 88.1 | 100%
[5 empty] | 88.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84681.8096 | 1367325.3602 | 88.12 | 100%
[5 empty] | 88.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84704.571 | 1367692.8797 | 88.14 | 100%
[5 empty] | 88.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84727.3324 | 1368060.3993 | 88.16 | 100%
[5 empty] | 88.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84750.0938 | 1368427.9188 | 88.18 | 100%
[5 empty] | 88.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84772.8552 | 1368795.4383 | 88.2 | 100%
[5 empty] | 88.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84795.6165 | 1369162.9578 | 88.22 | 100%
[5 empty] | 88.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84818.3779 | 1369530.4773 | 88.24 | 100%
[5 empty] | 88.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84841.1393 | 1369897.9969 | 88.26 | 100%
[5 empty] | 88.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84863.9007 | 1370265.5164 | 88.28 | 100%
[5 empty] | 88.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84886.6621 | 1370633.0359 | 88.3 | 100%
[5 empty] | 88.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84909.4235 | 1371000.5554 | 88.32 | 100%
[5 empty] | 88.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84932.1848 | 1371368.0749 | 88.34 | 100%
[5 empty] | 88.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84954.9462 | 1371735.5945 | 88.36 | 100%
[5 empty] | 88.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 84977.7076 | 1372103.114 | 88.38 | 100%
[5 empty] | 88.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85000.469 | 1372470.6335 | 88.4 | 100%
[5 empty] | 88.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85023.2304 | 1372838.153 | 88.42 | 100%
[5 empty] | 88.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85045.9918 | 1373205.6725 | 88.44 | 100%
[5 empty] | 88.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85068.7531 | 1373573.1921 | 88.46 | 100%
[5 empty] | 88.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85091.5145 | 1373940.7116 | 88.48 | 100%
[5 empty] | 88.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85114.2759 | 1374308.2311 | 88.5 | 100%
[5 empty] | 88.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85137.0373 | 1374675.7506 | 88.52 | 100%
[5 empty] | 88.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85159.7987 | 1375043.2701 | 88.54 | 100%
[5 empty] | 88.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85182.5601 | 1375410.7897 | 88.56 | 100%
[5 empty] | 88.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85205.3215 | 1375778.3092 | 88.58 | 100%
[5 empty] | 88.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85228.0828 | 1376145.8287 | 88.6 | 100%
[5 empty] | 88.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85250.8442 | 1376513.3482 | 88.62 | 100%
[5 empty] | 88.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85273.6056 | 1376880.8677 | 88.64 | 100%
[5 empty] | 88.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85296.367 | 1377248.3873 | 88.66 | 100%
[5 empty] | 88.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85319.1284 | 1377615.9068 | 88.68 | 100%
[5 empty] | 88.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85341.8898 | 1377983.4263 | 88.7 | 100%
[5 empty] | 88.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85364.6511 | 1378350.9458 | 88.72 | 100%
[5 empty] | 88.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85387.4125 | 1378718.4653 | 88.74 | 100%
[5 empty] | 88.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85410.1739 | 1379085.9849 | 88.76 | 100%
[5 empty] | 88.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85432.9353 | 1379453.5044 | 88.78 | 100%
[5 empty] | 88.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85455.6967 | 1379821.0239 | 88.8 | 100%
[5 empty] | 88.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85478.4581 | 1380188.5434 | 88.82 | 100%
[5 empty] | 88.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85501.2194 | 1380556.0629 | 88.84 | 100%
[5 empty] | 88.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85523.9808 | 1380923.5825 | 88.86 | 100%
[5 empty] | 88.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85546.7422 | 1381291.102 | 88.88 | 100%
[5 empty] | 88.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85569.5036 | 1381658.6215 | 88.9 | 100%
[5 empty] | 88.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85592.265 | 1382026.141 | 88.92 | 100%
[5 empty] | 88.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85615.0264 | 1382393.6605 | 88.94 | 100%
[5 empty] | 88.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85637.7878 | 1382761.1801 | 88.96 | 100%
[5 empty] | 88.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85660.5491 | 1383128.6996 | 88.98 | 100%
[5 empty] | 89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85683.3105 | 1383496.2191 | 89 | 100%
[5 empty] | 89.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85706.0719 | 1383863.7386 | 89.02 | 100%
[5 empty] | 89.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85728.8333 | 1384231.2581 | 89.04 | 100%
[5 empty] | 89.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85751.5947 | 1384598.7777 | 89.06 | 100%
[5 empty] | 89.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85774.3561 | 1384966.2972 | 89.08 | 100%
[5 empty] | 89.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85797.1174 | 1385333.8167 | 89.1 | 100%
[5 empty] | 89.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85819.8788 | 1385701.3362 | 89.12 | 100%
[5 empty] | 89.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85842.6402 | 1386068.8557 | 89.14 | 100%
[5 empty] | 89.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85865.4016 | 1386436.3753 | 89.16 | 100%
[5 empty] | 89.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85888.163 | 1386803.8948 | 89.18 | 100%
[5 empty] | 89.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85910.9244 | 1387171.4143 | 89.2 | 100%
[5 empty] | 89.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85933.6858 | 1387538.9338 | 89.22 | 100%
[5 empty] | 89.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85956.4471 | 1387906.4533 | 89.24 | 100%
[5 empty] | 89.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 85979.2085 | 1388273.9729 | 89.26 | 100%
[5 empty] | 89.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86001.9699 | 1388641.4924 | 89.28 | 100%
[5 empty] | 89.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86024.7313 | 1389009.0119 | 89.3 | 100%
[5 empty] | 89.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86047.4927 | 1389376.5314 | 89.32 | 100%
[5 empty] | 89.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86070.2541 | 1389744.0509 | 89.34 | 100%
[5 empty] | 89.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86093.0154 | 1390111.5705 | 89.36 | 100%
[5 empty] | 89.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86115.7768 | 1390479.09 | 89.38 | 100%
[5 empty] | 89.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86138.5382 | 1390846.6095 | 89.4 | 100%
[5 empty] | 89.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86161.2996 | 1391214.129 | 89.42 | 100%
[5 empty] | 89.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86184.061 | 1391581.6485 | 89.44 | 100%
[5 empty] | 89.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86206.8224 | 1391949.1681 | 89.46 | 100%
[5 empty] | 89.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86229.5837 | 1392316.6876 | 89.48 | 100%
[5 empty] | 89.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86252.3451 | 1392684.2071 | 89.5 | 100%
[5 empty] | 89.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86275.1065 | 1393051.7266 | 89.52 | 100%
[5 empty] | 89.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86297.8679 | 1393419.2461 | 89.54 | 100%
[5 empty] | 89.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86320.6293 | 1393786.7657 | 89.56 | 100%
[5 empty] | 89.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86343.3907 | 1394154.2852 | 89.58 | 100%
[5 empty] | 89.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86366.1521 | 1394521.8047 | 89.6 | 100%
[5 empty] | 89.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86388.9134 | 1394889.3242 | 89.62 | 100%
[5 empty] | 89.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86411.6748 | 1395256.8437 | 89.64 | 100%
[5 empty] | 89.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86434.4362 | 1395624.3633 | 89.66 | 100%
[5 empty] | 89.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86457.1976 | 1395991.8828 | 89.68 | 100%
[5 empty] | 89.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86479.959 | 1396359.4023 | 89.7 | 100%
[5 empty] | 89.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86502.7204 | 1396726.9218 | 89.72 | 100%
[5 empty] | 89.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86525.4817 | 1397094.4413 | 89.74 | 100%
[5 empty] | 89.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86548.2431 | 1397461.9609 | 89.76 | 100%
[5 empty] | 89.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86571.0045 | 1397829.4804 | 89.78 | 100%
[5 empty] | 89.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86593.7659 | 1398196.9999 | 89.8 | 100%
[5 empty] | 89.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86616.5273 | 1398564.5194 | 89.82 | 100%
[5 empty] | 89.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86639.2887 | 1398932.0389 | 89.84 | 100%
[5 empty] | 89.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86662.05 | 1399299.5585 | 89.86 | 100%
[5 empty] | 89.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86684.8114 | 1399667.078 | 89.88 | 100%
[5 empty] | 89.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86707.5728 | 1400034.5975 | 89.9 | 100%
[5 empty] | 89.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86730.3342 | 1400402.117 | 89.92 | 100%
[5 empty] | 89.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86753.0956 | 1400769.6365 | 89.94 | 100%
[5 empty] | 89.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86775.857 | 1401137.1561 | 89.96 | 100%
[5 empty] | 89.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86798.6184 | 1401504.6756 | 89.98 | 100%
[5 empty] | 90 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86821.3797 | 1401872.1951 | 90 | 100%
[5 empty] | 90.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86844.1411 | 1402239.7146 | 90.02 | 100%
[5 empty] | 90.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86866.9025 | 1402607.2341 | 90.04 | 100%
[5 empty] | 90.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86889.6639 | 1402974.7537 | 90.06 | 100%
[5 empty] | 90.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86912.4253 | 1403342.2732 | 90.08 | 100%
[5 empty] | 90.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86935.1867 | 1403709.7927 | 90.1 | 100%
[5 empty] | 90.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86957.948 | 1404077.3122 | 90.12 | 100%
[5 empty] | 90.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 86980.7094 | 1404444.8317 | 90.14 | 100%
[5 empty] | 90.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87003.4708 | 1404812.3513 | 90.16 | 100%
[5 empty] | 90.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87026.2322 | 1405179.8708 | 90.18 | 100%
[5 empty] | 90.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87048.9936 | 1405547.3903 | 90.2 | 100%
[5 empty] | 90.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87071.755 | 1405914.9098 | 90.22 | 100%
[5 empty] | 90.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87094.5164 | 1406282.4293 | 90.24 | 100%
[5 empty] | 90.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87117.2777 | 1406649.9489 | 90.26 | 100%
[5 empty] | 90.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87140.0391 | 1407017.4684 | 90.28 | 100%
[5 empty] | 90.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87162.8005 | 1407384.9879 | 90.3 | 100%
[5 empty] | 90.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87185.5619 | 1407752.5074 | 90.32 | 100%
[5 empty] | 90.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87208.3233 | 1408120.0269 | 90.34 | 100%
[5 empty] | 90.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87231.0847 | 1408487.5465 | 90.36 | 100%
[5 empty] | 90.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87253.846 | 1408855.066 | 90.38 | 100%
[5 empty] | 90.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87276.6074 | 1409222.5855 | 90.4 | 100%
[5 empty] | 90.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87299.3688 | 1409590.105 | 90.42 | 100%
[5 empty] | 90.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87322.1302 | 1409957.6245 | 90.44 | 100%
[5 empty] | 90.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87344.8916 | 1410325.1441 | 90.46 | 100%
[5 empty] | 90.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87367.653 | 1410692.6636 | 90.48 | 100%
[5 empty] | 90.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87390.4143 | 1411060.1831 | 90.5 | 100%
[5 empty] | 90.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87413.1757 | 1411427.7026 | 90.52 | 100%
[5 empty] | 90.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87435.9371 | 1411795.2221 | 90.54 | 100%
[5 empty] | 90.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87458.6985 | 1412162.7417 | 90.56 | 100%
[5 empty] | 90.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87481.4599 | 1412530.2612 | 90.58 | 100%
[5 empty] | 90.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87504.2213 | 1412897.7807 | 90.6 | 100%
[5 empty] | 90.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87526.9827 | 1413265.3002 | 90.62 | 100%
[5 empty] | 90.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87549.744 | 1413632.8197 | 90.64 | 100%
[5 empty] | 90.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87572.5054 | 1414000.3393 | 90.66 | 100%
[5 empty] | 90.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87595.2668 | 1414367.8588 | 90.68 | 100%
[5 empty] | 90.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87618.0282 | 1414735.3783 | 90.7 | 100%
[5 empty] | 90.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87640.7896 | 1415102.8978 | 90.72 | 100%
[5 empty] | 90.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87663.551 | 1415470.4173 | 90.74 | 100%
[5 empty] | 90.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87686.3123 | 1415837.9369 | 90.76 | 100%
[5 empty] | 90.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87709.0737 | 1416205.4564 | 90.78 | 100%
[5 empty] | 90.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87731.8351 | 1416572.9759 | 90.8 | 100%
[5 empty] | 90.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87754.5965 | 1416940.4954 | 90.82 | 100%
[5 empty] | 90.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87777.3579 | 1417308.0149 | 90.84 | 100%
[5 empty] | 90.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87800.1193 | 1417675.5345 | 90.86 | 100%
[5 empty] | 90.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87822.8806 | 1418043.054 | 90.88 | 100%
[5 empty] | 90.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87845.642 | 1418410.5735 | 90.9 | 100%
[5 empty] | 90.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87868.4034 | 1418778.093 | 90.92 | 100%
[5 empty] | 90.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87891.1648 | 1419145.6125 | 90.94 | 100%
[5 empty] | 90.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87913.9262 | 1419513.1321 | 90.96 | 100%
[5 empty] | 90.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87936.6876 | 1419880.6516 | 90.98 | 100%
[5 empty] | 91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87959.449 | 1420248.1711 | 91 | 100%
[5 empty] | 91.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 87982.2103 | 1420615.6906 | 91.02 | 100%
[5 empty] | 91.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88004.9717 | 1420983.2101 | 91.04 | 100%
[5 empty] | 91.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88027.7331 | 1421350.7297 | 91.06 | 100%
[5 empty] | 91.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88050.4945 | 1421718.2492 | 91.08 | 100%
[5 empty] | 91.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88073.2559 | 1422085.7687 | 91.1 | 100%
[5 empty] | 91.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88096.0173 | 1422453.2882 | 91.12 | 100%
[5 empty] | 91.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88118.7786 | 1422820.8077 | 91.14 | 100%
[5 empty] | 91.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88141.54 | 1423188.3273 | 91.16 | 100%
[5 empty] | 91.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88164.3014 | 1423555.8468 | 91.18 | 100%
[5 empty] | 91.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88187.0628 | 1423923.3663 | 91.2 | 100%
[5 empty] | 91.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88209.8242 | 1424290.8858 | 91.22 | 100%
[5 empty] | 91.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88232.5856 | 1424658.4053 | 91.24 | 100%
[5 empty] | 91.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88255.347 | 1425025.9249 | 91.26 | 100%
[5 empty] | 91.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88278.1083 | 1425393.4444 | 91.28 | 100%
[5 empty] | 91.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88300.8697 | 1425760.9639 | 91.3 | 100%
[5 empty] | 91.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88323.6311 | 1426128.4834 | 91.32 | 100%
[5 empty] | 91.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88346.3925 | 1426496.0029 | 91.34 | 100%
[5 empty] | 91.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88369.1539 | 1426863.5225 | 91.36 | 100%
[5 empty] | 91.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88391.9153 | 1427231.042 | 91.38 | 100%
[5 empty] | 91.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88414.6766 | 1427598.5615 | 91.4 | 100%
[5 empty] | 91.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88437.438 | 1427966.081 | 91.42 | 100%
[5 empty] | 91.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88460.1994 | 1428333.6005 | 91.44 | 100%
[5 empty] | 91.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88482.9608 | 1428701.1201 | 91.46 | 100%
[5 empty] | 91.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88505.7222 | 1429068.6396 | 91.48 | 100%
[5 empty] | 91.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88528.4836 | 1429436.1591 | 91.5 | 100%
[5 empty] | 91.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88551.2449 | 1429803.6786 | 91.52 | 100%
[5 empty] | 91.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88574.0063 | 1430171.1981 | 91.54 | 100%
[5 empty] | 91.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88596.7677 | 1430538.7177 | 91.56 | 100%
[5 empty] | 91.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88619.5291 | 1430906.2372 | 91.58 | 100%
[5 empty] | 91.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88642.2905 | 1431273.7567 | 91.6 | 100%
[5 empty] | 91.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88665.0519 | 1431641.2762 | 91.62 | 100%
[5 empty] | 91.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88687.8133 | 1432008.7957 | 91.64 | 100%
[5 empty] | 91.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88710.5746 | 1432376.3153 | 91.66 | 100%
[5 empty] | 91.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88733.336 | 1432743.8348 | 91.68 | 100%
[5 empty] | 91.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88756.0974 | 1433111.3543 | 91.7 | 100%
[5 empty] | 91.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88778.8588 | 1433478.8738 | 91.72 | 100%
[5 empty] | 91.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88801.6202 | 1433846.3933 | 91.74 | 100%
[5 empty] | 91.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88824.3816 | 1434213.9129 | 91.76 | 100%
[5 empty] | 91.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88847.1429 | 1434581.4324 | 91.78 | 100%
[5 empty] | 91.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88869.9043 | 1434948.9519 | 91.8 | 100%
[5 empty] | 91.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88892.6657 | 1435316.4714 | 91.82 | 100%
[5 empty] | 91.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88915.4271 | 1435683.9909 | 91.84 | 100%
[5 empty] | 91.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88938.1885 | 1436051.5105 | 91.86 | 100%
[5 empty] | 91.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88960.9499 | 1436419.03 | 91.88 | 100%
[5 empty] | 91.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 88983.7113 | 1436786.5495 | 91.9 | 100%
[5 empty] | 91.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89006.4726 | 1437154.069 | 91.92 | 100%
[5 empty] | 91.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89029.234 | 1437521.5885 | 91.94 | 100%
[5 empty] | 91.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89051.9954 | 1437889.1081 | 91.96 | 100%
[5 empty] | 91.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89074.7568 | 1438256.6276 | 91.98 | 100%
[5 empty] | 92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89097.5182 | 1438624.1471 | 92 | 100%
[5 empty] | 92.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89120.2796 | 1438991.6666 | 92.02 | 100%
[5 empty] | 92.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89143.0409 | 1439359.1861 | 92.04 | 100%
[5 empty] | 92.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89165.8023 | 1439726.7057 | 92.06 | 100%
[5 empty] | 92.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89188.5637 | 1440094.2252 | 92.08 | 100%
[5 empty] | 92.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89211.3251 | 1440461.7447 | 92.1 | 100%
[5 empty] | 92.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89234.0865 | 1440829.2642 | 92.12 | 100%
[5 empty] | 92.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89256.8479 | 1441196.7837 | 92.14 | 100%
[5 empty] | 92.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89279.6092 | 1441564.3033 | 92.16 | 100%
[5 empty] | 92.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89302.3706 | 1441931.8228 | 92.18 | 100%
[5 empty] | 92.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89325.132 | 1442299.3423 | 92.2 | 100%
[5 empty] | 92.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89347.8934 | 1442666.8618 | 92.22 | 100%
[5 empty] | 92.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89370.6548 | 1443034.3813 | 92.24 | 100%
[5 empty] | 92.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89393.4162 | 1443401.9009 | 92.26 | 100%
[5 empty] | 92.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89416.1776 | 1443769.4204 | 92.28 | 100%
[5 empty] | 92.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89438.9389 | 1444136.9399 | 92.3 | 100%
[5 empty] | 92.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89461.7003 | 1444504.4594 | 92.32 | 100%
[5 empty] | 92.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89484.4617 | 1444871.9789 | 92.34 | 100%
[5 empty] | 92.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89507.2231 | 1445239.4985 | 92.36 | 100%
[5 empty] | 92.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89529.9845 | 1445607.018 | 92.38 | 100%
[5 empty] | 92.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89552.7459 | 1445974.5375 | 92.4 | 100%
[5 empty] | 92.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89575.5072 | 1446342.057 | 92.42 | 100%
[5 empty] | 92.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89598.2686 | 1446709.5765 | 92.44 | 100%
[5 empty] | 92.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89621.03 | 1447077.0961 | 92.46 | 100%
[5 empty] | 92.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89643.7914 | 1447444.6156 | 92.48 | 100%
[5 empty] | 92.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89666.5528 | 1447812.1351 | 92.5 | 100%
[5 empty] | 92.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89689.3142 | 1448179.6546 | 92.52 | 100%
[5 empty] | 92.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89712.0755 | 1448547.1741 | 92.54 | 100%
[5 empty] | 92.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89734.8369 | 1448914.6937 | 92.56 | 100%
[5 empty] | 92.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89757.5983 | 1449282.2132 | 92.58 | 100%
[5 empty] | 92.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89780.3597 | 1449649.7327 | 92.6 | 100%
[5 empty] | 92.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89803.1211 | 1450017.2522 | 92.62 | 100%
[5 empty] | 92.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89825.8825 | 1450384.7717 | 92.64 | 100%
[5 empty] | 92.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89848.6439 | 1450752.2913 | 92.66 | 100%
[5 empty] | 92.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89871.4052 | 1451119.8108 | 92.68 | 100%
[5 empty] | 92.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89894.1666 | 1451487.3303 | 92.7 | 100%
[5 empty] | 92.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89916.928 | 1451854.8498 | 92.72 | 100%
[5 empty] | 92.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89939.6894 | 1452222.3693 | 92.74 | 100%
[5 empty] | 92.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89962.4508 | 1452589.8889 | 92.76 | 100%
[5 empty] | 92.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 89985.2122 | 1452957.4084 | 92.78 | 100%
[5 empty] | 92.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90007.9735 | 1453324.9279 | 92.8 | 100%
[5 empty] | 92.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90030.7349 | 1453692.4474 | 92.82 | 100%
[5 empty] | 92.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90053.4963 | 1454059.9669 | 92.84 | 100%
[5 empty] | 92.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90076.2577 | 1454427.4865 | 92.86 | 100%
[5 empty] | 92.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90099.0191 | 1454795.006 | 92.88 | 100%
[5 empty] | 92.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90121.7805 | 1455162.5255 | 92.9 | 100%
[5 empty] | 92.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90144.5419 | 1455530.045 | 92.92 | 100%
[5 empty] | 92.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90167.3032 | 1455897.5645 | 92.94 | 100%
[5 empty] | 92.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90190.0646 | 1456265.0841 | 92.96 | 100%
[5 empty] | 92.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90212.826 | 1456632.6036 | 92.98 | 100%
[5 empty] | 93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90235.5874 | 1457000.1231 | 93 | 100%
[5 empty] | 93.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90258.3488 | 1457367.6426 | 93.02 | 100%
[5 empty] | 93.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90281.1102 | 1457735.1621 | 93.04 | 100%
[5 empty] | 93.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90303.8715 | 1458102.6817 | 93.06 | 100%
[5 empty] | 93.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90326.6329 | 1458470.2012 | 93.08 | 100%
[5 empty] | 93.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90349.3943 | 1458837.7207 | 93.1 | 100%
[5 empty] | 93.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90372.1557 | 1459205.2402 | 93.12 | 100%
[5 empty] | 93.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90394.9171 | 1459572.7597 | 93.14 | 100%
[5 empty] | 93.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90417.6785 | 1459940.2793 | 93.16 | 100%
[5 empty] | 93.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90440.4398 | 1460307.7988 | 93.18 | 100%
[5 empty] | 93.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90463.2012 | 1460675.3183 | 93.2 | 100%
[5 empty] | 93.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90485.9626 | 1461042.8378 | 93.22 | 100%
[5 empty] | 93.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90508.724 | 1461410.3573 | 93.24 | 100%
[5 empty] | 93.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90531.4854 | 1461777.8769 | 93.26 | 100%
[5 empty] | 93.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90554.2468 | 1462145.3964 | 93.28 | 100%
[5 empty] | 93.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90577.0082 | 1462512.9159 | 93.3 | 100%
[5 empty] | 93.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90599.7695 | 1462880.4354 | 93.32 | 100%
[5 empty] | 93.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90622.5309 | 1463247.9549 | 93.34 | 100%
[5 empty] | 93.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90645.2923 | 1463615.4745 | 93.36 | 100%
[5 empty] | 93.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90668.0537 | 1463982.994 | 93.38 | 100%
[5 empty] | 93.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90690.8151 | 1464350.5135 | 93.4 | 100%
[5 empty] | 93.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90713.5765 | 1464718.033 | 93.42 | 100%
[5 empty] | 93.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90736.3378 | 1465085.5525 | 93.44 | 100%
[5 empty] | 93.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90759.0992 | 1465453.0721 | 93.46 | 100%
[5 empty] | 93.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90781.8606 | 1465820.5916 | 93.48 | 100%
[5 empty] | 93.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90804.622 | 1466188.1111 | 93.5 | 100%
[5 empty] | 93.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90827.3834 | 1466555.6306 | 93.52 | 100%
[5 empty] | 93.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90850.1448 | 1466923.1501 | 93.54 | 100%
[5 empty] | 93.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90872.9061 | 1467290.6697 | 93.56 | 100%
[5 empty] | 93.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90895.6675 | 1467658.1892 | 93.58 | 100%
[5 empty] | 93.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90918.4289 | 1468025.7087 | 93.6 | 100%
[5 empty] | 93.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90941.1903 | 1468393.2282 | 93.62 | 100%
[5 empty] | 93.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90963.9517 | 1468760.7477 | 93.64 | 100%
[5 empty] | 93.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 90986.7131 | 1469128.2673 | 93.66 | 100%
[5 empty] | 93.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91009.4745 | 1469495.7868 | 93.68 | 100%
[5 empty] | 93.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91032.2358 | 1469863.3063 | 93.7 | 100%
[5 empty] | 93.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91054.9972 | 1470230.8258 | 93.72 | 100%
[5 empty] | 93.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91077.7586 | 1470598.3453 | 93.74 | 100%
[5 empty] | 93.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91100.52 | 1470965.8649 | 93.76 | 100%
[5 empty] | 93.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91123.2814 | 1471333.3844 | 93.78 | 100%
[5 empty] | 93.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91146.0428 | 1471700.9039 | 93.8 | 100%
[5 empty] | 93.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91168.8041 | 1472068.4234 | 93.82 | 100%
[5 empty] | 93.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91191.5655 | 1472435.9429 | 93.84 | 100%
[5 empty] | 93.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91214.3269 | 1472803.4625 | 93.86 | 100%
[5 empty] | 93.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91237.0883 | 1473170.982 | 93.88 | 100%
[5 empty] | 93.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91259.8497 | 1473538.5015 | 93.9 | 100%
[5 empty] | 93.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91282.6111 | 1473906.021 | 93.92 | 100%
[5 empty] | 93.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91305.3725 | 1474273.5405 | 93.94 | 100%
[5 empty] | 93.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91328.1338 | 1474641.0601 | 93.96 | 100%
[5 empty] | 93.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91350.8952 | 1475008.5796 | 93.98 | 100%
[5 empty] | 94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91373.6566 | 1475376.0991 | 94 | 100%
[5 empty] | 94.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91396.418 | 1475743.6186 | 94.02 | 100%
[5 empty] | 94.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91419.1794 | 1476111.1381 | 94.04 | 100%
[5 empty] | 94.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91441.9408 | 1476478.6577 | 94.06 | 100%
[5 empty] | 94.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91464.7021 | 1476846.1772 | 94.08 | 100%
[5 empty] | 94.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91487.4635 | 1477213.6967 | 94.1 | 100%
[5 empty] | 94.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91510.2249 | 1477581.2162 | 94.12 | 100%
[5 empty] | 94.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91532.9863 | 1477948.7357 | 94.14 | 100%
[5 empty] | 94.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91555.7477 | 1478316.2553 | 94.16 | 100%
[5 empty] | 94.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91578.5091 | 1478683.7748 | 94.18 | 100%
[5 empty] | 94.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91601.2704 | 1479051.2943 | 94.2 | 100%
[5 empty] | 94.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91624.0318 | 1479418.8138 | 94.22 | 100%
[5 empty] | 94.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91646.7932 | 1479786.3333 | 94.24 | 100%
[5 empty] | 94.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91669.5546 | 1480153.8529 | 94.26 | 100%
[5 empty] | 94.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91692.316 | 1480521.3724 | 94.28 | 100%
[5 empty] | 94.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91715.0774 | 1480888.8919 | 94.3 | 100%
[5 empty] | 94.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91737.8388 | 1481256.4114 | 94.32 | 100%
[5 empty] | 94.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91760.6001 | 1481623.9309 | 94.34 | 100%
[5 empty] | 94.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91783.3615 | 1481991.4505 | 94.36 | 100%
[5 empty] | 94.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91806.1229 | 1482358.97 | 94.38 | 100%
[5 empty] | 94.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91828.8843 | 1482726.4895 | 94.4 | 100%
[5 empty] | 94.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91851.6457 | 1483094.009 | 94.42 | 100%
[5 empty] | 94.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91874.4071 | 1483461.5285 | 94.44 | 100%
[5 empty] | 94.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91897.1684 | 1483829.0481 | 94.46 | 100%
[5 empty] | 94.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91919.9298 | 1484196.5676 | 94.48 | 100%
[5 empty] | 94.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91942.6912 | 1484564.0871 | 94.5 | 100%
[5 empty] | 94.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91965.4526 | 1484931.6066 | 94.52 | 100%
[5 empty] | 94.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 91988.214 | 1485299.1261 | 94.54 | 100%
[5 empty] | 94.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92010.9754 | 1485666.6457 | 94.56 | 100%
[5 empty] | 94.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92033.7368 | 1486034.1652 | 94.58 | 100%
[5 empty] | 94.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92056.4981 | 1486401.6847 | 94.6 | 100%
[5 empty] | 94.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92079.2595 | 1486769.2042 | 94.62 | 100%
[5 empty] | 94.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92102.0209 | 1487136.7237 | 94.64 | 100%
[5 empty] | 94.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92124.7823 | 1487504.2433 | 94.66 | 100%
[5 empty] | 94.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92147.5437 | 1487871.7628 | 94.68 | 100%
[5 empty] | 94.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92170.3051 | 1488239.2823 | 94.7 | 100%
[5 empty] | 94.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92193.0664 | 1488606.8018 | 94.72 | 100%
[5 empty] | 94.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92215.8278 | 1488974.3213 | 94.74 | 100%
[5 empty] | 94.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92238.5892 | 1489341.8409 | 94.76 | 100%
[5 empty] | 94.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92261.3506 | 1489709.3604 | 94.78 | 100%
[5 empty] | 94.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92284.112 | 1490076.8799 | 94.8 | 100%
[5 empty] | 94.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92306.8734 | 1490444.3994 | 94.82 | 100%
[5 empty] | 94.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92329.6347 | 1490811.9189 | 94.84 | 100%
[5 empty] | 94.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92352.3961 | 1491179.4385 | 94.86 | 100%
[5 empty] | 94.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92375.1575 | 1491546.958 | 94.88 | 100%
[5 empty] | 94.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92397.9189 | 1491914.4775 | 94.9 | 100%
[5 empty] | 94.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92420.6803 | 1492281.997 | 94.92 | 100%
[5 empty] | 94.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92443.4417 | 1492649.5165 | 94.94 | 100%
[5 empty] | 94.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92466.2031 | 1493017.0361 | 94.96 | 100%
[5 empty] | 94.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92488.9644 | 1493384.5556 | 94.98 | 100%
[5 empty] | 95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92511.7258 | 1493752.0751 | 95 | 100%
[5 empty] | 95.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92534.4872 | 1494119.5946 | 95.02 | 100%
[5 empty] | 95.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92557.2486 | 1494487.1141 | 95.04 | 100%
[5 empty] | 95.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92580.01 | 1494854.6337 | 95.06 | 100%
[5 empty] | 95.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92602.7714 | 1495222.1532 | 95.08 | 100%
[5 empty] | 95.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92625.5327 | 1495589.6727 | 95.1 | 100%
[5 empty] | 95.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92648.2941 | 1495957.1922 | 95.12 | 100%
[5 empty] | 95.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92671.0555 | 1496324.7117 | 95.14 | 100%
[5 empty] | 95.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92693.8169 | 1496692.2313 | 95.16 | 100%
[5 empty] | 95.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92716.5783 | 1497059.7508 | 95.18 | 100%
[5 empty] | 95.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92739.3397 | 1497427.2703 | 95.2 | 100%
[5 empty] | 95.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92762.101 | 1497794.7898 | 95.22 | 100%
[5 empty] | 95.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92784.8624 | 1498162.3093 | 95.24 | 100%
[5 empty] | 95.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92807.6238 | 1498529.8289 | 95.26 | 100%
[5 empty] | 95.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92830.3852 | 1498897.3484 | 95.28 | 100%
[5 empty] | 95.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92853.1466 | 1499264.8679 | 95.3 | 100%
[5 empty] | 95.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92875.908 | 1499632.3874 | 95.32 | 100%
[5 empty] | 95.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92898.6694 | 1499999.9069 | 95.34 | 100%
[5 empty] | 95.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92921.4307 | 1500367.4265 | 95.36 | 100%
[5 empty] | 95.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92944.1921 | 1500734.946 | 95.38 | 100%
[5 empty] | 95.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92966.9535 | 1501102.4655 | 95.4 | 100%
[5 empty] | 95.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 92989.7149 | 1501469.985 | 95.42 | 100%
[5 empty] | 95.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93012.4763 | 1501837.5045 | 95.44 | 100%
[5 empty] | 95.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93035.2377 | 1502205.0241 | 95.46 | 100%
[5 empty] | 95.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93057.999 | 1502572.5436 | 95.48 | 100%
[5 empty] | 95.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93080.7604 | 1502940.0631 | 95.5 | 100%
[5 empty] | 95.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93103.5218 | 1503307.5826 | 95.52 | 100%
[5 empty] | 95.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93126.2832 | 1503675.1021 | 95.54 | 100%
[5 empty] | 95.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93149.0446 | 1504042.6217 | 95.56 | 100%
[5 empty] | 95.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93171.806 | 1504410.1412 | 95.58 | 100%
[5 empty] | 95.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93194.5674 | 1504777.6607 | 95.6 | 100%
[5 empty] | 95.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93217.3287 | 1505145.1802 | 95.62 | 100%
[5 empty] | 95.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93240.0901 | 1505512.6997 | 95.64 | 100%
[5 empty] | 95.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93262.8515 | 1505880.2193 | 95.66 | 100%
[5 empty] | 95.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93285.6129 | 1506247.7388 | 95.68 | 100%
[5 empty] | 95.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93308.3743 | 1506615.2583 | 95.7 | 100%
[5 empty] | 95.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93331.1357 | 1506982.7778 | 95.72 | 100%
[5 empty] | 95.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93353.897 | 1507350.2973 | 95.74 | 100%
[5 empty] | 95.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93376.6584 | 1507717.8169 | 95.76 | 100%
[5 empty] | 95.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93399.4198 | 1508085.3364 | 95.78 | 100%
[5 empty] | 95.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93422.1812 | 1508452.8559 | 95.8 | 100%
[5 empty] | 95.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93444.9426 | 1508820.3754 | 95.82 | 100%
[5 empty] | 95.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93467.704 | 1509187.8949 | 95.84 | 100%
[5 empty] | 95.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93490.4653 | 1509555.4145 | 95.86 | 100%
[5 empty] | 95.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93513.2267 | 1509922.934 | 95.88 | 100%
[5 empty] | 95.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93535.9881 | 1510290.4535 | 95.9 | 100%
[5 empty] | 95.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93558.7495 | 1510657.973 | 95.92 | 100%
[5 empty] | 95.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93581.5109 | 1511025.4925 | 95.94 | 100%
[5 empty] | 95.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93604.2723 | 1511393.0121 | 95.96 | 100%
[5 empty] | 95.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93627.0337 | 1511760.5316 | 95.98 | 100%
[5 empty] | 96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93649.795 | 1512128.0511 | 96 | 100%
[5 empty] | 96.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93672.5564 | 1512495.5706 | 96.02 | 100%
[5 empty] | 96.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93695.3178 | 1512863.0901 | 96.04 | 100%
[5 empty] | 96.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93718.0792 | 1513230.6097 | 96.06 | 100%
[5 empty] | 96.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93740.8406 | 1513598.1292 | 96.08 | 100%
[5 empty] | 96.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93763.602 | 1513965.6487 | 96.1 | 100%
[5 empty] | 96.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93786.3633 | 1514333.1682 | 96.12 | 100%
[5 empty] | 96.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93809.1247 | 1514700.6877 | 96.14 | 100%
[5 empty] | 96.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93831.8861 | 1515068.2073 | 96.16 | 100%
[5 empty] | 96.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93854.6475 | 1515435.7268 | 96.18 | 100%
[5 empty] | 96.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93877.4089 | 1515803.2463 | 96.2 | 100%
[5 empty] | 96.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93900.1703 | 1516170.7658 | 96.22 | 100%
[5 empty] | 96.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93922.9316 | 1516538.2853 | 96.24 | 100%
[5 empty] | 96.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93945.693 | 1516905.8049 | 96.26 | 100%
[5 empty] | 96.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93968.4544 | 1517273.3244 | 96.28 | 100%
[5 empty] | 96.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 93991.2158 | 1517640.8439 | 96.3 | 100%
[5 empty] | 96.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94013.9772 | 1518008.3634 | 96.32 | 100%
[5 empty] | 96.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94036.7386 | 1518375.8829 | 96.34 | 100%
[5 empty] | 96.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94059.5 | 1518743.4025 | 96.36 | 100%
[5 empty] | 96.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94082.2613 | 1519110.922 | 96.38 | 100%
[5 empty] | 96.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94105.0227 | 1519478.4415 | 96.4 | 100%
[5 empty] | 96.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94127.7841 | 1519845.961 | 96.42 | 100%
[5 empty] | 96.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94150.5455 | 1520213.4805 | 96.44 | 100%
[5 empty] | 96.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94173.3069 | 1520581.0001 | 96.46 | 100%
[5 empty] | 96.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94196.0683 | 1520948.5196 | 96.48 | 100%
[5 empty] | 96.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94218.8296 | 1521316.0391 | 96.5 | 100%
[5 empty] | 96.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94241.591 | 1521683.5586 | 96.52 | 100%
[5 empty] | 96.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94264.3524 | 1522051.0781 | 96.54 | 100%
[5 empty] | 96.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94287.1138 | 1522418.5977 | 96.56 | 100%
[5 empty] | 96.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94309.8752 | 1522786.1172 | 96.58 | 100%
[5 empty] | 96.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94332.6366 | 1523153.6367 | 96.6 | 100%
[5 empty] | 96.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94355.398 | 1523521.1562 | 96.62 | 100%
[5 empty] | 96.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94378.1593 | 1523888.6757 | 96.64 | 100%
[5 empty] | 96.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94400.9207 | 1524256.1953 | 96.66 | 100%
[5 empty] | 96.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94423.6821 | 1524623.7148 | 96.68 | 100%
[5 empty] | 96.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94446.4435 | 1524991.2343 | 96.7 | 100%
[5 empty] | 96.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94469.2049 | 1525358.7538 | 96.72 | 100%
[5 empty] | 96.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94491.9663 | 1525726.2733 | 96.74 | 100%
[5 empty] | 96.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94514.7276 | 1526093.7929 | 96.76 | 100%
[5 empty] | 96.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94537.489 | 1526461.3124 | 96.78 | 100%
[5 empty] | 96.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94560.2504 | 1526828.8319 | 96.8 | 100%
[5 empty] | 96.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94583.0118 | 1527196.3514 | 96.82 | 100%
[5 empty] | 96.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94605.7732 | 1527563.8709 | 96.84 | 100%
[5 empty] | 96.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94628.5346 | 1527931.3905 | 96.86 | 100%
[5 empty] | 96.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94651.2959 | 1528298.91 | 96.88 | 100%
[5 empty] | 96.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94674.0573 | 1528666.4295 | 96.9 | 100%
[5 empty] | 96.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94696.8187 | 1529033.949 | 96.92 | 100%
[5 empty] | 96.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94719.5801 | 1529401.4685 | 96.94 | 100%
[5 empty] | 96.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94742.3415 | 1529768.9881 | 96.96 | 100%
[5 empty] | 96.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94765.1029 | 1530136.5076 | 96.98 | 100%
[5 empty] | 97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94787.8643 | 1530504.0271 | 97 | 100%
[5 empty] | 97.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94810.6256 | 1530871.5466 | 97.02 | 100%
[5 empty] | 97.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94833.387 | 1531239.0661 | 97.04 | 100%
[5 empty] | 97.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94856.1484 | 1531606.5857 | 97.06 | 100%
[5 empty] | 97.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94878.9098 | 1531974.1052 | 97.08 | 100%
[5 empty] | 97.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94901.6712 | 1532341.6247 | 97.1 | 100%
[5 empty] | 97.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94924.4326 | 1532709.1442 | 97.12 | 100%
[5 empty] | 97.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94947.1939 | 1533076.6637 | 97.14 | 100%
[5 empty] | 97.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94969.9553 | 1533444.1833 | 97.16 | 100%
[5 empty] | 97.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 94992.7167 | 1533811.7028 | 97.18 | 100%
[5 empty] | 97.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95015.4781 | 1534179.2223 | 97.2 | 100%
[5 empty] | 97.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95038.2395 | 1534546.7418 | 97.22 | 100%
[5 empty] | 97.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95061.0009 | 1534914.2613 | 97.24 | 100%
[5 empty] | 97.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95083.7622 | 1535281.7809 | 97.26 | 100%
[5 empty] | 97.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95106.5236 | 1535649.3004 | 97.28 | 100%
[5 empty] | 97.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95129.285 | 1536016.8199 | 97.3 | 100%
[5 empty] | 97.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95152.0464 | 1536384.3394 | 97.32 | 100%
[5 empty] | 97.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95174.8078 | 1536751.8589 | 97.34 | 100%
[5 empty] | 97.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95197.5692 | 1537119.3785 | 97.36 | 100%
[5 empty] | 97.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95220.3306 | 1537486.898 | 97.38 | 100%
[5 empty] | 97.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95243.0919 | 1537854.4175 | 97.4 | 100%
[5 empty] | 97.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95265.8533 | 1538221.937 | 97.42 | 100%
[5 empty] | 97.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95288.6147 | 1538589.4565 | 97.44 | 100%
[5 empty] | 97.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95311.3761 | 1538956.9761 | 97.46 | 100%
[5 empty] | 97.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95334.1375 | 1539324.4956 | 97.48 | 100%
[5 empty] | 97.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95356.8989 | 1539692.0151 | 97.5 | 100%
[5 empty] | 97.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95379.6602 | 1540059.5346 | 97.52 | 100%
[5 empty] | 97.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95402.4216 | 1540427.0541 | 97.54 | 100%
[5 empty] | 97.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95425.183 | 1540794.5737 | 97.56 | 100%
[5 empty] | 97.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95447.9444 | 1541162.0932 | 97.58 | 100%
[5 empty] | 97.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95470.7058 | 1541529.6127 | 97.6 | 100%
[5 empty] | 97.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95493.4672 | 1541897.1322 | 97.62 | 100%
[5 empty] | 97.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95516.2286 | 1542264.6517 | 97.64 | 100%
[5 empty] | 97.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95538.9899 | 1542632.1713 | 97.66 | 100%
[5 empty] | 97.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95561.7513 | 1542999.6908 | 97.68 | 100%
[5 empty] | 97.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95584.5127 | 1543367.2103 | 97.7 | 100%
[5 empty] | 97.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95607.2741 | 1543734.7298 | 97.72 | 100%
[5 empty] | 97.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95630.0355 | 1544102.2493 | 97.74 | 100%
[5 empty] | 97.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95652.7969 | 1544469.7689 | 97.76 | 100%
[5 empty] | 97.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95675.5582 | 1544837.2884 | 97.78 | 100%
[5 empty] | 97.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95698.3196 | 1545204.8079 | 97.8 | 100%
[5 empty] | 97.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95721.081 | 1545572.3274 | 97.82 | 100%
[5 empty] | 97.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95743.8424 | 1545939.8469 | 97.84 | 100%
[5 empty] | 97.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95766.6038 | 1546307.3665 | 97.86 | 100%
[5 empty] | 97.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95789.3652 | 1546674.886 | 97.88 | 100%
[5 empty] | 97.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95812.1265 | 1547042.4055 | 97.9 | 100%
[5 empty] | 97.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95834.8879 | 1547409.925 | 97.92 | 100%
[5 empty] | 97.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95857.6493 | 1547777.4445 | 97.94 | 100%
[5 empty] | 97.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95880.4107 | 1548144.9641 | 97.96 | 100%
[5 empty] | 97.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95903.1721 | 1548512.4836 | 97.98 | 100%
[5 empty] | 98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95925.9335 | 1548880.0031 | 98 | 100%
[5 empty] | 98.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95948.6949 | 1549247.5226 | 98.02 | 100%
[5 empty] | 98.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95971.4562 | 1549615.0421 | 98.04 | 100%
[5 empty] | 98.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 95994.2176 | 1549982.5617 | 98.06 | 100%
[5 empty] | 98.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96016.979 | 1550350.0812 | 98.08 | 100%
[5 empty] | 98.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96039.7404 | 1550717.6007 | 98.1 | 100%
[5 empty] | 98.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96062.5018 | 1551085.1202 | 98.12 | 100%
[5 empty] | 98.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96085.2632 | 1551452.6397 | 98.14 | 100%
[5 empty] | 98.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96108.0245 | 1551820.1593 | 98.16 | 100%
[5 empty] | 98.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96130.7859 | 1552187.6788 | 98.18 | 100%
[5 empty] | 98.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96153.5473 | 1552555.1983 | 98.2 | 100%
[5 empty] | 98.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96176.3087 | 1552922.7178 | 98.22 | 100%
[5 empty] | 98.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96199.0701 | 1553290.2373 | 98.24 | 100%
[5 empty] | 98.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96221.8315 | 1553657.7569 | 98.26 | 100%
[5 empty] | 98.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96244.5929 | 1554025.2764 | 98.28 | 100%
[5 empty] | 98.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96267.3542 | 1554392.7959 | 98.3 | 100%
[5 empty] | 98.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96290.1156 | 1554760.3154 | 98.32 | 100%
[5 empty] | 98.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96312.877 | 1555127.8349 | 98.34 | 100%
[5 empty] | 98.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96335.6384 | 1555495.3545 | 98.36 | 100%
[5 empty] | 98.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96358.3998 | 1555862.874 | 98.38 | 100%
[5 empty] | 98.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96381.1612 | 1556230.3935 | 98.4 | 100%
[5 empty] | 98.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96403.9225 | 1556597.913 | 98.42 | 100%
[5 empty] | 98.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96426.6839 | 1556965.4325 | 98.44 | 100%
[5 empty] | 98.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96449.4453 | 1557332.9521 | 98.46 | 100%
[5 empty] | 98.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96472.2067 | 1557700.4716 | 98.48 | 100%
[5 empty] | 98.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96494.9681 | 1558067.9911 | 98.5 | 100%
[5 empty] | 98.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96517.7295 | 1558435.5106 | 98.52 | 100%
[5 empty] | 98.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96540.4908 | 1558803.0301 | 98.54 | 100%
[5 empty] | 98.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96563.2522 | 1559170.5497 | 98.56 | 100%
[5 empty] | 98.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96586.0136 | 1559538.0692 | 98.58 | 100%
[5 empty] | 98.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96608.775 | 1559905.5887 | 98.6 | 100%
[5 empty] | 98.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96631.5364 | 1560273.1082 | 98.62 | 100%
[5 empty] | 98.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96654.2978 | 1560640.6277 | 98.64 | 100%
[5 empty] | 98.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96677.0592 | 1561008.1473 | 98.66 | 100%
[5 empty] | 98.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96699.8205 | 1561375.6668 | 98.68 | 100%
[5 empty] | 98.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96722.5819 | 1561743.1863 | 98.7 | 100%
[5 empty] | 98.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96745.3433 | 1562110.7058 | 98.72 | 100%
[5 empty] | 98.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96768.1047 | 1562478.2253 | 98.74 | 100%
[5 empty] | 98.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96790.8661 | 1562845.7449 | 98.76 | 100%
[5 empty] | 98.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96813.6275 | 1563213.2644 | 98.78 | 100%
[5 empty] | 98.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96836.3888 | 1563580.7839 | 98.8 | 100%
[5 empty] | 98.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96859.1502 | 1563948.3034 | 98.82 | 100%
[5 empty] | 98.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96881.9116 | 1564315.8229 | 98.84 | 100%
[5 empty] | 98.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96904.673 | 1564683.3425 | 98.86 | 100%
[5 empty] | 98.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96927.4344 | 1565050.862 | 98.88 | 100%
[5 empty] | 98.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96950.1958 | 1565418.3815 | 98.9 | 100%
[5 empty] | 98.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96972.9571 | 1565785.901 | 98.92 | 100%
[5 empty] | 98.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 96995.7185 | 1566153.4205 | 98.94 | 100%
[5 empty] | 98.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97018.4799 | 1566520.9401 | 98.96 | 100%
[5 empty] | 98.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97041.2413 | 1566888.4596 | 98.98 | 100%
[5 empty] | 99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97064.0027 | 1567255.9791 | 99 | 100%
[5 empty] | 99.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97086.7641 | 1567623.4986 | 99.02 | 100%
[5 empty] | 99.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97109.5255 | 1567991.0181 | 99.04 | 100%
[5 empty] | 99.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97132.2868 | 1568358.5377 | 99.06 | 100%
[5 empty] | 99.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97155.0482 | 1568726.0572 | 99.08 | 100%
[5 empty] | 99.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97177.8096 | 1569093.5767 | 99.1 | 100%
[5 empty] | 99.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97200.571 | 1569461.0962 | 99.12 | 100%
[5 empty] | 99.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97223.3324 | 1569828.6157 | 99.14 | 100%
[5 empty] | 99.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97246.0938 | 1570196.1353 | 99.16 | 100%
[5 empty] | 99.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97268.8551 | 1570563.6548 | 99.18 | 100%
[5 empty] | 99.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97291.6165 | 1570931.1743 | 99.2 | 100%
[5 empty] | 99.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97314.3779 | 1571298.6938 | 99.22 | 100%
[5 empty] | 99.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97337.1393 | 1571666.2133 | 99.24 | 100%
[5 empty] | 99.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97359.9007 | 1572033.7329 | 99.26 | 100%
[5 empty] | 99.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97382.6621 | 1572401.2524 | 99.28 | 100%
[5 empty] | 99.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97405.4235 | 1572768.7719 | 99.3 | 100%
[5 empty] | 99.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97428.1848 | 1573136.2914 | 99.32 | 100%
[5 empty] | 99.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97450.9462 | 1573503.8109 | 99.34 | 100%
[5 empty] | 99.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97473.7076 | 1573871.3305 | 99.36 | 100%
[5 empty] | 99.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97496.469 | 1574238.85 | 99.38 | 100%
[5 empty] | 99.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97519.2304 | 1574606.3695 | 99.4 | 100%
[5 empty] | 99.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97541.9918 | 1574973.889 | 99.42 | 100%
[5 empty] | 99.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97564.7531 | 1575341.4085 | 99.44 | 100%
[5 empty] | 99.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97587.5145 | 1575708.9281 | 99.46 | 100%
[5 empty] | 99.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97610.2759 | 1576076.4476 | 99.48 | 100%
[5 empty] | 99.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97633.0373 | 1576443.9671 | 99.5 | 100%
[5 empty] | 99.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97655.7987 | 1576811.4866 | 99.52 | 100%
[5 empty] | 99.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97678.5601 | 1577179.0061 | 99.54 | 100%
[5 empty] | 99.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97701.3214 | 1577546.5257 | 99.56 | 100%
[5 empty] | 99.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97724.0828 | 1577914.0452 | 99.58 | 100%
[5 empty] | 99.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97746.8442 | 1578281.5647 | 99.6 | 100%
[5 empty] | 99.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97769.6056 | 1578649.0842 | 99.62 | 100%
[5 empty] | 99.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97792.367 | 1579016.6037 | 99.64 | 100%
[5 empty] | 99.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97815.1284 | 1579384.1233 | 99.66 | 100%
[5 empty] | 99.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97837.8898 | 1579751.6428 | 99.68 | 100%
[5 empty] | 99.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97860.6511 | 1580119.1623 | 99.7 | 100%
[5 empty] | 99.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97883.4125 | 1580486.6818 | 99.72 | 100%
[5 empty] | 99.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97906.1739 | 1580854.2013 | 99.74 | 100%
[5 empty] | 99.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97928.9353 | 1581221.7209 | 99.76 | 100%
[5 empty] | 99.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97951.6967 | 1581589.2404 | 99.78 | 100%
[5 empty] | 99.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97974.4581 | 1581956.7599 | 99.8 | 100%
[5 empty] | 99.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 97997.2194 | 1582324.2794 | 99.82 | 100%
[5 empty] | 99.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98019.9808 | 1582691.7989 | 99.84 | 100%
[5 empty] | 99.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98042.7422 | 1583059.3185 | 99.86 | 100%
[5 empty] | 99.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98065.5036 | 1583426.838 | 99.88 | 100%
[5 empty] | 99.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98088.265 | 1583794.3575 | 99.9 | 100%
[5 empty] | 99.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98111.0264 | 1584161.877 | 99.92 | 100%
[5 empty] | 99.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98133.7877 | 1584529.3965 | 99.94 | 100%
[5 empty] | 99.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98156.5491 | 1584896.9161 | 99.96 | 100%
[5 empty] | 99.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98179.3105 | 1585264.4356 | 99.98 | 100%
[5 empty] | 100 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98202.0719 | 1585631.9551 | 100 | 100%
[5 empty] | 100.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98224.8333 | 1585999.4746 | 100.02 | 100%
[5 empty] | 100.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98247.5947 | 1586366.9941 | 100.04 | 100%
[5 empty] | 100.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98270.3561 | 1586734.5137 | 100.06 | 100%
[5 empty] | 100.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98293.1174 | 1587102.0332 | 100.08 | 100%
[5 empty] | 100.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98315.8788 | 1587469.5527 | 100.1 | 100%
[5 empty] | 100.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98338.6402 | 1587837.0722 | 100.12 | 100%
[5 empty] | 100.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98361.4016 | 1588204.5917 | 100.14 | 100%
[5 empty] | 100.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98384.163 | 1588572.1113 | 100.16 | 100%
[5 empty] | 100.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98406.9244 | 1588939.6308 | 100.18 | 100%
[5 empty] | 100.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98429.6857 | 1589307.1503 | 100.2 | 100%
[5 empty] | 100.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98452.4471 | 1589674.6698 | 100.22 | 100%
[5 empty] | 100.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98475.2085 | 1590042.1893 | 100.24 | 100%
[5 empty] | 100.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98497.9699 | 1590409.7089 | 100.26 | 100%
[5 empty] | 100.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98520.7313 | 1590777.2284 | 100.28 | 100%
[5 empty] | 100.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98543.4927 | 1591144.7479 | 100.3 | 100%
[5 empty] | 100.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98566.2541 | 1591512.2674 | 100.32 | 100%
[5 empty] | 100.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98589.0154 | 1591879.7869 | 100.34 | 100%
[5 empty] | 100.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98611.7768 | 1592247.3065 | 100.36 | 100%
[5 empty] | 100.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98634.5382 | 1592614.826 | 100.38 | 100%
[5 empty] | 100.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98657.2996 | 1592982.3455 | 100.4 | 100%
[5 empty] | 100.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98680.061 | 1593349.865 | 100.42 | 100%
[5 empty] | 100.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98702.8224 | 1593717.3845 | 100.44 | 100%
[5 empty] | 100.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98725.5837 | 1594084.9041 | 100.46 | 100%
[5 empty] | 100.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98748.3451 | 1594452.4236 | 100.48 | 100%
[5 empty] | 100.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98771.1065 | 1594819.9431 | 100.5 | 100%
[5 empty] | 100.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98793.8679 | 1595187.4626 | 100.52 | 100%
[5 empty] | 100.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98816.6293 | 1595554.9821 | 100.54 | 100%
[5 empty] | 100.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98839.3907 | 1595922.5017 | 100.56 | 100%
[5 empty] | 100.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98862.152 | 1596290.0212 | 100.58 | 100%
[5 empty] | 100.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98884.9134 | 1596657.5407 | 100.6 | 100%
[5 empty] | 100.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98907.6748 | 1597025.0602 | 100.62 | 100%
[5 empty] | 100.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98930.4362 | 1597392.5797 | 100.64 | 100%
[5 empty] | 100.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98953.1976 | 1597760.0993 | 100.66 | 100%
[5 empty] | 100.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98975.959 | 1598127.6188 | 100.68 | 100%
[5 empty] | 100.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 98998.7204 | 1598495.1383 | 100.7 | 100%
[5 empty] | 100.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99021.4817 | 1598862.6578 | 100.72 | 100%
[5 empty] | 100.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99044.2431 | 1599230.1773 | 100.74 | 100%
[5 empty] | 100.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99067.0045 | 1599597.6969 | 100.76 | 100%
[5 empty] | 100.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99089.7659 | 1599965.2164 | 100.78 | 100%
[5 empty] | 100.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99112.5273 | 1600332.7359 | 100.8 | 100%
[5 empty] | 100.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99135.2887 | 1600700.2554 | 100.82 | 100%
[5 empty] | 100.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99158.05 | 1601067.7749 | 100.84 | 100%
[5 empty] | 100.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99180.8114 | 1601435.2945 | 100.86 | 100%
[5 empty] | 100.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99203.5728 | 1601802.814 | 100.88 | 100%
[5 empty] | 100.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99226.3342 | 1602170.3335 | 100.9 | 100%
[5 empty] | 100.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99249.0956 | 1602537.853 | 100.92 | 100%
[5 empty] | 100.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99271.857 | 1602905.3725 | 100.94 | 100%
[5 empty] | 100.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99294.6183 | 1603272.8921 | 100.96 | 100%
[5 empty] | 100.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99317.3797 | 1603640.4116 | 100.98 | 100%
[5 empty] | 101 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99340.1411 | 1604007.9311 | 101 | 100%
[5 empty] | 101.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99362.9025 | 1604375.4506 | 101.02 | 100%
[5 empty] | 101.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99385.6639 | 1604742.9701 | 101.04 | 100%
[5 empty] | 101.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99408.4253 | 1605110.4897 | 101.06 | 100%
[5 empty] | 101.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99431.1867 | 1605478.0092 | 101.08 | 100%
[5 empty] | 101.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99453.948 | 1605845.5287 | 101.1 | 100%
[5 empty] | 101.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99476.7094 | 1606213.0482 | 101.12 | 100%
[5 empty] | 101.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99499.4708 | 1606580.5677 | 101.14 | 100%
[5 empty] | 101.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99522.2322 | 1606948.0873 | 101.16 | 100%
[5 empty] | 101.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99544.9936 | 1607315.6068 | 101.18 | 100%
[5 empty] | 101.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99567.755 | 1607683.1263 | 101.2 | 100%
[5 empty] | 101.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99590.5163 | 1608050.6458 | 101.22 | 100%
[5 empty] | 101.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99613.2777 | 1608418.1653 | 101.24 | 100%
[5 empty] | 101.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99636.0391 | 1608785.6849 | 101.26 | 100%
[5 empty] | 101.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99658.8005 | 1609153.2044 | 101.28 | 100%
[5 empty] | 101.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99681.5619 | 1609520.7239 | 101.3 | 100%
[5 empty] | 101.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99704.3233 | 1609888.2434 | 101.32 | 100%
[5 empty] | 101.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99727.0847 | 1610255.7629 | 101.34 | 100%
[5 empty] | 101.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99749.846 | 1610623.2825 | 101.36 | 100%
[5 empty] | 101.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99772.6074 | 1610990.802 | 101.38 | 100%
[5 empty] | 101.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99795.3688 | 1611358.3215 | 101.4 | 100%
[5 empty] | 101.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99818.1302 | 1611725.841 | 101.42 | 100%
[5 empty] | 101.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99840.8916 | 1612093.3605 | 101.44 | 100%
[5 empty] | 101.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99863.653 | 1612460.8801 | 101.46 | 100%
[5 empty] | 101.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99886.4143 | 1612828.3996 | 101.48 | 100%
[5 empty] | 101.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99909.1757 | 1613195.9191 | 101.5 | 100%
[5 empty] | 101.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99931.9371 | 1613563.4386 | 101.52 | 100%
[5 empty] | 101.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99954.6985 | 1613930.9581 | 101.54 | 100%
[5 empty] | 101.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 99977.4599 | 1614298.4777 | 101.56 | 100%
[5 empty] | 101.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100000.2213 | 1614665.9972 | 101.58 | 100%
[5 empty] | 101.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100022.9826 | 1615033.5167 | 101.6 | 100%
[5 empty] | 101.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100045.744 | 1615401.0362 | 101.62 | 100%
[5 empty] | 101.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100068.5054 | 1615768.5557 | 101.64 | 100%
[5 empty] | 101.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100091.2668 | 1616136.0753 | 101.66 | 100%
[5 empty] | 101.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100114.0282 | 1616503.5948 | 101.68 | 100%
[5 empty] | 101.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100136.7896 | 1616871.1143 | 101.7 | 100%
[5 empty] | 101.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100159.551 | 1617238.6338 | 101.72 | 100%
[5 empty] | 101.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100182.3123 | 1617606.1533 | 101.74 | 100%
[5 empty] | 101.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100205.0737 | 1617973.6729 | 101.76 | 100%
[5 empty] | 101.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100227.8351 | 1618341.1924 | 101.78 | 100%
[5 empty] | 101.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100250.5965 | 1618708.7119 | 101.8 | 100%
[5 empty] | 101.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100273.3579 | 1619076.2314 | 101.82 | 100%
[5 empty] | 101.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100296.1193 | 1619443.7509 | 101.84 | 100%
[5 empty] | 101.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100318.8806 | 1619811.2705 | 101.86 | 100%
[5 empty] | 101.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100341.642 | 1620178.79 | 101.88 | 100%
[5 empty] | 101.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100364.4034 | 1620546.3095 | 101.9 | 100%
[5 empty] | 101.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100387.1648 | 1620913.829 | 101.92 | 100%
[5 empty] | 101.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100409.9262 | 1621281.3485 | 101.94 | 100%
[5 empty] | 101.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100432.6876 | 1621648.8681 | 101.96 | 100%
[5 empty] | 101.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100455.449 | 1622016.3876 | 101.98 | 100%
[5 empty] | 102 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100478.2103 | 1622383.9071 | 102 | 100%
[5 empty] | 102.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100500.9717 | 1622751.4266 | 102.02 | 100%
[5 empty] | 102.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100523.7331 | 1623118.9461 | 102.04 | 100%
[5 empty] | 102.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100546.4945 | 1623486.4657 | 102.06 | 100%
[5 empty] | 102.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100569.2559 | 1623853.9852 | 102.08 | 100%
[5 empty] | 102.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100592.0173 | 1624221.5047 | 102.1 | 100%
[5 empty] | 102.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100614.7786 | 1624589.0242 | 102.12 | 100%
[5 empty] | 102.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100637.54 | 1624956.5437 | 102.14 | 100%
[5 empty] | 102.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100660.3014 | 1625324.0633 | 102.16 | 100%
[5 empty] | 102.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100683.0628 | 1625691.5828 | 102.18 | 100%
[5 empty] | 102.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100705.8242 | 1626059.1023 | 102.2 | 100%
[5 empty] | 102.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100728.5856 | 1626426.6218 | 102.22 | 100%
[5 empty] | 102.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100751.3469 | 1626794.1413 | 102.24 | 100%
[5 empty] | 102.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100774.1083 | 1627161.6609 | 102.26 | 100%
[5 empty] | 102.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100796.8697 | 1627529.1804 | 102.28 | 100%
[5 empty] | 102.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100819.6311 | 1627896.6999 | 102.3 | 100%
[5 empty] | 102.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100842.3925 | 1628264.2194 | 102.32 | 100%
[5 empty] | 102.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100865.1539 | 1628631.7389 | 102.34 | 100%
[5 empty] | 102.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100887.9153 | 1628999.2585 | 102.36 | 100%
[5 empty] | 102.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100910.6766 | 1629366.778 | 102.38 | 100%
[5 empty] | 102.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100933.438 | 1629734.2975 | 102.4 | 100%
[5 empty] | 102.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100956.1994 | 1630101.817 | 102.42 | 100%
[5 empty] | 102.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 100978.9608 | 1630469.3365 | 102.44 | 100%
[5 empty] | 102.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101001.7222 | 1630836.8561 | 102.46 | 100%
[5 empty] | 102.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101024.4836 | 1631204.3756 | 102.48 | 100%
[5 empty] | 102.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101047.2449 | 1631571.8951 | 102.5 | 100%
[5 empty] | 102.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101070.0063 | 1631939.4146 | 102.52 | 100%
[5 empty] | 102.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101092.7677 | 1632306.9341 | 102.54 | 100%
[5 empty] | 102.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101115.5291 | 1632674.4537 | 102.56 | 100%
[5 empty] | 102.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101138.2905 | 1633041.9732 | 102.58 | 100%
[5 empty] | 102.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101161.0519 | 1633409.4927 | 102.6 | 100%
[5 empty] | 102.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101183.8132 | 1633777.0122 | 102.62 | 100%
[5 empty] | 102.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101206.5746 | 1634144.5317 | 102.64 | 100%
[5 empty] | 102.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101229.336 | 1634512.0513 | 102.66 | 100%
[5 empty] | 102.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101252.0974 | 1634879.5708 | 102.68 | 100%
[5 empty] | 102.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101274.8588 | 1635247.0903 | 102.7 | 100%
[5 empty] | 102.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101297.6202 | 1635614.6098 | 102.72 | 100%
[5 empty] | 102.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101320.3816 | 1635982.1293 | 102.74 | 100%
[5 empty] | 102.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101343.1429 | 1636349.6489 | 102.76 | 100%
[5 empty] | 102.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101365.9043 | 1636717.1684 | 102.78 | 100%
[5 empty] | 102.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101388.6657 | 1637084.6879 | 102.8 | 100%
[5 empty] | 102.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101411.4271 | 1637452.2074 | 102.82 | 100%
[5 empty] | 102.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101434.1885 | 1637819.7269 | 102.84 | 100%
[5 empty] | 102.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101456.9499 | 1638187.2465 | 102.86 | 100%
[5 empty] | 102.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101479.7112 | 1638554.766 | 102.88 | 100%
[5 empty] | 102.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101502.4726 | 1638922.2855 | 102.9 | 100%
[5 empty] | 102.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101525.234 | 1639289.805 | 102.92 | 100%
[5 empty] | 102.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101547.9954 | 1639657.3245 | 102.94 | 100%
[5 empty] | 102.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101570.7568 | 1640024.8441 | 102.96 | 100%
[5 empty] | 102.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101593.5182 | 1640392.3636 | 102.98 | 100%
[5 empty] | 103 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101616.2796 | 1640759.8831 | 103 | 100%
[5 empty] | 103.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101639.0409 | 1641127.4026 | 103.02 | 100%
[5 empty] | 103.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101661.8023 | 1641494.9221 | 103.04 | 100%
[5 empty] | 103.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101684.5637 | 1641862.4417 | 103.06 | 100%
[5 empty] | 103.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101707.3251 | 1642229.9612 | 103.08 | 100%
[5 empty] | 103.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101730.0865 | 1642597.4807 | 103.1 | 100%
[5 empty] | 103.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101752.8479 | 1642965.0002 | 103.12 | 100%
[5 empty] | 103.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101775.6092 | 1643332.5197 | 103.14 | 100%
[5 empty] | 103.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101798.3706 | 1643700.0393 | 103.16 | 100%
[5 empty] | 103.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101821.132 | 1644067.5588 | 103.18 | 100%
[5 empty] | 103.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101843.8934 | 1644435.0783 | 103.2 | 100%
[5 empty] | 103.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101866.6548 | 1644802.5978 | 103.22 | 100%
[5 empty] | 103.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101889.4162 | 1645170.1173 | 103.24 | 100%
[5 empty] | 103.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101912.1775 | 1645537.6369 | 103.26 | 100%
[5 empty] | 103.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101934.9389 | 1645905.1564 | 103.28 | 100%
[5 empty] | 103.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101957.7003 | 1646272.6759 | 103.3 | 100%
[5 empty] | 103.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 101980.4617 | 1646640.1954 | 103.32 | 100%
[5 empty] | 103.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102003.2231 | 1647007.7149 | 103.34 | 100%
[5 empty] | 103.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102025.9845 | 1647375.2345 | 103.36 | 100%
[5 empty] | 103.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102048.7459 | 1647742.754 | 103.38 | 100%
[5 empty] | 103.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102071.5072 | 1648110.2735 | 103.4 | 100%
[5 empty] | 103.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102094.2686 | 1648477.793 | 103.42 | 100%
[5 empty] | 103.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102117.03 | 1648845.3125 | 103.44 | 100%
[5 empty] | 103.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102139.7914 | 1649212.8321 | 103.46 | 100%
[5 empty] | 103.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102162.5528 | 1649580.3516 | 103.48 | 100%
[5 empty] | 103.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102185.3142 | 1649947.8711 | 103.5 | 100%
[5 empty] | 103.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102208.0755 | 1650315.3906 | 103.52 | 100%
[5 empty] | 103.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102230.8369 | 1650682.9101 | 103.54 | 100%
[5 empty] | 103.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102253.5983 | 1651050.4297 | 103.56 | 100%
[5 empty] | 103.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102276.3597 | 1651417.9492 | 103.58 | 100%
[5 empty] | 103.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102299.1211 | 1651785.4687 | 103.6 | 100%
[5 empty] | 103.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102321.8825 | 1652152.9882 | 103.62 | 100%
[5 empty] | 103.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102344.6438 | 1652520.5077 | 103.64 | 100%
[5 empty] | 103.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102367.4052 | 1652888.0273 | 103.66 | 100%
[5 empty] | 103.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102390.1666 | 1653255.5468 | 103.68 | 100%
[5 empty] | 103.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102412.928 | 1653623.0663 | 103.7 | 100%
[5 empty] | 103.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102435.6894 | 1653990.5858 | 103.72 | 100%
[5 empty] | 103.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102458.4508 | 1654358.1053 | 103.74 | 100%
[5 empty] | 103.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102481.2122 | 1654725.6249 | 103.76 | 100%
[5 empty] | 103.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102503.9735 | 1655093.1444 | 103.78 | 100%
[5 empty] | 103.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102526.7349 | 1655460.6639 | 103.8 | 100%
[5 empty] | 103.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102549.4963 | 1655828.1834 | 103.82 | 100%
[5 empty] | 103.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102572.2577 | 1656195.7029 | 103.84 | 100%
[5 empty] | 103.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102595.0191 | 1656563.2225 | 103.86 | 100%
[5 empty] | 103.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102617.7805 | 1656930.742 | 103.88 | 100%
[5 empty] | 103.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102640.5418 | 1657298.2615 | 103.9 | 100%
[5 empty] | 103.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102663.3032 | 1657665.781 | 103.92 | 100%
[5 empty] | 103.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102686.0646 | 1658033.3005 | 103.94 | 100%
[5 empty] | 103.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102708.826 | 1658400.8201 | 103.96 | 100%
[5 empty] | 103.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102731.5874 | 1658768.3396 | 103.98 | 100%
[5 empty] | 104 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102754.3488 | 1659135.8591 | 104 | 100%
[5 empty] | 104.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102777.1102 | 1659503.3786 | 104.02 | 100%
[5 empty] | 104.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102799.8715 | 1659870.8981 | 104.04 | 100%
[5 empty] | 104.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102822.6329 | 1660238.4177 | 104.06 | 100%
[5 empty] | 104.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102845.3943 | 1660605.9372 | 104.08 | 100%
[5 empty] | 104.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102868.1557 | 1660973.4567 | 104.1 | 100%
[5 empty] | 104.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102890.9171 | 1661340.9762 | 104.12 | 100%
[5 empty] | 104.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102913.6785 | 1661708.4957 | 104.14 | 100%
[5 empty] | 104.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102936.4398 | 1662076.0153 | 104.16 | 100%
[5 empty] | 104.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102959.2012 | 1662443.5348 | 104.18 | 100%
[5 empty] | 104.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 102981.9626 | 1662811.0543 | 104.2 | 100%
[5 empty] | 104.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103004.724 | 1663178.5738 | 104.22 | 100%
[5 empty] | 104.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103027.4854 | 1663546.0933 | 104.24 | 100%
[5 empty] | 104.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103050.2468 | 1663913.6129 | 104.26 | 100%
[5 empty] | 104.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103073.0081 | 1664281.1324 | 104.28 | 100%
[5 empty] | 104.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103095.7695 | 1664648.6519 | 104.3 | 100%
[5 empty] | 104.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103118.5309 | 1665016.1714 | 104.32 | 100%
[5 empty] | 104.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103141.2923 | 1665383.6909 | 104.34 | 100%
[5 empty] | 104.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103164.0537 | 1665751.2105 | 104.36 | 100%
[5 empty] | 104.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103186.8151 | 1666118.73 | 104.38 | 100%
[5 empty] | 104.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103209.5765 | 1666486.2495 | 104.4 | 100%
[5 empty] | 104.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103232.3378 | 1666853.769 | 104.42 | 100%
[5 empty] | 104.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103255.0992 | 1667221.2885 | 104.44 | 100%
[5 empty] | 104.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103277.8606 | 1667588.8081 | 104.46 | 100%
[5 empty] | 104.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103300.622 | 1667956.3276 | 104.48 | 100%
[5 empty] | 104.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103323.3834 | 1668323.8471 | 104.5 | 100%
[5 empty] | 104.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103346.1448 | 1668691.3666 | 104.52 | 100%
[5 empty] | 104.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103368.9061 | 1669058.8861 | 104.54 | 100%
[5 empty] | 104.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103391.6675 | 1669426.4057 | 104.56 | 100%
[5 empty] | 104.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103414.4289 | 1669793.9252 | 104.58 | 100%
[5 empty] | 104.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103437.1903 | 1670161.4447 | 104.6 | 100%
[5 empty] | 104.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103459.9517 | 1670528.9642 | 104.62 | 100%
[5 empty] | 104.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103482.7131 | 1670896.4837 | 104.64 | 100%
[5 empty] | 104.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103505.4744 | 1671264.0033 | 104.66 | 100%
[5 empty] | 104.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103528.2358 | 1671631.5228 | 104.68 | 100%
[5 empty] | 104.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103550.9972 | 1671999.0423 | 104.7 | 100%
[5 empty] | 104.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103573.7586 | 1672366.5618 | 104.72 | 100%
[5 empty] | 104.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103596.52 | 1672734.0813 | 104.74 | 100%
[5 empty] | 104.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103619.2814 | 1673101.6009 | 104.76 | 100%
[5 empty] | 104.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103642.0428 | 1673469.1204 | 104.78 | 100%
[5 empty] | 104.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103664.8041 | 1673836.6399 | 104.8 | 100%
[5 empty] | 104.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103687.5655 | 1674204.1594 | 104.82 | 100%
[5 empty] | 104.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103710.3269 | 1674571.6789 | 104.84 | 100%
[5 empty] | 104.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103733.0883 | 1674939.1985 | 104.86 | 100%
[5 empty] | 104.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103755.8497 | 1675306.718 | 104.88 | 100%
[5 empty] | 104.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103778.6111 | 1675674.2375 | 104.9 | 100%
[5 empty] | 104.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103801.3724 | 1676041.757 | 104.92 | 100%
[5 empty] | 104.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103824.1338 | 1676409.2765 | 104.94 | 100%
[5 empty] | 104.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103846.8952 | 1676776.7961 | 104.96 | 100%
[5 empty] | 104.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103869.6566 | 1677144.3156 | 104.98 | 100%
[5 empty] | 105 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103892.418 | 1677511.8351 | 105 | 100%
[5 empty] | 105.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103915.1794 | 1677879.3546 | 105.02 | 100%
[5 empty] | 105.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103937.9408 | 1678246.8741 | 105.04 | 100%
[5 empty] | 105.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103960.7021 | 1678614.3937 | 105.06 | 100%
[5 empty] | 105.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 103983.4635 | 1678981.9132 | 105.08 | 100%
[5 empty] | 105.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104006.2249 | 1679349.4327 | 105.1 | 100%
[5 empty] | 105.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104028.9863 | 1679716.9522 | 105.12 | 100%
[5 empty] | 105.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104051.7477 | 1680084.4717 | 105.14 | 100%
[5 empty] | 105.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104074.5091 | 1680451.9913 | 105.16 | 100%
[5 empty] | 105.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104097.2704 | 1680819.5108 | 105.18 | 100%
[5 empty] | 105.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104120.0318 | 1681187.0303 | 105.2 | 100%
[5 empty] | 105.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104142.7932 | 1681554.5498 | 105.22 | 100%
[5 empty] | 105.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104165.5546 | 1681922.0693 | 105.24 | 100%
[5 empty] | 105.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104188.316 | 1682289.5889 | 105.26 | 100%
[5 empty] | 105.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104211.0774 | 1682657.1084 | 105.28 | 100%
[5 empty] | 105.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104233.8387 | 1683024.6279 | 105.3 | 100%
[5 empty] | 105.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104256.6001 | 1683392.1474 | 105.32 | 100%
[5 empty] | 105.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104279.3615 | 1683759.6669 | 105.34 | 100%
[5 empty] | 105.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104302.1229 | 1684127.1865 | 105.36 | 100%
[5 empty] | 105.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104324.8843 | 1684494.706 | 105.38 | 100%
[5 empty] | 105.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104347.6457 | 1684862.2255 | 105.4 | 100%
[5 empty] | 105.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104370.4071 | 1685229.745 | 105.42 | 100%
[5 empty] | 105.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104393.1684 | 1685597.2645 | 105.44 | 100%
[5 empty] | 105.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104415.9298 | 1685964.7841 | 105.46 | 100%
[5 empty] | 105.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104438.6912 | 1686332.3036 | 105.48 | 100%
[5 empty] | 105.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104461.4526 | 1686699.8231 | 105.5 | 100%
[5 empty] | 105.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104484.214 | 1687067.3426 | 105.52 | 100%
[5 empty] | 105.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104506.9754 | 1687434.8621 | 105.54 | 100%
[5 empty] | 105.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104529.7367 | 1687802.3817 | 105.56 | 100%
[5 empty] | 105.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104552.4981 | 1688169.9012 | 105.58 | 100%
[5 empty] | 105.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104575.2595 | 1688537.4207 | 105.6 | 100%
[5 empty] | 105.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104598.0209 | 1688904.9402 | 105.62 | 100%
[5 empty] | 105.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104620.7823 | 1689272.4597 | 105.64 | 100%
[5 empty] | 105.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104643.5437 | 1689639.9793 | 105.66 | 100%
[5 empty] | 105.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104666.3051 | 1690007.4988 | 105.68 | 100%
[5 empty] | 105.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104689.0664 | 1690375.0183 | 105.7 | 100%
[5 empty] | 105.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104711.8278 | 1690742.5378 | 105.72 | 100%
[5 empty] | 105.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104734.5892 | 1691110.0573 | 105.74 | 100%
[5 empty] | 105.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104757.3506 | 1691477.5769 | 105.76 | 100%
[5 empty] | 105.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104780.112 | 1691845.0964 | 105.78 | 100%
[5 empty] | 105.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104802.8734 | 1692212.6159 | 105.8 | 100%
[5 empty] | 105.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104825.6347 | 1692580.1354 | 105.82 | 100%
[5 empty] | 105.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104848.3961 | 1692947.6549 | 105.84 | 100%
[5 empty] | 105.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104871.1575 | 1693315.1745 | 105.86 | 100%
[5 empty] | 105.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104893.9189 | 1693682.694 | 105.88 | 100%
[5 empty] | 105.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104916.6803 | 1694050.2135 | 105.9 | 100%
[5 empty] | 105.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104939.4417 | 1694417.733 | 105.92 | 100%
[5 empty] | 105.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104962.203 | 1694785.2525 | 105.94 | 100%
[5 empty] | 105.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 104984.9644 | 1695152.7721 | 105.96 | 100%
[5 empty] | 105.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105007.7258 | 1695520.2916 | 105.98 | 100%
[5 empty] | 106 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105030.4872 | 1695887.8111 | 106 | 100%
[5 empty] | 106.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105053.2486 | 1696255.3306 | 106.02 | 100%
[5 empty] | 106.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105076.01 | 1696622.8501 | 106.04 | 100%
[5 empty] | 106.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105098.7714 | 1696990.3697 | 106.06 | 100%
[5 empty] | 106.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105121.5327 | 1697357.8892 | 106.08 | 100%
[5 empty] | 106.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105144.2941 | 1697725.4087 | 106.1 | 100%
[5 empty] | 106.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105167.0555 | 1698092.9282 | 106.12 | 100%
[5 empty] | 106.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105189.8169 | 1698460.4477 | 106.14 | 100%
[5 empty] | 106.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105212.5783 | 1698827.9673 | 106.16 | 100%
[5 empty] | 106.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105235.3397 | 1699195.4868 | 106.18 | 100%
[5 empty] | 106.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105258.101 | 1699563.0063 | 106.2 | 100%
[5 empty] | 106.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105280.8624 | 1699930.5258 | 106.22 | 100%
[5 empty] | 106.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105303.6238 | 1700298.0453 | 106.24 | 100%
[5 empty] | 106.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105326.3852 | 1700665.5649 | 106.26 | 100%
[5 empty] | 106.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105349.1466 | 1701033.0844 | 106.28 | 100%
[5 empty] | 106.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105371.908 | 1701400.6039 | 106.3 | 100%
[5 empty] | 106.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105394.6693 | 1701768.1234 | 106.32 | 100%
[5 empty] | 106.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105417.4307 | 1702135.6429 | 106.34 | 100%
[5 empty] | 106.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105440.1921 | 1702503.1625 | 106.36 | 100%
[5 empty] | 106.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105462.9535 | 1702870.682 | 106.38 | 100%
[5 empty] | 106.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105485.7149 | 1703238.2015 | 106.4 | 100%
[5 empty] | 106.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105508.4763 | 1703605.721 | 106.42 | 100%
[5 empty] | 106.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105531.2377 | 1703973.2405 | 106.44 | 100%
[5 empty] | 106.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105553.999 | 1704340.7601 | 106.46 | 100%
[5 empty] | 106.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105576.7604 | 1704708.2796 | 106.48 | 100%
[5 empty] | 106.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105599.5218 | 1705075.7991 | 106.5 | 100%
[5 empty] | 106.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105622.2832 | 1705443.3186 | 106.52 | 100%
[5 empty] | 106.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105645.0446 | 1705810.8381 | 106.54 | 100%
[5 empty] | 106.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105667.806 | 1706178.3577 | 106.56 | 100%
[5 empty] | 106.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105690.5673 | 1706545.8772 | 106.58 | 100%
[5 empty] | 106.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105713.3287 | 1706913.3967 | 106.6 | 100%
[5 empty] | 106.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105736.0901 | 1707280.9162 | 106.62 | 100%
[5 empty] | 106.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105758.8515 | 1707648.4357 | 106.64 | 100%
[5 empty] | 106.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105781.6129 | 1708015.9553 | 106.66 | 100%
[5 empty] | 106.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105804.3743 | 1708383.4748 | 106.68 | 100%
[5 empty] | 106.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105827.1357 | 1708750.9943 | 106.7 | 100%
[5 empty] | 106.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105849.897 | 1709118.5138 | 106.72 | 100%
[5 empty] | 106.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105872.6584 | 1709486.0333 | 106.74 | 100%
[5 empty] | 106.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105895.4198 | 1709853.5529 | 106.76 | 100%
[5 empty] | 106.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105918.1812 | 1710221.0724 | 106.78 | 100%
[5 empty] | 106.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105940.9426 | 1710588.5919 | 106.8 | 100%
[5 empty] | 106.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105963.704 | 1710956.1114 | 106.82 | 100%
[5 empty] | 106.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 105986.4653 | 1711323.6309 | 106.84 | 100%
[5 empty] | 106.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106009.2267 | 1711691.1505 | 106.86 | 100%
[5 empty] | 106.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106031.9881 | 1712058.67 | 106.88 | 100%
[5 empty] | 106.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106054.7495 | 1712426.1895 | 106.9 | 100%
[5 empty] | 106.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106077.5109 | 1712793.709 | 106.92 | 100%
[5 empty] | 106.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106100.2723 | 1713161.2285 | 106.94 | 100%
[5 empty] | 106.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106123.0336 | 1713528.7481 | 106.96 | 100%
[5 empty] | 106.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106145.795 | 1713896.2676 | 106.98 | 100%
[5 empty] | 107 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106168.5564 | 1714263.7871 | 107 | 100%
[5 empty] | 107.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106191.3178 | 1714631.3066 | 107.02 | 100%
[5 empty] | 107.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106214.0792 | 1714998.8261 | 107.04 | 100%
[5 empty] | 107.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106236.8406 | 1715366.3457 | 107.06 | 100%
[5 empty] | 107.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106259.602 | 1715733.8652 | 107.08 | 100%
[5 empty] | 107.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106282.3633 | 1716101.3847 | 107.1 | 100%
[5 empty] | 107.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106305.1247 | 1716468.9042 | 107.12 | 100%
[5 empty] | 107.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106327.8861 | 1716836.4237 | 107.14 | 100%
[5 empty] | 107.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106350.6475 | 1717203.9433 | 107.16 | 100%
[5 empty] | 107.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106373.4089 | 1717571.4628 | 107.18 | 100%
[5 empty] | 107.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106396.1703 | 1717938.9823 | 107.2 | 100%
[5 empty] | 107.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106418.9316 | 1718306.5018 | 107.22 | 100%
[5 empty] | 107.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106441.693 | 1718674.0213 | 107.24 | 100%
[5 empty] | 107.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106464.4544 | 1719041.5409 | 107.26 | 100%
[5 empty] | 107.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106487.2158 | 1719409.0604 | 107.28 | 100%
[5 empty] | 107.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106509.9772 | 1719776.5799 | 107.3 | 100%
[5 empty] | 107.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106532.7386 | 1720144.0994 | 107.32 | 100%
[5 empty] | 107.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106555.4999 | 1720511.6189 | 107.34 | 100%
[5 empty] | 107.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106578.2613 | 1720879.1385 | 107.36 | 100%
[5 empty] | 107.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106601.0227 | 1721246.658 | 107.38 | 100%
[5 empty] | 107.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106623.7841 | 1721614.1775 | 107.4 | 100%
[5 empty] | 107.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106646.5455 | 1721981.697 | 107.42 | 100%
[5 empty] | 107.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106669.3069 | 1722349.2165 | 107.44 | 100%
[5 empty] | 107.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106692.0683 | 1722716.7361 | 107.46 | 100%
[5 empty] | 107.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106714.8296 | 1723084.2556 | 107.48 | 100%
[5 empty] | 107.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106737.591 | 1723451.7751 | 107.5 | 100%
[5 empty] | 107.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106760.3524 | 1723819.2946 | 107.52 | 100%
[5 empty] | 107.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106783.1138 | 1724186.8141 | 107.54 | 100%
[5 empty] | 107.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106805.8752 | 1724554.3337 | 107.56 | 100%
[5 empty] | 107.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106828.6366 | 1724921.8532 | 107.58 | 100%
[5 empty] | 107.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106851.3979 | 1725289.3727 | 107.6 | 100%
[5 empty] | 107.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106874.1593 | 1725656.8922 | 107.62 | 100%
[5 empty] | 107.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106896.9207 | 1726024.4117 | 107.64 | 100%
[5 empty] | 107.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106919.6821 | 1726391.9313 | 107.66 | 100%
[5 empty] | 107.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106942.4435 | 1726759.4508 | 107.68 | 100%
[5 empty] | 107.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106965.2049 | 1727126.9703 | 107.7 | 100%
[5 empty] | 107.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 106987.9663 | 1727494.4898 | 107.72 | 100%
[5 empty] | 107.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107010.7276 | 1727862.0093 | 107.74 | 100%
[5 empty] | 107.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107033.489 | 1728229.5289 | 107.76 | 100%
[5 empty] | 107.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107056.2504 | 1728597.0484 | 107.78 | 100%
[5 empty] | 107.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107079.0118 | 1728964.5679 | 107.8 | 100%
[5 empty] | 107.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107101.7732 | 1729332.0874 | 107.82 | 100%
[5 empty] | 107.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107124.5346 | 1729699.6069 | 107.84 | 100%
[5 empty] | 107.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107147.2959 | 1730067.1265 | 107.86 | 100%
[5 empty] | 107.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107170.0573 | 1730434.646 | 107.88 | 100%
[5 empty] | 107.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107192.8187 | 1730802.1655 | 107.9 | 100%
[5 empty] | 107.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107215.5801 | 1731169.685 | 107.92 | 100%
[5 empty] | 107.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107238.3415 | 1731537.2045 | 107.94 | 100%
[5 empty] | 107.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107261.1029 | 1731904.7241 | 107.96 | 100%
[5 empty] | 107.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107283.8642 | 1732272.2436 | 107.98 | 100%
[5 empty] | 108 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107306.6256 | 1732639.7631 | 108 | 100%
[5 empty] | 108.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107329.387 | 1733007.2826 | 108.02 | 100%
[5 empty] | 108.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107352.1484 | 1733374.8021 | 108.04 | 100%
[5 empty] | 108.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107374.9098 | 1733742.3217 | 108.06 | 100%
[5 empty] | 108.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107397.6712 | 1734109.8412 | 108.08 | 100%
[5 empty] | 108.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107420.4326 | 1734477.3607 | 108.1 | 100%
[5 empty] | 108.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107443.1939 | 1734844.8802 | 108.12 | 100%
[5 empty] | 108.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107465.9553 | 1735212.3997 | 108.14 | 100%
[5 empty] | 108.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107488.7167 | 1735579.9193 | 108.16 | 100%
[5 empty] | 108.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107511.4781 | 1735947.4388 | 108.18 | 100%
[5 empty] | 108.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107534.2395 | 1736314.9583 | 108.2 | 100%
[5 empty] | 108.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107557.0009 | 1736682.4778 | 108.22 | 100%
[5 empty] | 108.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107579.7622 | 1737049.9973 | 108.24 | 100%
[5 empty] | 108.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107602.5236 | 1737417.5169 | 108.26 | 100%
[5 empty] | 108.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107625.285 | 1737785.0364 | 108.28 | 100%
[5 empty] | 108.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107648.0464 | 1738152.5559 | 108.3 | 100%
[5 empty] | 108.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107670.8078 | 1738520.0754 | 108.32 | 100%
[5 empty] | 108.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107693.5692 | 1738887.5949 | 108.34 | 100%
[5 empty] | 108.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107716.3306 | 1739255.1145 | 108.36 | 100%
[5 empty] | 108.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107739.0919 | 1739622.634 | 108.38 | 100%
[5 empty] | 108.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107761.8533 | 1739990.1535 | 108.4 | 100%
[5 empty] | 108.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107784.6147 | 1740357.673 | 108.42 | 100%
[5 empty] | 108.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107807.3761 | 1740725.1925 | 108.44 | 100%
[5 empty] | 108.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107830.1375 | 1741092.7121 | 108.46 | 100%
[5 empty] | 108.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107852.8989 | 1741460.2316 | 108.48 | 100%
[5 empty] | 108.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107875.6602 | 1741827.7511 | 108.5 | 100%
[5 empty] | 108.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107898.4216 | 1742195.2706 | 108.52 | 100%
[5 empty] | 108.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107921.183 | 1742562.7901 | 108.54 | 100%
[5 empty] | 108.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107943.9444 | 1742930.3097 | 108.56 | 100%
[5 empty] | 108.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107966.7058 | 1743297.8292 | 108.58 | 100%
[5 empty] | 108.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 107989.4672 | 1743665.3487 | 108.6 | 100%
[5 empty] | 108.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108012.2285 | 1744032.8682 | 108.62 | 100%
[5 empty] | 108.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108034.9899 | 1744400.3877 | 108.64 | 100%
[5 empty] | 108.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108057.7513 | 1744767.9073 | 108.66 | 100%
[5 empty] | 108.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108080.5127 | 1745135.4268 | 108.68 | 100%
[5 empty] | 108.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108103.2741 | 1745502.9463 | 108.7 | 100%
[5 empty] | 108.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108126.0355 | 1745870.4658 | 108.72 | 100%
[5 empty] | 108.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108148.7969 | 1746237.9853 | 108.74 | 100%
[5 empty] | 108.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108171.5582 | 1746605.5049 | 108.76 | 100%
[5 empty] | 108.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108194.3196 | 1746973.0244 | 108.78 | 100%
[5 empty] | 108.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108217.081 | 1747340.5439 | 108.8 | 100%
[5 empty] | 108.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108239.8424 | 1747708.0634 | 108.82 | 100%
[5 empty] | 108.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108262.6038 | 1748075.5829 | 108.84 | 100%
[5 empty] | 108.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108285.3652 | 1748443.1025 | 108.86 | 100%
[5 empty] | 108.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108308.1265 | 1748810.622 | 108.88 | 100%
[5 empty] | 108.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108330.8879 | 1749178.1415 | 108.9 | 100%
[5 empty] | 108.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108353.6493 | 1749545.661 | 108.92 | 100%
[5 empty] | 108.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108376.4107 | 1749913.1805 | 108.94 | 100%
[5 empty] | 108.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108399.1721 | 1750280.7001 | 108.96 | 100%
[5 empty] | 108.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108421.9335 | 1750648.2196 | 108.98 | 100%
[5 empty] | 109 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108444.6948 | 1751015.7391 | 109 | 100%
[5 empty] | 109.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108467.4562 | 1751383.2586 | 109.02 | 100%
[5 empty] | 109.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108490.2176 | 1751750.7781 | 109.04 | 100%
[5 empty] | 109.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108512.979 | 1752118.2977 | 109.06 | 100%
[5 empty] | 109.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108535.7404 | 1752485.8172 | 109.08 | 100%
[5 empty] | 109.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108558.5018 | 1752853.3367 | 109.1 | 100%
[5 empty] | 109.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108581.2632 | 1753220.8562 | 109.12 | 100%
[5 empty] | 109.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108604.0245 | 1753588.3757 | 109.14 | 100%
[5 empty] | 109.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108626.7859 | 1753955.8953 | 109.16 | 100%
[5 empty] | 109.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108649.5473 | 1754323.4148 | 109.18 | 100%
[5 empty] | 109.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108672.3087 | 1754690.9343 | 109.2 | 100%
[5 empty] | 109.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108695.0701 | 1755058.4538 | 109.22 | 100%
[5 empty] | 109.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108717.8315 | 1755425.9733 | 109.24 | 100%
[5 empty] | 109.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108740.5928 | 1755793.4929 | 109.26 | 100%
[5 empty] | 109.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108763.3542 | 1756161.0124 | 109.28 | 100%
[5 empty] | 109.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108786.1156 | 1756528.5319 | 109.3 | 100%
[5 empty] | 109.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108808.877 | 1756896.0514 | 109.32 | 100%
[5 empty] | 109.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108831.6384 | 1757263.5709 | 109.34 | 100%
[5 empty] | 109.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108854.3998 | 1757631.0905 | 109.36 | 100%
[5 empty] | 109.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108877.1612 | 1757998.61 | 109.38 | 100%
[5 empty] | 109.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108899.9225 | 1758366.1295 | 109.4 | 100%
[5 empty] | 109.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108922.6839 | 1758733.649 | 109.42 | 100%
[5 empty] | 109.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108945.4453 | 1759101.1685 | 109.44 | 100%
[5 empty] | 109.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108968.2067 | 1759468.6881 | 109.46 | 100%
[5 empty] | 109.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 108990.9681 | 1759836.2076 | 109.48 | 100%
[5 empty] | 109.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109013.7295 | 1760203.7271 | 109.5 | 100%
[5 empty] | 109.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109036.4908 | 1760571.2466 | 109.52 | 100%
[5 empty] | 109.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109059.2522 | 1760938.7661 | 109.54 | 100%
[5 empty] | 109.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109082.0136 | 1761306.2857 | 109.56 | 100%
[5 empty] | 109.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109104.775 | 1761673.8052 | 109.58 | 100%
[5 empty] | 109.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109127.5364 | 1762041.3247 | 109.6 | 100%
[5 empty] | 109.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109150.2978 | 1762408.8442 | 109.62 | 100%
[5 empty] | 109.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109173.0591 | 1762776.3637 | 109.64 | 100%
[5 empty] | 109.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109195.8205 | 1763143.8833 | 109.66 | 100%
[5 empty] | 109.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109218.5819 | 1763511.4028 | 109.68 | 100%
[5 empty] | 109.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109241.3433 | 1763878.9223 | 109.7 | 100%
[5 empty] | 109.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109264.1047 | 1764246.4418 | 109.72 | 100%
[5 empty] | 109.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109286.8661 | 1764613.9613 | 109.74 | 100%
[5 empty] | 109.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109309.6275 | 1764981.4809 | 109.76 | 100%
[5 empty] | 109.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109332.3888 | 1765349.0004 | 109.78 | 100%
[5 empty] | 109.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109355.1502 | 1765716.5199 | 109.8 | 100%
[5 empty] | 109.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109377.9116 | 1766084.0394 | 109.82 | 100%
[5 empty] | 109.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109400.673 | 1766451.5589 | 109.84 | 100%
[5 empty] | 109.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109423.4344 | 1766819.0785 | 109.86 | 100%
[5 empty] | 109.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109446.1958 | 1767186.598 | 109.88 | 100%
[5 empty] | 109.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109468.9571 | 1767554.1175 | 109.9 | 100%
[5 empty] | 109.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109491.7185 | 1767921.637 | 109.92 | 100%
[5 empty] | 109.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109514.4799 | 1768289.1565 | 109.94 | 100%
[5 empty] | 109.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109537.2413 | 1768656.6761 | 109.96 | 100%
[5 empty] | 109.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109560.0027 | 1769024.1956 | 109.98 | 100%
[5 empty] | 110 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109582.7641 | 1769391.7151 | 110 | 100%
[5 empty] | 110.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109605.5254 | 1769759.2346 | 110.02 | 100%
[5 empty] | 110.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109628.2868 | 1770126.7541 | 110.04 | 100%
[5 empty] | 110.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109651.0482 | 1770494.2737 | 110.06 | 100%
[5 empty] | 110.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109673.8096 | 1770861.7932 | 110.08 | 100%
[5 empty] | 110.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109696.571 | 1771229.3127 | 110.1 | 100%
[5 empty] | 110.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109719.3324 | 1771596.8322 | 110.12 | 100%
[5 empty] | 110.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109742.0938 | 1771964.3517 | 110.14 | 100%
[5 empty] | 110.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109764.8551 | 1772331.8713 | 110.16 | 100%
[5 empty] | 110.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109787.6165 | 1772699.3908 | 110.18 | 100%
[5 empty] | 110.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109810.3779 | 1773066.9103 | 110.2 | 100%
[5 empty] | 110.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109833.1393 | 1773434.4298 | 110.22 | 100%
[5 empty] | 110.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109855.9007 | 1773801.9493 | 110.24 | 100%
[5 empty] | 110.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109878.6621 | 1774169.4689 | 110.26 | 100%
[5 empty] | 110.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109901.4234 | 1774536.9884 | 110.28 | 100%
[5 empty] | 110.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109924.1848 | 1774904.5079 | 110.3 | 100%
[5 empty] | 110.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109946.9462 | 1775272.0274 | 110.32 | 100%
[5 empty] | 110.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109969.7076 | 1775639.5469 | 110.34 | 100%
[5 empty] | 110.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 109992.469 | 1776007.0665 | 110.36 | 100%
[5 empty] | 110.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110015.2304 | 1776374.586 | 110.38 | 100%
[5 empty] | 110.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110037.9918 | 1776742.1055 | 110.4 | 100%
[5 empty] | 110.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110060.7531 | 1777109.625 | 110.42 | 100%
[5 empty] | 110.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110083.5145 | 1777477.1445 | 110.44 | 100%
[5 empty] | 110.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110106.2759 | 1777844.6641 | 110.46 | 100%
[5 empty] | 110.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110129.0373 | 1778212.1836 | 110.48 | 100%
[5 empty] | 110.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110151.7987 | 1778579.7031 | 110.5 | 100%
[5 empty] | 110.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110174.5601 | 1778947.2226 | 110.52 | 100%
[5 empty] | 110.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110197.3214 | 1779314.7421 | 110.54 | 100%
[5 empty] | 110.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110220.0828 | 1779682.2617 | 110.56 | 100%
[5 empty] | 110.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110242.8442 | 1780049.7812 | 110.58 | 100%
[5 empty] | 110.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110265.6056 | 1780417.3007 | 110.6 | 100%
[5 empty] | 110.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110288.367 | 1780784.8202 | 110.62 | 100%
[5 empty] | 110.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110311.1284 | 1781152.3397 | 110.64 | 100%
[5 empty] | 110.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110333.8897 | 1781519.8593 | 110.66 | 100%
[5 empty] | 110.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110356.6511 | 1781887.3788 | 110.68 | 100%
[5 empty] | 110.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110379.4125 | 1782254.8983 | 110.7 | 100%
[5 empty] | 110.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110402.1739 | 1782622.4178 | 110.72 | 100%
[5 empty] | 110.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110424.9353 | 1782989.9373 | 110.74 | 100%
[5 empty] | 110.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110447.6967 | 1783357.4569 | 110.76 | 100%
[5 empty] | 110.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110470.4581 | 1783724.9764 | 110.78 | 100%
[5 empty] | 110.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110493.2194 | 1784092.4959 | 110.8 | 100%
[5 empty] | 110.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110515.9808 | 1784460.0154 | 110.82 | 100%
[5 empty] | 110.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110538.7422 | 1784827.5349 | 110.84 | 100%
[5 empty] | 110.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110561.5036 | 1785195.0545 | 110.86 | 100%
[5 empty] | 110.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110584.265 | 1785562.574 | 110.88 | 100%
[5 empty] | 110.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110607.0264 | 1785930.0935 | 110.9 | 100%
[5 empty] | 110.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110629.7877 | 1786297.613 | 110.92 | 100%
[5 empty] | 110.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110652.5491 | 1786665.1325 | 110.94 | 100%
[5 empty] | 110.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110675.3105 | 1787032.6521 | 110.96 | 100%
[5 empty] | 110.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110698.0719 | 1787400.1716 | 110.98 | 100%
[5 empty] | 111 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110720.8333 | 1787767.6911 | 111 | 100%
[5 empty] | 111.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110743.5947 | 1788135.2106 | 111.02 | 100%
[5 empty] | 111.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110766.356 | 1788502.7301 | 111.04 | 100%
[5 empty] | 111.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110789.1174 | 1788870.2497 | 111.06 | 100%
[5 empty] | 111.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110811.8788 | 1789237.7692 | 111.08 | 100%
[5 empty] | 111.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110834.6402 | 1789605.2887 | 111.1 | 100%
[5 empty] | 111.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110857.4016 | 1789972.8082 | 111.12 | 100%
[5 empty] | 111.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110880.163 | 1790340.3277 | 111.14 | 100%
[5 empty] | 111.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110902.9244 | 1790707.8473 | 111.16 | 100%
[5 empty] | 111.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110925.6857 | 1791075.3668 | 111.18 | 100%
[5 empty] | 111.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110948.4471 | 1791442.8863 | 111.2 | 100%
[5 empty] | 111.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110971.2085 | 1791810.4058 | 111.22 | 100%
[5 empty] | 111.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 110993.9699 | 1792177.9253 | 111.24 | 100%
[5 empty] | 111.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111016.7313 | 1792545.4449 | 111.26 | 100%
[5 empty] | 111.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111039.4927 | 1792912.9644 | 111.28 | 100%
[5 empty] | 111.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111062.254 | 1793280.4839 | 111.3 | 100%
[5 empty] | 111.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111085.0154 | 1793648.0034 | 111.32 | 100%
[5 empty] | 111.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111107.7768 | 1794015.5229 | 111.34 | 100%
[5 empty] | 111.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111130.5382 | 1794383.0425 | 111.36 | 100%
[5 empty] | 111.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111153.2996 | 1794750.562 | 111.38 | 100%
[5 empty] | 111.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111176.061 | 1795118.0815 | 111.4 | 100%
[5 empty] | 111.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111198.8224 | 1795485.601 | 111.42 | 100%
[5 empty] | 111.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111221.5837 | 1795853.1205 | 111.44 | 100%
[5 empty] | 111.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111244.3451 | 1796220.6401 | 111.46 | 100%
[5 empty] | 111.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111267.1065 | 1796588.1596 | 111.48 | 100%
[5 empty] | 111.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111289.8679 | 1796955.6791 | 111.5 | 100%
[5 empty] | 111.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111312.6293 | 1797323.1986 | 111.52 | 100%
[5 empty] | 111.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111335.3907 | 1797690.7181 | 111.54 | 100%
[5 empty] | 111.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111358.152 | 1798058.2377 | 111.56 | 100%
[5 empty] | 111.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111380.9134 | 1798425.7572 | 111.58 | 100%
[5 empty] | 111.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111403.6748 | 1798793.2767 | 111.6 | 100%
[5 empty] | 111.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111426.4362 | 1799160.7962 | 111.62 | 100%
[5 empty] | 111.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111449.1976 | 1799528.3157 | 111.64 | 100%
[5 empty] | 111.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111471.959 | 1799895.8353 | 111.66 | 100%
[5 empty] | 111.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111494.7203 | 1800263.3548 | 111.68 | 100%
[5 empty] | 111.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111517.4817 | 1800630.8743 | 111.7 | 100%
[5 empty] | 111.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111540.2431 | 1800998.3938 | 111.72 | 100%
[5 empty] | 111.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111563.0045 | 1801365.9133 | 111.74 | 100%
[5 empty] | 111.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111585.7659 | 1801733.4329 | 111.76 | 100%
[5 empty] | 111.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111608.5273 | 1802100.9524 | 111.78 | 100%
[5 empty] | 111.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111631.2887 | 1802468.4719 | 111.8 | 100%
[5 empty] | 111.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111654.05 | 1802835.9914 | 111.82 | 100%
[5 empty] | 111.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111676.8114 | 1803203.5109 | 111.84 | 100%
[5 empty] | 111.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111699.5728 | 1803571.0305 | 111.86 | 100%
[5 empty] | 111.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111722.3342 | 1803938.55 | 111.88 | 100%
[5 empty] | 111.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111745.0956 | 1804306.0695 | 111.9 | 100%
[5 empty] | 111.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111767.857 | 1804673.589 | 111.92 | 100%
[5 empty] | 111.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111790.6183 | 1805041.1085 | 111.94 | 100%
[5 empty] | 111.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111813.3797 | 1805408.6281 | 111.96 | 100%
[5 empty] | 111.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111836.1411 | 1805776.1476 | 111.98 | 100%
[5 empty] | 112 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111858.9025 | 1806143.6671 | 112 | 100%
[5 empty] | 112.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111881.6639 | 1806511.1866 | 112.02 | 100%
[5 empty] | 112.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111904.4253 | 1806878.7061 | 112.04 | 100%
[5 empty] | 112.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111927.1867 | 1807246.2257 | 112.06 | 100%
[5 empty] | 112.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111949.948 | 1807613.7452 | 112.08 | 100%
[5 empty] | 112.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111972.7094 | 1807981.2647 | 112.1 | 100%
[5 empty] | 112.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 111995.4708 | 1808348.7842 | 112.12 | 100%
[5 empty] | 112.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112018.2322 | 1808716.3037 | 112.14 | 100%
[5 empty] | 112.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112040.9936 | 1809083.8233 | 112.16 | 100%
[5 empty] | 112.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112063.755 | 1809451.3428 | 112.18 | 100%
[5 empty] | 112.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112086.5163 | 1809818.8623 | 112.2 | 100%
[5 empty] | 112.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112109.2777 | 1810186.3818 | 112.22 | 100%
[5 empty] | 112.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112132.0391 | 1810553.9013 | 112.24 | 100%
[5 empty] | 112.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112154.8005 | 1810921.4209 | 112.26 | 100%
[5 empty] | 112.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112177.5619 | 1811288.9404 | 112.28 | 100%
[5 empty] | 112.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112200.3233 | 1811656.4599 | 112.3 | 100%
[5 empty] | 112.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112223.0846 | 1812023.9794 | 112.32 | 100%
[5 empty] | 112.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112245.846 | 1812391.4989 | 112.34 | 100%
[5 empty] | 112.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112268.6074 | 1812759.0185 | 112.36 | 100%
[5 empty] | 112.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112291.3688 | 1813126.538 | 112.38 | 100%
[5 empty] | 112.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112314.1302 | 1813494.0575 | 112.4 | 100%
[5 empty] | 112.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112336.8916 | 1813861.577 | 112.42 | 100%
[5 empty] | 112.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112359.653 | 1814229.0965 | 112.44 | 100%
[5 empty] | 112.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112382.4143 | 1814596.6161 | 112.46 | 100%
[5 empty] | 112.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112405.1757 | 1814964.1356 | 112.48 | 100%
[5 empty] | 112.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112427.9371 | 1815331.6551 | 112.5 | 100%
[5 empty] | 112.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112450.6985 | 1815699.1746 | 112.52 | 100%
[5 empty] | 112.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112473.4599 | 1816066.6941 | 112.54 | 100%
[5 empty] | 112.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112496.2213 | 1816434.2137 | 112.56 | 100%
[5 empty] | 112.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112518.9826 | 1816801.7332 | 112.58 | 100%
[5 empty] | 112.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112541.744 | 1817169.2527 | 112.6 | 100%
[5 empty] | 112.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112564.5054 | 1817536.7722 | 112.62 | 100%
[5 empty] | 112.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112587.2668 | 1817904.2917 | 112.64 | 100%
[5 empty] | 112.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112610.0282 | 1818271.8113 | 112.66 | 100%
[5 empty] | 112.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112632.7896 | 1818639.3308 | 112.68 | 100%
[5 empty] | 112.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112655.5509 | 1819006.8503 | 112.7 | 100%
[5 empty] | 112.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112678.3123 | 1819374.3698 | 112.72 | 100%
[5 empty] | 112.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112701.0737 | 1819741.8893 | 112.74 | 100%
[5 empty] | 112.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112723.8351 | 1820109.4089 | 112.76 | 100%
[5 empty] | 112.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112746.5965 | 1820476.9284 | 112.78 | 100%
[5 empty] | 112.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112769.3579 | 1820844.4479 | 112.8 | 100%
[5 empty] | 112.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112792.1193 | 1821211.9674 | 112.82 | 100%
[5 empty] | 112.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112814.8806 | 1821579.4869 | 112.84 | 100%
[5 empty] | 112.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112837.642 | 1821947.0065 | 112.86 | 100%
[5 empty] | 112.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112860.4034 | 1822314.526 | 112.88 | 100%
[5 empty] | 112.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112883.1648 | 1822682.0455 | 112.9 | 100%
[5 empty] | 112.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112905.9262 | 1823049.565 | 112.92 | 100%
[5 empty] | 112.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112928.6876 | 1823417.0845 | 112.94 | 100%
[5 empty] | 112.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112951.4489 | 1823784.6041 | 112.96 | 100%
[5 empty] | 112.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112974.2103 | 1824152.1236 | 112.98 | 100%
[5 empty] | 113 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 112996.9717 | 1824519.6431 | 113 | 100%
[5 empty] | 113.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113019.7331 | 1824887.1626 | 113.02 | 100%
[5 empty] | 113.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113042.4945 | 1825254.6821 | 113.04 | 100%
[5 empty] | 113.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113065.2559 | 1825622.2017 | 113.06 | 100%
[5 empty] | 113.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113088.0173 | 1825989.7212 | 113.08 | 100%
[5 empty] | 113.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113110.7786 | 1826357.2407 | 113.1 | 100%
[5 empty] | 113.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113133.54 | 1826724.7602 | 113.12 | 100%
[5 empty] | 113.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113156.3014 | 1827092.2797 | 113.14 | 100%
[5 empty] | 113.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113179.0628 | 1827459.7993 | 113.16 | 100%
[5 empty] | 113.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113201.8242 | 1827827.3188 | 113.18 | 100%
[5 empty] | 113.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113224.5856 | 1828194.8383 | 113.2 | 100%
[5 empty] | 113.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113247.3469 | 1828562.3578 | 113.22 | 100%
[5 empty] | 113.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113270.1083 | 1828929.8773 | 113.24 | 100%
[5 empty] | 113.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113292.8697 | 1829297.3969 | 113.26 | 100%
[5 empty] | 113.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113315.6311 | 1829664.9164 | 113.28 | 100%
[5 empty] | 113.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113338.3925 | 1830032.4359 | 113.3 | 100%
[5 empty] | 113.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113361.1539 | 1830399.9554 | 113.32 | 100%
[5 empty] | 113.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113383.9152 | 1830767.4749 | 113.34 | 100%
[5 empty] | 113.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113406.6766 | 1831134.9945 | 113.36 | 100%
[5 empty] | 113.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113429.438 | 1831502.514 | 113.38 | 100%
[5 empty] | 113.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113452.1994 | 1831870.0335 | 113.4 | 100%
[5 empty] | 113.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113474.9608 | 1832237.553 | 113.42 | 100%
[5 empty] | 113.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113497.7222 | 1832605.0725 | 113.44 | 100%
[5 empty] | 113.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113520.4836 | 1832972.5921 | 113.46 | 100%
[5 empty] | 113.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113543.2449 | 1833340.1116 | 113.48 | 100%
[5 empty] | 113.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113566.0063 | 1833707.6311 | 113.5 | 100%
[5 empty] | 113.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113588.7677 | 1834075.1506 | 113.52 | 100%
[5 empty] | 113.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113611.5291 | 1834442.6701 | 113.54 | 100%
[5 empty] | 113.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113634.2905 | 1834810.1897 | 113.56 | 100%
[5 empty] | 113.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113657.0519 | 1835177.7092 | 113.58 | 100%
[5 empty] | 113.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113679.8132 | 1835545.2287 | 113.6 | 100%
[5 empty] | 113.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113702.5746 | 1835912.7482 | 113.62 | 100%
[5 empty] | 113.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113725.336 | 1836280.2677 | 113.64 | 100%
[5 empty] | 113.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113748.0974 | 1836647.7873 | 113.66 | 100%
[5 empty] | 113.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113770.8588 | 1837015.3068 | 113.68 | 100%
[5 empty] | 113.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113793.6202 | 1837382.8263 | 113.7 | 100%
[5 empty] | 113.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113816.3815 | 1837750.3458 | 113.72 | 100%
[5 empty] | 113.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113839.1429 | 1838117.8653 | 113.74 | 100%
[5 empty] | 113.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113861.9043 | 1838485.3849 | 113.76 | 100%
[5 empty] | 113.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113884.6657 | 1838852.9044 | 113.78 | 100%
[5 empty] | 113.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113907.4271 | 1839220.4239 | 113.8 | 100%
[5 empty] | 113.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113930.1885 | 1839587.9434 | 113.82 | 100%
[5 empty] | 113.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113952.9499 | 1839955.4629 | 113.84 | 100%
[5 empty] | 113.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113975.7112 | 1840322.9825 | 113.86 | 100%
[5 empty] | 113.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 113998.4726 | 1840690.502 | 113.88 | 100%
[5 empty] | 113.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114021.234 | 1841058.0215 | 113.9 | 100%
[5 empty] | 113.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114043.9954 | 1841425.541 | 113.92 | 100%
[5 empty] | 113.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114066.7568 | 1841793.0605 | 113.94 | 100%
[5 empty] | 113.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114089.5182 | 1842160.5801 | 113.96 | 100%
[5 empty] | 113.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114112.2795 | 1842528.0996 | 113.98 | 100%
[5 empty] | 114 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114135.0409 | 1842895.6191 | 114 | 100%
[5 empty] | 114.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114157.8023 | 1843263.1386 | 114.02 | 100%
[5 empty] | 114.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114180.5637 | 1843630.6581 | 114.04 | 100%
[5 empty] | 114.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114203.3251 | 1843998.1777 | 114.06 | 100%
[5 empty] | 114.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114226.0865 | 1844365.6972 | 114.08 | 100%
[5 empty] | 114.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114248.8479 | 1844733.2167 | 114.1 | 100%
[5 empty] | 114.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114271.6092 | 1845100.7362 | 114.12 | 100%
[5 empty] | 114.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114294.3706 | 1845468.2557 | 114.14 | 100%
[5 empty] | 114.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114317.132 | 1845835.7753 | 114.16 | 100%
[5 empty] | 114.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114339.8934 | 1846203.2948 | 114.18 | 100%
[5 empty] | 114.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114362.6548 | 1846570.8143 | 114.2 | 100%
[5 empty] | 114.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114385.4162 | 1846938.3338 | 114.22 | 100%
[5 empty] | 114.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114408.1775 | 1847305.8533 | 114.24 | 100%
[5 empty] | 114.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114430.9389 | 1847673.3729 | 114.26 | 100%
[5 empty] | 114.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114453.7003 | 1848040.8924 | 114.28 | 100%
[5 empty] | 114.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114476.4617 | 1848408.4119 | 114.3 | 100%
[5 empty] | 114.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114499.2231 | 1848775.9314 | 114.32 | 100%
[5 empty] | 114.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114521.9845 | 1849143.4509 | 114.34 | 100%
[5 empty] | 114.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114544.7458 | 1849510.9705 | 114.36 | 100%
[5 empty] | 114.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114567.5072 | 1849878.49 | 114.38 | 100%
[5 empty] | 114.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114590.2686 | 1850246.0095 | 114.4 | 100%
[5 empty] | 114.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114613.03 | 1850613.529 | 114.42 | 100%
[5 empty] | 114.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114635.7914 | 1850981.0485 | 114.44 | 100%
[5 empty] | 114.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114658.5528 | 1851348.5681 | 114.46 | 100%
[5 empty] | 114.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114681.3142 | 1851716.0876 | 114.48 | 100%
[5 empty] | 114.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114704.0755 | 1852083.6071 | 114.5 | 100%
[5 empty] | 114.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114726.8369 | 1852451.1266 | 114.52 | 100%
[5 empty] | 114.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114749.5983 | 1852818.6461 | 114.54 | 100%
[5 empty] | 114.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114772.3597 | 1853186.1657 | 114.56 | 100%
[5 empty] | 114.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114795.1211 | 1853553.6852 | 114.58 | 100%
[5 empty] | 114.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114817.8825 | 1853921.2047 | 114.6 | 100%
[5 empty] | 114.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114840.6438 | 1854288.7242 | 114.62 | 100%
[5 empty] | 114.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114863.4052 | 1854656.2437 | 114.64 | 100%
[5 empty] | 114.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114886.1666 | 1855023.7633 | 114.66 | 100%
[5 empty] | 114.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114908.928 | 1855391.2828 | 114.68 | 100%
[5 empty] | 114.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114931.6894 | 1855758.8023 | 114.7 | 100%
[5 empty] | 114.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114954.4508 | 1856126.3218 | 114.72 | 100%
[5 empty] | 114.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114977.2121 | 1856493.8413 | 114.74 | 100%
[5 empty] | 114.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 114999.9735 | 1856861.3609 | 114.76 | 100%
[5 empty] | 114.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115022.7349 | 1857228.8804 | 114.78 | 100%
[5 empty] | 114.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115045.4963 | 1857596.3999 | 114.8 | 100%
[5 empty] | 114.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115068.2577 | 1857963.9194 | 114.82 | 100%
[5 empty] | 114.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115091.0191 | 1858331.4389 | 114.84 | 100%
[5 empty] | 114.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115113.7805 | 1858698.9585 | 114.86 | 100%
[5 empty] | 114.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115136.5418 | 1859066.478 | 114.88 | 100%
[5 empty] | 114.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115159.3032 | 1859433.9975 | 114.9 | 100%
[5 empty] | 114.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115182.0646 | 1859801.517 | 114.92 | 100%
[5 empty] | 114.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115204.826 | 1860169.0365 | 114.94 | 100%
[5 empty] | 114.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115227.5874 | 1860536.5561 | 114.96 | 100%
[5 empty] | 114.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115250.3488 | 1860904.0756 | 114.98 | 100%
[5 empty] | 115 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115273.1101 | 1861271.5951 | 115 | 100%
[5 empty] | 115.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115295.8715 | 1861639.1146 | 115.02 | 100%
[5 empty] | 115.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115318.6329 | 1862006.6341 | 115.04 | 100%
[5 empty] | 115.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115341.3943 | 1862374.1537 | 115.06 | 100%
[5 empty] | 115.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115364.1557 | 1862741.6732 | 115.08 | 100%
[5 empty] | 115.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115386.9171 | 1863109.1927 | 115.1 | 100%
[5 empty] | 115.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115409.6785 | 1863476.7122 | 115.12 | 100%
[5 empty] | 115.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115432.4398 | 1863844.2317 | 115.14 | 100%
[5 empty] | 115.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115455.2012 | 1864211.7513 | 115.16 | 100%
[5 empty] | 115.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115477.9626 | 1864579.2708 | 115.18 | 100%
[5 empty] | 115.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115500.724 | 1864946.7903 | 115.2 | 100%
[5 empty] | 115.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115523.4854 | 1865314.3098 | 115.22 | 100%
[5 empty] | 115.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115546.2468 | 1865681.8293 | 115.24 | 100%
[5 empty] | 115.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115569.0081 | 1866049.3489 | 115.26 | 100%
[5 empty] | 115.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115591.7695 | 1866416.8684 | 115.28 | 100%
[5 empty] | 115.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115614.5309 | 1866784.3879 | 115.3 | 100%
[5 empty] | 115.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115637.2923 | 1867151.9074 | 115.32 | 100%
[5 empty] | 115.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115660.0537 | 1867519.4269 | 115.34 | 100%
[5 empty] | 115.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115682.8151 | 1867886.9465 | 115.36 | 100%
[5 empty] | 115.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115705.5764 | 1868254.466 | 115.38 | 100%
[5 empty] | 115.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115728.3378 | 1868621.9855 | 115.4 | 100%
[5 empty] | 115.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115751.0992 | 1868989.505 | 115.42 | 100%
[5 empty] | 115.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115773.8606 | 1869357.0245 | 115.44 | 100%
[5 empty] | 115.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115796.622 | 1869724.5441 | 115.46 | 100%
[5 empty] | 115.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115819.3834 | 1870092.0636 | 115.48 | 100%
[5 empty] | 115.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115842.1448 | 1870459.5831 | 115.5 | 100%
[5 empty] | 115.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115864.9061 | 1870827.1026 | 115.52 | 100%
[5 empty] | 115.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115887.6675 | 1871194.6221 | 115.54 | 100%
[5 empty] | 115.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115910.4289 | 1871562.1417 | 115.56 | 100%
[5 empty] | 115.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115933.1903 | 1871929.6612 | 115.58 | 100%
[5 empty] | 115.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115955.9517 | 1872297.1807 | 115.6 | 100%
[5 empty] | 115.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 115978.7131 | 1872664.7002 | 115.62 | 100%
[5 empty] | 115.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116001.4744 | 1873032.2197 | 115.64 | 100%
[5 empty] | 115.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116024.2358 | 1873399.7393 | 115.66 | 100%
[5 empty] | 115.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116046.9972 | 1873767.2588 | 115.68 | 100%
[5 empty] | 115.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116069.7586 | 1874134.7783 | 115.7 | 100%
[5 empty] | 115.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116092.52 | 1874502.2978 | 115.72 | 100%
[5 empty] | 115.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116115.2814 | 1874869.8173 | 115.74 | 100%
[5 empty] | 115.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116138.0428 | 1875237.3369 | 115.76 | 100%
[5 empty] | 115.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116160.8041 | 1875604.8564 | 115.78 | 100%
[5 empty] | 115.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116183.5655 | 1875972.3759 | 115.8 | 100%
[5 empty] | 115.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116206.3269 | 1876339.8954 | 115.82 | 100%
[5 empty] | 115.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116229.0883 | 1876707.4149 | 115.84 | 100%
[5 empty] | 115.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116251.8497 | 1877074.9345 | 115.86 | 100%
[5 empty] | 115.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116274.6111 | 1877442.454 | 115.88 | 100%
[5 empty] | 115.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116297.3724 | 1877809.9735 | 115.9 | 100%
[5 empty] | 115.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116320.1338 | 1878177.493 | 115.92 | 100%
[5 empty] | 115.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116342.8952 | 1878545.0125 | 115.94 | 100%
[5 empty] | 115.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116365.6566 | 1878912.5321 | 115.96 | 100%
[5 empty] | 115.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116388.418 | 1879280.0516 | 115.98 | 100%
[5 empty] | 116 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116411.1794 | 1879647.5711 | 116 | 100%
[5 empty] | 116.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116433.9407 | 1880015.0906 | 116.02 | 100%
[5 empty] | 116.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116456.7021 | 1880382.6101 | 116.04 | 100%
[5 empty] | 116.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116479.4635 | 1880750.1297 | 116.06 | 100%
[5 empty] | 116.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116502.2249 | 1881117.6492 | 116.08 | 100%
[5 empty] | 116.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116524.9863 | 1881485.1687 | 116.1 | 100%
[5 empty] | 116.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116547.7477 | 1881852.6882 | 116.12 | 100%
[5 empty] | 116.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116570.5091 | 1882220.2077 | 116.14 | 100%
[5 empty] | 116.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116593.2704 | 1882587.7273 | 116.16 | 100%
[5 empty] | 116.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116616.0318 | 1882955.2468 | 116.18 | 100%
[5 empty] | 116.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116638.7932 | 1883322.7663 | 116.2 | 100%
[5 empty] | 116.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116661.5546 | 1883690.2858 | 116.22 | 100%
[5 empty] | 116.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116684.316 | 1884057.8053 | 116.24 | 100%
[5 empty] | 116.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116707.0774 | 1884425.3249 | 116.26 | 100%
[5 empty] | 116.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116729.8387 | 1884792.8444 | 116.28 | 100%
[5 empty] | 116.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116752.6001 | 1885160.3639 | 116.3 | 100%
[5 empty] | 116.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116775.3615 | 1885527.8834 | 116.32 | 100%
[5 empty] | 116.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116798.1229 | 1885895.4029 | 116.34 | 100%
[5 empty] | 116.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116820.8843 | 1886262.9225 | 116.36 | 100%
[5 empty] | 116.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116843.6457 | 1886630.442 | 116.38 | 100%
[5 empty] | 116.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116866.407 | 1886997.9615 | 116.4 | 100%
[5 empty] | 116.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116889.1684 | 1887365.481 | 116.42 | 100%
[5 empty] | 116.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116911.9298 | 1887733.0005 | 116.44 | 100%
[5 empty] | 116.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116934.6912 | 1888100.5201 | 116.46 | 100%
[5 empty] | 116.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116957.4526 | 1888468.0396 | 116.48 | 100%
[5 empty] | 116.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 116980.214 | 1888835.5591 | 116.5 | 100%
[5 empty] | 116.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117002.9754 | 1889203.0786 | 116.52 | 100%
[5 empty] | 116.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117025.7367 | 1889570.5981 | 116.54 | 100%
[5 empty] | 116.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117048.4981 | 1889938.1177 | 116.56 | 100%
[5 empty] | 116.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117071.2595 | 1890305.6372 | 116.58 | 100%
[5 empty] | 116.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117094.0209 | 1890673.1567 | 116.6 | 100%
[5 empty] | 116.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117116.7823 | 1891040.6762 | 116.62 | 100%
[5 empty] | 116.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117139.5437 | 1891408.1957 | 116.64 | 100%
[5 empty] | 116.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117162.305 | 1891775.7153 | 116.66 | 100%
[5 empty] | 116.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117185.0664 | 1892143.2348 | 116.68 | 100%
[5 empty] | 116.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117207.8278 | 1892510.7543 | 116.7 | 100%
[5 empty] | 116.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117230.5892 | 1892878.2738 | 116.72 | 100%
[5 empty] | 116.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117253.3506 | 1893245.7933 | 116.74 | 100%
[5 empty] | 116.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117276.112 | 1893613.3129 | 116.76 | 100%
[5 empty] | 116.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117298.8734 | 1893980.8324 | 116.78 | 100%
[5 empty] | 116.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117321.6347 | 1894348.3519 | 116.8 | 100%
[5 empty] | 116.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117344.3961 | 1894715.8714 | 116.82 | 100%
[5 empty] | 116.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117367.1575 | 1895083.3909 | 116.84 | 100%
[5 empty] | 116.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117389.9189 | 1895450.9105 | 116.86 | 100%
[5 empty] | 116.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117412.6803 | 1895818.43 | 116.88 | 100%
[5 empty] | 116.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117435.4417 | 1896185.9495 | 116.9 | 100%
[5 empty] | 116.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117458.203 | 1896553.469 | 116.92 | 100%
[5 empty] | 116.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117480.9644 | 1896920.9885 | 116.94 | 100%
[5 empty] | 116.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117503.7258 | 1897288.5081 | 116.96 | 100%
[5 empty] | 116.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117526.4872 | 1897656.0276 | 116.98 | 100%
[5 empty] | 117 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117549.2486 | 1898023.5471 | 117 | 100%
[5 empty] | 117.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117572.01 | 1898391.0666 | 117.02 | 100%
[5 empty] | 117.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117594.7713 | 1898758.5861 | 117.04 | 100%
[5 empty] | 117.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117617.5327 | 1899126.1057 | 117.06 | 100%
[5 empty] | 117.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117640.2941 | 1899493.6252 | 117.08 | 100%
[5 empty] | 117.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117663.0555 | 1899861.1447 | 117.1 | 100%
[5 empty] | 117.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117685.8169 | 1900228.6642 | 117.12 | 100%
[5 empty] | 117.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117708.5783 | 1900596.1837 | 117.14 | 100%
[5 empty] | 117.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117731.3397 | 1900963.7033 | 117.16 | 100%
[5 empty] | 117.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117754.101 | 1901331.2228 | 117.18 | 100%
[5 empty] | 117.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117776.8624 | 1901698.7423 | 117.2 | 100%
[5 empty] | 117.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117799.6238 | 1902066.2618 | 117.22 | 100%
[5 empty] | 117.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117822.3852 | 1902433.7813 | 117.24 | 100%
[5 empty] | 117.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117845.1466 | 1902801.3009 | 117.26 | 100%
[5 empty] | 117.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117867.908 | 1903168.8204 | 117.28 | 100%
[5 empty] | 117.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117890.6693 | 1903536.3399 | 117.3 | 100%
[5 empty] | 117.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117913.4307 | 1903903.8594 | 117.32 | 100%
[5 empty] | 117.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117936.1921 | 1904271.3789 | 117.34 | 100%
[5 empty] | 117.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117958.9535 | 1904638.8985 | 117.36 | 100%
[5 empty] | 117.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 117981.7149 | 1905006.418 | 117.38 | 100%
[5 empty] | 117.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118004.4763 | 1905373.9375 | 117.4 | 100%
[5 empty] | 117.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118027.2376 | 1905741.457 | 117.42 | 100%
[5 empty] | 117.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118049.999 | 1906108.9765 | 117.44 | 100%
[5 empty] | 117.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118072.7604 | 1906476.4961 | 117.46 | 100%
[5 empty] | 117.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118095.5218 | 1906844.0156 | 117.48 | 100%
[5 empty] | 117.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118118.2832 | 1907211.5351 | 117.5 | 100%
[5 empty] | 117.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118141.0446 | 1907579.0546 | 117.52 | 100%
[5 empty] | 117.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118163.806 | 1907946.5741 | 117.54 | 100%
[5 empty] | 117.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118186.5673 | 1908314.0937 | 117.56 | 100%
[5 empty] | 117.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118209.3287 | 1908681.6132 | 117.58 | 100%
[5 empty] | 117.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118232.0901 | 1909049.1327 | 117.6 | 100%
[5 empty] | 117.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118254.8515 | 1909416.6522 | 117.62 | 100%
[5 empty] | 117.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118277.6129 | 1909784.1717 | 117.64 | 100%
[5 empty] | 117.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118300.3743 | 1910151.6913 | 117.66 | 100%
[5 empty] | 117.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118323.1356 | 1910519.2108 | 117.68 | 100%
[5 empty] | 117.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118345.897 | 1910886.7303 | 117.7 | 100%
[5 empty] | 117.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118368.6584 | 1911254.2498 | 117.72 | 100%
[5 empty] | 117.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118391.4198 | 1911621.7693 | 117.74 | 100%
[5 empty] | 117.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118414.1812 | 1911989.2889 | 117.76 | 100%
[5 empty] | 117.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118436.9426 | 1912356.8084 | 117.78 | 100%
[5 empty] | 117.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118459.704 | 1912724.3279 | 117.8 | 100%
[5 empty] | 117.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118482.4653 | 1913091.8474 | 117.82 | 100%
[5 empty] | 117.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118505.2267 | 1913459.3669 | 117.84 | 100%
[5 empty] | 117.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118527.9881 | 1913826.8865 | 117.86 | 100%
[5 empty] | 117.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118550.7495 | 1914194.406 | 117.88 | 100%
[5 empty] | 117.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118573.5109 | 1914561.9255 | 117.9 | 100%
[5 empty] | 117.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118596.2723 | 1914929.445 | 117.92 | 100%
[5 empty] | 117.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118619.0336 | 1915296.9645 | 117.94 | 100%
[5 empty] | 117.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118641.795 | 1915664.4841 | 117.96 | 100%
[5 empty] | 117.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118664.5564 | 1916032.0036 | 117.98 | 100%
[5 empty] | 118 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118687.3178 | 1916399.5231 | 118 | 100%
[5 empty] | 118.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118710.0792 | 1916767.0426 | 118.02 | 100%
[5 empty] | 118.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118732.8406 | 1917134.5621 | 118.04 | 100%
[5 empty] | 118.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118755.6019 | 1917502.0817 | 118.06 | 100%
[5 empty] | 118.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118778.3633 | 1917869.6012 | 118.08 | 100%
[5 empty] | 118.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118801.1247 | 1918237.1207 | 118.1 | 100%
[5 empty] | 118.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118823.8861 | 1918604.6402 | 118.12 | 100%
[5 empty] | 118.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118846.6475 | 1918972.1597 | 118.14 | 100%
[5 empty] | 118.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118869.4089 | 1919339.6793 | 118.16 | 100%
[5 empty] | 118.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118892.1703 | 1919707.1988 | 118.18 | 100%
[5 empty] | 118.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118914.9316 | 1920074.7183 | 118.2 | 100%
[5 empty] | 118.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118937.693 | 1920442.2378 | 118.22 | 100%
[5 empty] | 118.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118960.4544 | 1920809.7573 | 118.24 | 100%
[5 empty] | 118.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 118983.2158 | 1921177.2769 | 118.26 | 100%
[5 empty] | 118.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119005.9772 | 1921544.7964 | 118.28 | 100%
[5 empty] | 118.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119028.7386 | 1921912.3159 | 118.3 | 100%
[5 empty] | 118.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119051.4999 | 1922279.8354 | 118.32 | 100%
[5 empty] | 118.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119074.2613 | 1922647.3549 | 118.34 | 100%
[5 empty] | 118.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119097.0227 | 1923014.8745 | 118.36 | 100%
[5 empty] | 118.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119119.7841 | 1923382.394 | 118.38 | 100%
[5 empty] | 118.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119142.5455 | 1923749.9135 | 118.4 | 100%
[5 empty] | 118.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119165.3069 | 1924117.433 | 118.42 | 100%
[5 empty] | 118.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119188.0683 | 1924484.9525 | 118.44 | 100%
[5 empty] | 118.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119210.8296 | 1924852.4721 | 118.46 | 100%
[5 empty] | 118.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119233.591 | 1925219.9916 | 118.48 | 100%
[5 empty] | 118.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119256.3524 | 1925587.5111 | 118.5 | 100%
[5 empty] | 118.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119279.1138 | 1925955.0306 | 118.52 | 100%
[5 empty] | 118.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119301.8752 | 1926322.5501 | 118.54 | 100%
[5 empty] | 118.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119324.6366 | 1926690.0697 | 118.56 | 100%
[5 empty] | 118.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119347.3979 | 1927057.5892 | 118.58 | 100%
[5 empty] | 118.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119370.1593 | 1927425.1087 | 118.6 | 100%
[5 empty] | 118.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119392.9207 | 1927792.6282 | 118.62 | 100%
[5 empty] | 118.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119415.6821 | 1928160.1477 | 118.64 | 100%
[5 empty] | 118.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119438.4435 | 1928527.6673 | 118.66 | 100%
[5 empty] | 118.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119461.2049 | 1928895.1868 | 118.68 | 100%
[5 empty] | 118.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119483.9662 | 1929262.7063 | 118.7 | 100%
[5 empty] | 118.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119506.7276 | 1929630.2258 | 118.72 | 100%
[5 empty] | 118.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119529.489 | 1929997.7453 | 118.74 | 100%
[5 empty] | 118.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119552.2504 | 1930365.2649 | 118.76 | 100%
[5 empty] | 118.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119575.0118 | 1930732.7844 | 118.78 | 100%
[5 empty] | 118.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119597.7732 | 1931100.3039 | 118.8 | 100%
[5 empty] | 118.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119620.5346 | 1931467.8234 | 118.82 | 100%
[5 empty] | 118.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119643.2959 | 1931835.3429 | 118.84 | 100%
[5 empty] | 118.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119666.0573 | 1932202.8625 | 118.86 | 100%
[5 empty] | 118.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119688.8187 | 1932570.382 | 118.88 | 100%
[5 empty] | 118.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119711.5801 | 1932937.9015 | 118.9 | 100%
[5 empty] | 118.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119734.3415 | 1933305.421 | 118.92 | 100%
[5 empty] | 118.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119757.1029 | 1933672.9405 | 118.94 | 100%
[5 empty] | 118.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119779.8642 | 1934040.4601 | 118.96 | 100%
[5 empty] | 118.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119802.6256 | 1934407.9796 | 118.98 | 100%
[5 empty] | 119 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119825.387 | 1934775.4991 | 119 | 100%
[5 empty] | 119.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119848.1484 | 1935143.0186 | 119.02 | 100%
[5 empty] | 119.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119870.9098 | 1935510.5381 | 119.04 | 100%
[5 empty] | 119.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119893.6712 | 1935878.0577 | 119.06 | 100%
[5 empty] | 119.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119916.4325 | 1936245.5772 | 119.08 | 100%
[5 empty] | 119.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119939.1939 | 1936613.0967 | 119.1 | 100%
[5 empty] | 119.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119961.9553 | 1936980.6162 | 119.12 | 100%
[5 empty] | 119.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 119984.7167 | 1937348.1357 | 119.14 | 100%
[5 empty] | 119.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120007.4781 | 1937715.6553 | 119.16 | 100%
[5 empty] | 119.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120030.2395 | 1938083.1748 | 119.18 | 100%
[5 empty] | 119.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120053.0009 | 1938450.6943 | 119.2 | 100%
[5 empty] | 119.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120075.7622 | 1938818.2138 | 119.22 | 100%
[5 empty] | 119.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120098.5236 | 1939185.7333 | 119.24 | 100%
[5 empty] | 119.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120121.285 | 1939553.2529 | 119.26 | 100%
[5 empty] | 119.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120144.0464 | 1939920.7724 | 119.28 | 100%
[5 empty] | 119.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120166.8078 | 1940288.2919 | 119.3 | 100%
[5 empty] | 119.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120189.5692 | 1940655.8114 | 119.32 | 100%
[5 empty] | 119.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120212.3305 | 1941023.3309 | 119.34 | 100%
[5 empty] | 119.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120235.0919 | 1941390.8505 | 119.36 | 100%
[5 empty] | 119.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120257.8533 | 1941758.37 | 119.38 | 100%
[5 empty] | 119.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120280.6147 | 1942125.8895 | 119.4 | 100%
[5 empty] | 119.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120303.3761 | 1942493.409 | 119.42 | 100%
[5 empty] | 119.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120326.1375 | 1942860.9285 | 119.44 | 100%
[5 empty] | 119.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120348.8989 | 1943228.4481 | 119.46 | 100%
[5 empty] | 119.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120371.6602 | 1943595.9676 | 119.48 | 100%
[5 empty] | 119.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120394.4216 | 1943963.4871 | 119.5 | 100%
[5 empty] | 119.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120417.183 | 1944331.0066 | 119.52 | 100%
[5 empty] | 119.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120439.9444 | 1944698.5261 | 119.54 | 100%
[5 empty] | 119.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120462.7058 | 1945066.0457 | 119.56 | 100%
[5 empty] | 119.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120485.4672 | 1945433.5652 | 119.58 | 100%
[5 empty] | 119.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120508.2285 | 1945801.0847 | 119.6 | 100%
[5 empty] | 119.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120530.9899 | 1946168.6042 | 119.62 | 100%
[5 empty] | 119.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120553.7513 | 1946536.1237 | 119.64 | 100%
[5 empty] | 119.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120576.5127 | 1946903.6433 | 119.66 | 100%
[5 empty] | 119.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120599.2741 | 1947271.1628 | 119.68 | 100%
[5 empty] | 119.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120622.0355 | 1947638.6823 | 119.7 | 100%
[5 empty] | 119.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120644.7968 | 1948006.2018 | 119.72 | 100%
[5 empty] | 119.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120667.5582 | 1948373.7213 | 119.74 | 100%
[5 empty] | 119.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120690.3196 | 1948741.2409 | 119.76 | 100%
[5 empty] | 119.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120713.081 | 1949108.7604 | 119.78 | 100%
[5 empty] | 119.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120735.8424 | 1949476.2799 | 119.8 | 100%
[5 empty] | 119.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120758.6038 | 1949843.7994 | 119.82 | 100%
[5 empty] | 119.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120781.3652 | 1950211.3189 | 119.84 | 100%
[5 empty] | 119.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120804.1265 | 1950578.8385 | 119.86 | 100%
[5 empty] | 119.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120826.8879 | 1950946.358 | 119.88 | 100%
[5 empty] | 119.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120849.6493 | 1951313.8775 | 119.9 | 100%
[5 empty] | 119.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120872.4107 | 1951681.397 | 119.92 | 100%
[5 empty] | 119.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120895.1721 | 1952048.9165 | 119.94 | 100%
[5 empty] | 119.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120917.9335 | 1952416.4361 | 119.96 | 100%
[5 empty] | 119.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120940.6948 | 1952783.9556 | 119.98 | 100%
[5 empty] | 120 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120963.4562 | 1953151.4751 | 120 | 100%
[5 empty] | 120.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 120986.2176 | 1953518.9946 | 120.02 | 100%
[5 empty] | 120.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121008.979 | 1953886.5141 | 120.04 | 100%
[5 empty] | 120.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121031.7404 | 1954254.0337 | 120.06 | 100%
[5 empty] | 120.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121054.5018 | 1954621.5532 | 120.08 | 100%
[5 empty] | 120.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121077.2631 | 1954989.0727 | 120.1 | 100%
[5 empty] | 120.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121100.0245 | 1955356.5922 | 120.12 | 100%
[5 empty] | 120.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121122.7859 | 1955724.1117 | 120.14 | 100%
[5 empty] | 120.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121145.5473 | 1956091.6313 | 120.16 | 100%
[5 empty] | 120.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121168.3087 | 1956459.1508 | 120.18 | 100%
[5 empty] | 120.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121191.0701 | 1956826.6703 | 120.2 | 100%
[5 empty] | 120.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121213.8315 | 1957194.1898 | 120.22 | 100%
[5 empty] | 120.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121236.5928 | 1957561.7093 | 120.24 | 100%
[5 empty] | 120.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121259.3542 | 1957929.2289 | 120.26 | 100%
[5 empty] | 120.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121282.1156 | 1958296.7484 | 120.28 | 100%
[5 empty] | 120.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121304.877 | 1958664.2679 | 120.3 | 100%
[5 empty] | 120.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121327.6384 | 1959031.7874 | 120.32 | 100%
[5 empty] | 120.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121350.3998 | 1959399.3069 | 120.34 | 100%
[5 empty] | 120.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121373.1611 | 1959766.8265 | 120.36 | 100%
[5 empty] | 120.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121395.9225 | 1960134.346 | 120.38 | 100%
[5 empty] | 120.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121418.6839 | 1960501.8655 | 120.4 | 100%
[5 empty] | 120.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121441.4453 | 1960869.385 | 120.42 | 100%
[5 empty] | 120.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121464.2067 | 1961236.9045 | 120.44 | 100%
[5 empty] | 120.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121486.9681 | 1961604.4241 | 120.46 | 100%
[5 empty] | 120.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121509.7295 | 1961971.9436 | 120.48 | 100%
[5 empty] | 120.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121532.4908 | 1962339.4631 | 120.5 | 100%
[5 empty] | 120.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121555.2522 | 1962706.9826 | 120.52 | 100%
[5 empty] | 120.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121578.0136 | 1963074.5021 | 120.54 | 100%
[5 empty] | 120.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121600.775 | 1963442.0217 | 120.56 | 100%
[5 empty] | 120.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121623.5364 | 1963809.5412 | 120.58 | 100%
[5 empty] | 120.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121646.2978 | 1964177.0607 | 120.6 | 100%
[5 empty] | 120.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121669.0591 | 1964544.5802 | 120.62 | 100%
[5 empty] | 120.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121691.8205 | 1964912.0997 | 120.64 | 100%
[5 empty] | 120.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121714.5819 | 1965279.6193 | 120.66 | 100%
[5 empty] | 120.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121737.3433 | 1965647.1388 | 120.68 | 100%
[5 empty] | 120.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121760.1047 | 1966014.6583 | 120.7 | 100%
[5 empty] | 120.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121782.8661 | 1966382.1778 | 120.72 | 100%
[5 empty] | 120.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121805.6274 | 1966749.6973 | 120.74 | 100%
[5 empty] | 120.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121828.3888 | 1967117.2169 | 120.76 | 100%
[5 empty] | 120.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121851.1502 | 1967484.7364 | 120.78 | 100%
[5 empty] | 120.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121873.9116 | 1967852.2559 | 120.8 | 100%
[5 empty] | 120.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121896.673 | 1968219.7754 | 120.82 | 100%
[5 empty] | 120.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121919.4344 | 1968587.2949 | 120.84 | 100%
[5 empty] | 120.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121942.1958 | 1968954.8145 | 120.86 | 100%
[5 empty] | 120.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121964.9571 | 1969322.334 | 120.88 | 100%
[5 empty] | 120.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 121987.7185 | 1969689.8535 | 120.9 | 100%
[5 empty] | 120.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122010.4799 | 1970057.373 | 120.92 | 100%
[5 empty] | 120.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122033.2413 | 1970424.8925 | 120.94 | 100%
[5 empty] | 120.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122056.0027 | 1970792.4121 | 120.96 | 100%
[5 empty] | 120.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122078.7641 | 1971159.9316 | 120.98 | 100%
[5 empty] | 121 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122101.5254 | 1971527.4511 | 121 | 100%
[5 empty] | 121.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122124.2868 | 1971894.9706 | 121.02 | 100%
[5 empty] | 121.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122147.0482 | 1972262.4901 | 121.04 | 100%
[5 empty] | 121.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122169.8096 | 1972630.0097 | 121.06 | 100%
[5 empty] | 121.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122192.571 | 1972997.5292 | 121.08 | 100%
[5 empty] | 121.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122215.3324 | 1973365.0487 | 121.1 | 100%
[5 empty] | 121.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122238.0937 | 1973732.5682 | 121.12 | 100%
[5 empty] | 121.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122260.8551 | 1974100.0877 | 121.14 | 100%
[5 empty] | 121.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122283.6165 | 1974467.6073 | 121.16 | 100%
[5 empty] | 121.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122306.3779 | 1974835.1268 | 121.18 | 100%
[5 empty] | 121.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122329.1393 | 1975202.6463 | 121.2 | 100%
[5 empty] | 121.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122351.9007 | 1975570.1658 | 121.22 | 100%
[5 empty] | 121.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122374.6621 | 1975937.6853 | 121.24 | 100%
[5 empty] | 121.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122397.4234 | 1976305.2049 | 121.26 | 100%
[5 empty] | 121.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122420.1848 | 1976672.7244 | 121.28 | 100%
[5 empty] | 121.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122442.9462 | 1977040.2439 | 121.3 | 100%
[5 empty] | 121.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122465.7076 | 1977407.7634 | 121.32 | 100%
[5 empty] | 121.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122488.469 | 1977775.2829 | 121.34 | 100%
[5 empty] | 121.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122511.2304 | 1978142.8025 | 121.36 | 100%
[5 empty] | 121.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122533.9917 | 1978510.322 | 121.38 | 100%
[5 empty] | 121.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122556.7531 | 1978877.8415 | 121.4 | 100%
[5 empty] | 121.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122579.5145 | 1979245.361 | 121.42 | 100%
[5 empty] | 121.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122602.2759 | 1979612.8805 | 121.44 | 100%
[5 empty] | 121.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122625.0373 | 1979980.4001 | 121.46 | 100%
[5 empty] | 121.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122647.7987 | 1980347.9196 | 121.48 | 100%
[5 empty] | 121.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122670.5601 | 1980715.4391 | 121.5 | 100%
[5 empty] | 121.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122693.3214 | 1981082.9586 | 121.52 | 100%
[5 empty] | 121.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122716.0828 | 1981450.4781 | 121.54 | 100%
[5 empty] | 121.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122738.8442 | 1981817.9977 | 121.56 | 100%
[5 empty] | 121.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122761.6056 | 1982185.5172 | 121.58 | 100%
[5 empty] | 121.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122784.367 | 1982553.0367 | 121.6 | 100%
[5 empty] | 121.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122807.1284 | 1982920.5562 | 121.62 | 100%
[5 empty] | 121.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122829.8897 | 1983288.0757 | 121.64 | 100%
[5 empty] | 121.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122852.6511 | 1983655.5953 | 121.66 | 100%
[5 empty] | 121.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122875.4125 | 1984023.1148 | 121.68 | 100%
[5 empty] | 121.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122898.1739 | 1984390.6343 | 121.7 | 100%
[5 empty] | 121.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122920.9353 | 1984758.1538 | 121.72 | 100%
[5 empty] | 121.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122943.6967 | 1985125.6733 | 121.74 | 100%
[5 empty] | 121.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122966.458 | 1985493.1929 | 121.76 | 100%
[5 empty] | 121.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 122989.2194 | 1985860.7124 | 121.78 | 100%
[5 empty] | 121.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123011.9808 | 1986228.2319 | 121.8 | 100%
[5 empty] | 121.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123034.7422 | 1986595.7514 | 121.82 | 100%
[5 empty] | 121.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123057.5036 | 1986963.2709 | 121.84 | 100%
[5 empty] | 121.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123080.265 | 1987330.7905 | 121.86 | 100%
[5 empty] | 121.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123103.0264 | 1987698.31 | 121.88 | 100%
[5 empty] | 121.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123125.7877 | 1988065.8295 | 121.9 | 100%
[5 empty] | 121.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123148.5491 | 1988433.349 | 121.92 | 100%
[5 empty] | 121.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123171.3105 | 1988800.8685 | 121.94 | 100%
[5 empty] | 121.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123194.0719 | 1989168.3881 | 121.96 | 100%
[5 empty] | 121.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123216.8333 | 1989535.9076 | 121.98 | 100%
[5 empty] | 122 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123239.5947 | 1989903.4271 | 122 | 100%
[5 empty] | 122.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123262.356 | 1990270.9466 | 122.02 | 100%
[5 empty] | 122.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123285.1174 | 1990638.4661 | 122.04 | 100%
[5 empty] | 122.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123307.8788 | 1991005.9857 | 122.06 | 100%
[5 empty] | 122.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123330.6402 | 1991373.5052 | 122.08 | 100%
[5 empty] | 122.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123353.4016 | 1991741.0247 | 122.1 | 100%
[5 empty] | 122.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123376.163 | 1992108.5442 | 122.12 | 100%
[5 empty] | 122.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123398.9244 | 1992476.0637 | 122.14 | 100%
[5 empty] | 122.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123421.6857 | 1992843.5833 | 122.16 | 100%
[5 empty] | 122.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123444.4471 | 1993211.1028 | 122.18 | 100%
[5 empty] | 122.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123467.2085 | 1993578.6223 | 122.2 | 100%
[5 empty] | 122.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123489.9699 | 1993946.1418 | 122.22 | 100%
[5 empty] | 122.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123512.7313 | 1994313.6613 | 122.24 | 100%
[5 empty] | 122.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123535.4927 | 1994681.1809 | 122.26 | 100%
[5 empty] | 122.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123558.254 | 1995048.7004 | 122.28 | 100%
[5 empty] | 122.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123581.0154 | 1995416.2199 | 122.3 | 100%
[5 empty] | 122.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123603.7768 | 1995783.7394 | 122.32 | 100%
[5 empty] | 122.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123626.5382 | 1996151.2589 | 122.34 | 100%
[5 empty] | 122.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123649.2996 | 1996518.7785 | 122.36 | 100%
[5 empty] | 122.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123672.061 | 1996886.298 | 122.38 | 100%
[5 empty] | 122.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123694.8223 | 1997253.8175 | 122.4 | 100%
[5 empty] | 122.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123717.5837 | 1997621.337 | 122.42 | 100%
[5 empty] | 122.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123740.3451 | 1997988.8565 | 122.44 | 100%
[5 empty] | 122.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123763.1065 | 1998356.3761 | 122.46 | 100%
[5 empty] | 122.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123785.8679 | 1998723.8956 | 122.48 | 100%
[5 empty] | 122.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123808.6293 | 1999091.4151 | 122.5 | 100%
[5 empty] | 122.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123831.3907 | 1999458.9346 | 122.52 | 100%
[5 empty] | 122.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123854.152 | 1999826.4541 | 122.54 | 100%
[5 empty] | 122.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123876.9134 | 2000193.9737 | 122.56 | 100%
[5 empty] | 122.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123899.6748 | 2000561.4932 | 122.58 | 100%
[5 empty] | 122.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123922.4362 | 2000929.0127 | 122.6 | 100%
[5 empty] | 122.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123945.1976 | 2001296.5322 | 122.62 | 100%
[5 empty] | 122.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123967.959 | 2001664.0517 | 122.64 | 100%
[5 empty] | 122.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 123990.7203 | 2002031.5713 | 122.66 | 100%
[5 empty] | 122.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124013.4817 | 2002399.0908 | 122.68 | 100%
[5 empty] | 122.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124036.2431 | 2002766.6103 | 122.7 | 100%
[5 empty] | 122.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124059.0045 | 2003134.1298 | 122.72 | 100%
[5 empty] | 122.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124081.7659 | 2003501.6493 | 122.74 | 100%
[5 empty] | 122.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124104.5273 | 2003869.1689 | 122.76 | 100%
[5 empty] | 122.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124127.2886 | 2004236.6884 | 122.78 | 100%
[5 empty] | 122.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124150.05 | 2004604.2079 | 122.8 | 100%
[5 empty] | 122.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124172.8114 | 2004971.7274 | 122.82 | 100%
[5 empty] | 122.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124195.5728 | 2005339.2469 | 122.84 | 100%
[5 empty] | 122.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124218.3342 | 2005706.7665 | 122.86 | 100%
[5 empty] | 122.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124241.0956 | 2006074.286 | 122.88 | 100%
[5 empty] | 122.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124263.857 | 2006441.8055 | 122.9 | 100%
[5 empty] | 122.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124286.6183 | 2006809.325 | 122.92 | 100%
[5 empty] | 122.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124309.3797 | 2007176.8445 | 122.94 | 100%
[5 empty] | 122.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124332.1411 | 2007544.3641 | 122.96 | 100%
[5 empty] | 122.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124354.9025 | 2007911.8836 | 122.98 | 100%
[5 empty] | 123 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124377.6639 | 2008279.4031 | 123 | 100%
[5 empty] | 123.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124400.4253 | 2008646.9226 | 123.02 | 100%
[5 empty] | 123.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124423.1866 | 2009014.4421 | 123.04 | 100%
[5 empty] | 123.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124445.948 | 2009381.9617 | 123.06 | 100%
[5 empty] | 123.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124468.7094 | 2009749.4812 | 123.08 | 100%
[5 empty] | 123.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124491.4708 | 2010117.0007 | 123.1 | 100%
[5 empty] | 123.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124514.2322 | 2010484.5202 | 123.12 | 100%
[5 empty] | 123.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124536.9936 | 2010852.0397 | 123.14 | 100%
[5 empty] | 123.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124559.755 | 2011219.5593 | 123.16 | 100%
[5 empty] | 123.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124582.5163 | 2011587.0788 | 123.18 | 100%
[5 empty] | 123.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124605.2777 | 2011954.5983 | 123.2 | 100%
[5 empty] | 123.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124628.0391 | 2012322.1178 | 123.22 | 100%
[5 empty] | 123.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124650.8005 | 2012689.6373 | 123.24 | 100%
[5 empty] | 123.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124673.5619 | 2013057.1569 | 123.26 | 100%
[5 empty] | 123.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124696.3233 | 2013424.6764 | 123.28 | 100%
[5 empty] | 123.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124719.0846 | 2013792.1959 | 123.3 | 100%
[5 empty] | 123.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124741.846 | 2014159.7154 | 123.32 | 100%
[5 empty] | 123.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124764.6074 | 2014527.2349 | 123.34 | 100%
[5 empty] | 123.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124787.3688 | 2014894.7545 | 123.36 | 100%
[5 empty] | 123.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124810.1302 | 2015262.274 | 123.38 | 100%
[5 empty] | 123.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124832.8916 | 2015629.7935 | 123.4 | 100%
[5 empty] | 123.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124855.6529 | 2015997.313 | 123.42 | 100%
[5 empty] | 123.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124878.4143 | 2016364.8325 | 123.44 | 100%
[5 empty] | 123.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124901.1757 | 2016732.3521 | 123.46 | 100%
[5 empty] | 123.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124923.9371 | 2017099.8716 | 123.48 | 100%
[5 empty] | 123.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124946.6985 | 2017467.3911 | 123.5 | 100%
[5 empty] | 123.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124969.4599 | 2017834.9106 | 123.52 | 100%
[5 empty] | 123.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 124992.2213 | 2018202.4301 | 123.54 | 100%
[5 empty] | 123.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125014.9826 | 2018569.9497 | 123.56 | 100%
[5 empty] | 123.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125037.744 | 2018937.4692 | 123.58 | 100%
[5 empty] | 123.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125060.5054 | 2019304.9887 | 123.6 | 100%
[5 empty] | 123.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125083.2668 | 2019672.5082 | 123.62 | 100%
[5 empty] | 123.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125106.0282 | 2020040.0277 | 123.64 | 100%
[5 empty] | 123.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125128.7896 | 2020407.5473 | 123.66 | 100%
[5 empty] | 123.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125151.5509 | 2020775.0668 | 123.68 | 100%
[5 empty] | 123.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125174.3123 | 2021142.5863 | 123.7 | 100%
[5 empty] | 123.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125197.0737 | 2021510.1058 | 123.72 | 100%
[5 empty] | 123.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125219.8351 | 2021877.6253 | 123.74 | 100%
[5 empty] | 123.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125242.5965 | 2022245.1449 | 123.76 | 100%
[5 empty] | 123.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125265.3579 | 2022612.6644 | 123.78 | 100%
[5 empty] | 123.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125288.1192 | 2022980.1839 | 123.8 | 100%
[5 empty] | 123.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125310.8806 | 2023347.7034 | 123.82 | 100%
[5 empty] | 123.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125333.642 | 2023715.2229 | 123.84 | 100%
[5 empty] | 123.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125356.4034 | 2024082.7425 | 123.86 | 100%
[5 empty] | 123.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125379.1648 | 2024450.262 | 123.88 | 100%
[5 empty] | 123.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125401.9262 | 2024817.7815 | 123.9 | 100%
[5 empty] | 123.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125424.6876 | 2025185.301 | 123.92 | 100%
[5 empty] | 123.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125447.4489 | 2025552.8205 | 123.94 | 100%
[5 empty] | 123.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125470.2103 | 2025920.3401 | 123.96 | 100%
[5 empty] | 123.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125492.9717 | 2026287.8596 | 123.98 | 100%
[5 empty] | 124 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125515.7331 | 2026655.3791 | 124 | 100%
[5 empty] | 124.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125538.4945 | 2027022.8986 | 124.02 | 100%
[5 empty] | 124.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125561.2559 | 2027390.4181 | 124.04 | 100%
[5 empty] | 124.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125584.0172 | 2027757.9377 | 124.06 | 100%
[5 empty] | 124.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125606.7786 | 2028125.4572 | 124.08 | 100%
[5 empty] | 124.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125629.54 | 2028492.9767 | 124.1 | 100%
[5 empty] | 124.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125652.3014 | 2028860.4962 | 124.12 | 100%
[5 empty] | 124.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125675.0628 | 2029228.0157 | 124.14 | 100%
[5 empty] | 124.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125697.8242 | 2029595.5353 | 124.16 | 100%
[5 empty] | 124.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125720.5856 | 2029963.0548 | 124.18 | 100%
[5 empty] | 124.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125743.3469 | 2030330.5743 | 124.2 | 100%
[5 empty] | 124.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125766.1083 | 2030698.0938 | 124.22 | 100%
[5 empty] | 124.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125788.8697 | 2031065.6133 | 124.24 | 100%
[5 empty] | 124.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125811.6311 | 2031433.1329 | 124.26 | 100%
[5 empty] | 124.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125834.3925 | 2031800.6524 | 124.28 | 100%
[5 empty] | 124.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125857.1539 | 2032168.1719 | 124.3 | 100%
[5 empty] | 124.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125879.9152 | 2032535.6914 | 124.32 | 100%
[5 empty] | 124.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125902.6766 | 2032903.2109 | 124.34 | 100%
[5 empty] | 124.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125925.438 | 2033270.7305 | 124.36 | 100%
[5 empty] | 124.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125948.1994 | 2033638.25 | 124.38 | 100%
[5 empty] | 124.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125970.9608 | 2034005.7695 | 124.4 | 100%
[5 empty] | 124.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 125993.7222 | 2034373.289 | 124.42 | 100%
[5 empty] | 124.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126016.4835 | 2034740.8085 | 124.44 | 100%
[5 empty] | 124.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126039.2449 | 2035108.3281 | 124.46 | 100%
[5 empty] | 124.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126062.0063 | 2035475.8476 | 124.48 | 100%
[5 empty] | 124.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126084.7677 | 2035843.3671 | 124.5 | 100%
[5 empty] | 124.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126107.5291 | 2036210.8866 | 124.52 | 100%
[5 empty] | 124.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126130.2905 | 2036578.4061 | 124.54 | 100%
[5 empty] | 124.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126153.0519 | 2036945.9257 | 124.56 | 100%
[5 empty] | 124.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126175.8132 | 2037313.4452 | 124.58 | 100%
[5 empty] | 124.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126198.5746 | 2037680.9647 | 124.6 | 100%
[5 empty] | 124.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126221.336 | 2038048.4842 | 124.62 | 100%
[5 empty] | 124.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126244.0974 | 2038416.0037 | 124.64 | 100%
[5 empty] | 124.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126266.8588 | 2038783.5233 | 124.66 | 100%
[5 empty] | 124.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126289.6202 | 2039151.0428 | 124.68 | 100%
[5 empty] | 124.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126312.3815 | 2039518.5623 | 124.7 | 100%
[5 empty] | 124.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126335.1429 | 2039886.0818 | 124.72 | 100%
[5 empty] | 124.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126357.9043 | 2040253.6013 | 124.74 | 100%
[5 empty] | 124.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126380.6657 | 2040621.1209 | 124.76 | 100%
[5 empty] | 124.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126403.4271 | 2040988.6404 | 124.78 | 100%
[5 empty] | 124.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126426.1885 | 2041356.1599 | 124.8 | 100%
[5 empty] | 124.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126448.9498 | 2041723.6794 | 124.82 | 100%
[5 empty] | 124.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126471.7112 | 2042091.1989 | 124.84 | 100%
[5 empty] | 124.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126494.4726 | 2042458.7185 | 124.86 | 100%
[5 empty] | 124.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126517.234 | 2042826.238 | 124.88 | 100%
[5 empty] | 124.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126539.9954 | 2043193.7575 | 124.9 | 100%
[5 empty] | 124.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126562.7568 | 2043561.277 | 124.92 | 100%
[5 empty] | 124.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126585.5182 | 2043928.7965 | 124.94 | 100%
[5 empty] | 124.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126608.2795 | 2044296.3161 | 124.96 | 100%
[5 empty] | 124.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126631.0409 | 2044663.8356 | 124.98 | 100%
[5 empty] | 125 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126653.8023 | 2045031.3551 | 125 | 100%
[5 empty] | 125.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126676.5637 | 2045398.8746 | 125.02 | 100%
[5 empty] | 125.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126699.3251 | 2045766.3941 | 125.04 | 100%
[5 empty] | 125.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126722.0865 | 2046133.9137 | 125.06 | 100%
[5 empty] | 125.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126744.8478 | 2046501.4332 | 125.08 | 100%
[5 empty] | 125.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126767.6092 | 2046868.9527 | 125.1 | 100%
[5 empty] | 125.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126790.3706 | 2047236.4722 | 125.12 | 100%
[5 empty] | 125.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126813.132 | 2047603.9917 | 125.14 | 100%
[5 empty] | 125.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126835.8934 | 2047971.5113 | 125.16 | 100%
[5 empty] | 125.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126858.6548 | 2048339.0308 | 125.18 | 100%
[5 empty] | 125.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126881.4162 | 2048706.5503 | 125.2 | 100%
[5 empty] | 125.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126904.1775 | 2049074.0698 | 125.22 | 100%
[5 empty] | 125.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126926.9389 | 2049441.5893 | 125.24 | 100%
[5 empty] | 125.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126949.7003 | 2049809.1089 | 125.26 | 100%
[5 empty] | 125.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126972.4617 | 2050176.6284 | 125.28 | 100%
[5 empty] | 125.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 126995.2231 | 2050544.1479 | 125.3 | 100%
[5 empty] | 125.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127017.9845 | 2050911.6674 | 125.32 | 100%
[5 empty] | 125.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127040.7458 | 2051279.1869 | 125.34 | 100%
[5 empty] | 125.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127063.5072 | 2051646.7065 | 125.36 | 100%
[5 empty] | 125.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127086.2686 | 2052014.226 | 125.38 | 100%
[5 empty] | 125.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127109.03 | 2052381.7455 | 125.4 | 100%
[5 empty] | 125.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127131.7914 | 2052749.265 | 125.42 | 100%
[5 empty] | 125.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127154.5528 | 2053116.7845 | 125.44 | 100%
[5 empty] | 125.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127177.3141 | 2053484.3041 | 125.46 | 100%
[5 empty] | 125.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127200.0755 | 2053851.8236 | 125.48 | 100%
[5 empty] | 125.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127222.8369 | 2054219.3431 | 125.5 | 100%
[5 empty] | 125.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127245.5983 | 2054586.8626 | 125.52 | 100%
[5 empty] | 125.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127268.3597 | 2054954.3821 | 125.54 | 100%
[5 empty] | 125.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127291.1211 | 2055321.9017 | 125.56 | 100%
[5 empty] | 125.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127313.8825 | 2055689.4212 | 125.58 | 100%
[5 empty] | 125.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127336.6438 | 2056056.9407 | 125.6 | 100%
[5 empty] | 125.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127359.4052 | 2056424.4602 | 125.62 | 100%
[5 empty] | 125.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127382.1666 | 2056791.9797 | 125.64 | 100%
[5 empty] | 125.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127404.928 | 2057159.4993 | 125.66 | 100%
[5 empty] | 125.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127427.6894 | 2057527.0188 | 125.68 | 100%
[5 empty] | 125.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127450.4508 | 2057894.5383 | 125.7 | 100%
[5 empty] | 125.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127473.2121 | 2058262.0578 | 125.72 | 100%
[5 empty] | 125.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127495.9735 | 2058629.5773 | 125.74 | 100%
[5 empty] | 125.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127518.7349 | 2058997.0969 | 125.76 | 100%
[5 empty] | 125.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127541.4963 | 2059364.6164 | 125.78 | 100%
[5 empty] | 125.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127564.2577 | 2059732.1359 | 125.8 | 100%
[5 empty] | 125.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127587.0191 | 2060099.6554 | 125.82 | 100%
[5 empty] | 125.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127609.7805 | 2060467.1749 | 125.84 | 100%
[5 empty] | 125.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127632.5418 | 2060834.6945 | 125.86 | 100%
[5 empty] | 125.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127655.3032 | 2061202.214 | 125.88 | 100%
[5 empty] | 125.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127678.0646 | 2061569.7335 | 125.9 | 100%
[5 empty] | 125.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127700.826 | 2061937.253 | 125.92 | 100%
[5 empty] | 125.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127723.5874 | 2062304.7725 | 125.94 | 100%
[5 empty] | 125.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127746.3488 | 2062672.2921 | 125.96 | 100%
[5 empty] | 125.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127769.1101 | 2063039.8116 | 125.98 | 100%
[5 empty] | 126 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127791.8715 | 2063407.3311 | 126 | 100%
[5 empty] | 126.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127814.6329 | 2063774.8506 | 126.02 | 100%
[5 empty] | 126.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127837.3943 | 2064142.3701 | 126.04 | 100%
[5 empty] | 126.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127860.1557 | 2064509.8897 | 126.06 | 100%
[5 empty] | 126.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127882.9171 | 2064877.4092 | 126.08 | 100%
[5 empty] | 126.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127905.6784 | 2065244.9287 | 126.1 | 100%
[5 empty] | 126.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127928.4398 | 2065612.4482 | 126.12 | 100%
[5 empty] | 126.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127951.2012 | 2065979.9677 | 126.14 | 100%
[5 empty] | 126.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127973.9626 | 2066347.4873 | 126.16 | 100%
[5 empty] | 126.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 127996.724 | 2066715.0068 | 126.18 | 100%
[5 empty] | 126.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128019.4854 | 2067082.5263 | 126.2 | 100%
[5 empty] | 126.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128042.2468 | 2067450.0458 | 126.22 | 100%
[5 empty] | 126.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128065.0081 | 2067817.5653 | 126.24 | 100%
[5 empty] | 126.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128087.7695 | 2068185.0849 | 126.26 | 100%
[5 empty] | 126.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128110.5309 | 2068552.6044 | 126.28 | 100%
[5 empty] | 126.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128133.2923 | 2068920.1239 | 126.3 | 100%
[5 empty] | 126.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128156.0537 | 2069287.6434 | 126.32 | 100%
[5 empty] | 126.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128178.8151 | 2069655.1629 | 126.34 | 100%
[5 empty] | 126.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128201.5764 | 2070022.6825 | 126.36 | 100%
[5 empty] | 126.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128224.3378 | 2070390.202 | 126.38 | 100%
[5 empty] | 126.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128247.0992 | 2070757.7215 | 126.4 | 100%
[5 empty] | 126.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128269.8606 | 2071125.241 | 126.42 | 100%
[5 empty] | 126.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128292.622 | 2071492.7605 | 126.44 | 100%
[5 empty] | 126.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128315.3834 | 2071860.2801 | 126.46 | 100%
[5 empty] | 126.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128338.1447 | 2072227.7996 | 126.48 | 100%
[5 empty] | 126.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128360.9061 | 2072595.3191 | 126.5 | 100%
[5 empty] | 126.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128383.6675 | 2072962.8386 | 126.52 | 100%
[5 empty] | 126.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128406.4289 | 2073330.3581 | 126.54 | 100%
[5 empty] | 126.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128429.1903 | 2073697.8777 | 126.56 | 100%
[5 empty] | 126.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128451.9517 | 2074065.3972 | 126.58 | 100%
[5 empty] | 126.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128474.7131 | 2074432.9167 | 126.6 | 100%
[5 empty] | 126.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128497.4744 | 2074800.4362 | 126.62 | 100%
[5 empty] | 126.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128520.2358 | 2075167.9557 | 126.64 | 100%
[5 empty] | 126.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128542.9972 | 2075535.4753 | 126.66 | 100%
[5 empty] | 126.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128565.7586 | 2075902.9948 | 126.68 | 100%
[5 empty] | 126.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128588.52 | 2076270.5143 | 126.7 | 100%
[5 empty] | 126.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128611.2814 | 2076638.0338 | 126.72 | 100%
[5 empty] | 126.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128634.0427 | 2077005.5533 | 126.74 | 100%
[5 empty] | 126.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128656.8041 | 2077373.0729 | 126.76 | 100%
[5 empty] | 126.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128679.5655 | 2077740.5924 | 126.78 | 100%
[5 empty] | 126.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128702.3269 | 2078108.1119 | 126.8 | 100%
[5 empty] | 126.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128725.0883 | 2078475.6314 | 126.82 | 100%
[5 empty] | 126.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128747.8497 | 2078843.1509 | 126.84 | 100%
[5 empty] | 126.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128770.6111 | 2079210.6705 | 126.86 | 100%
[5 empty] | 126.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128793.3724 | 2079578.19 | 126.88 | 100%
[5 empty] | 126.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128816.1338 | 2079945.7095 | 126.9 | 100%
[5 empty] | 126.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128838.8952 | 2080313.229 | 126.92 | 100%
[5 empty] | 126.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128861.6566 | 2080680.7485 | 126.94 | 100%
[5 empty] | 126.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128884.418 | 2081048.2681 | 126.96 | 100%
[5 empty] | 126.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128907.1794 | 2081415.7876 | 126.98 | 100%
[5 empty] | 127 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128929.9407 | 2081783.3071 | 127 | 100%
[5 empty] | 127.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128952.7021 | 2082150.8266 | 127.02 | 100%
[5 empty] | 127.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128975.4635 | 2082518.3461 | 127.04 | 100%
[5 empty] | 127.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 128998.2249 | 2082885.8657 | 127.06 | 100%
[5 empty] | 127.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129020.9863 | 2083253.3852 | 127.08 | 100%
[5 empty] | 127.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129043.7477 | 2083620.9047 | 127.1 | 100%
[5 empty] | 127.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129066.509 | 2083988.4242 | 127.12 | 100%
[5 empty] | 127.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129089.2704 | 2084355.9437 | 127.14 | 100%
[5 empty] | 127.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129112.0318 | 2084723.4633 | 127.16 | 100%
[5 empty] | 127.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129134.7932 | 2085090.9828 | 127.18 | 100%
[5 empty] | 127.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129157.5546 | 2085458.5023 | 127.2 | 100%
[5 empty] | 127.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129180.316 | 2085826.0218 | 127.22 | 100%
[5 empty] | 127.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129203.0774 | 2086193.5413 | 127.24 | 100%
[5 empty] | 127.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129225.8387 | 2086561.0609 | 127.26 | 100%
[5 empty] | 127.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129248.6001 | 2086928.5804 | 127.28 | 100%
[5 empty] | 127.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129271.3615 | 2087296.0999 | 127.3 | 100%
[5 empty] | 127.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129294.1229 | 2087663.6194 | 127.32 | 100%
[5 empty] | 127.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129316.8843 | 2088031.1389 | 127.34 | 100%
[5 empty] | 127.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129339.6457 | 2088398.6585 | 127.36 | 100%
[5 empty] | 127.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129362.407 | 2088766.178 | 127.38 | 100%
[5 empty] | 127.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129385.1684 | 2089133.6975 | 127.4 | 100%
[5 empty] | 127.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129407.9298 | 2089501.217 | 127.42 | 100%
[5 empty] | 127.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129430.6912 | 2089868.7365 | 127.44 | 100%
[5 empty] | 127.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129453.4526 | 2090236.2561 | 127.46 | 100%
[5 empty] | 127.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129476.214 | 2090603.7756 | 127.48 | 100%
[5 empty] | 127.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129498.9753 | 2090971.2951 | 127.5 | 100%
[5 empty] | 127.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129521.7367 | 2091338.8146 | 127.52 | 100%
[5 empty] | 127.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129544.4981 | 2091706.3341 | 127.54 | 100%
[5 empty] | 127.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129567.2595 | 2092073.8537 | 127.56 | 100%
[5 empty] | 127.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129590.0209 | 2092441.3732 | 127.58 | 100%
[5 empty] | 127.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129612.7823 | 2092808.8927 | 127.6 | 100%
[5 empty] | 127.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129635.5437 | 2093176.4122 | 127.62 | 100%
[5 empty] | 127.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129658.305 | 2093543.9317 | 127.64 | 100%
[5 empty] | 127.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129681.0664 | 2093911.4513 | 127.66 | 100%
[5 empty] | 127.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129703.8278 | 2094278.9708 | 127.68 | 100%
[5 empty] | 127.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129726.5892 | 2094646.4903 | 127.7 | 100%
[5 empty] | 127.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129749.3506 | 2095014.0098 | 127.72 | 100%
[5 empty] | 127.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129772.112 | 2095381.5293 | 127.74 | 100%
[5 empty] | 127.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129794.8733 | 2095749.0489 | 127.76 | 100%
[5 empty] | 127.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129817.6347 | 2096116.5684 | 127.78 | 100%
[5 empty] | 127.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129840.3961 | 2096484.0879 | 127.8 | 100%
[5 empty] | 127.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129863.1575 | 2096851.6074 | 127.82 | 100%
[5 empty] | 127.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129885.9189 | 2097219.1269 | 127.84 | 100%
[5 empty] | 127.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129908.6803 | 2097586.6465 | 127.86 | 100%
[5 empty] | 127.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129931.4417 | 2097954.166 | 127.88 | 100%
[5 empty] | 127.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129954.203 | 2098321.6855 | 127.9 | 100%
[5 empty] | 127.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129976.9644 | 2098689.205 | 127.92 | 100%
[5 empty] | 127.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 129999.7258 | 2099056.7245 | 127.94 | 100%
[5 empty] | 127.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130022.4872 | 2099424.2441 | 127.96 | 100%
[5 empty] | 127.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130045.2486 | 2099791.7636 | 127.98 | 100%
[5 empty] | 128 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130068.01 | 2100159.2831 | 128 | 100%
[5 empty] | 128.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130090.7713 | 2100526.8026 | 128.02 | 100%
[5 empty] | 128.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130113.5327 | 2100894.3221 | 128.04 | 100%
[5 empty] | 128.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130136.2941 | 2101261.8417 | 128.06 | 100%
[5 empty] | 128.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130159.0555 | 2101629.3612 | 128.08 | 100%
[5 empty] | 128.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130181.8169 | 2101996.8807 | 128.1 | 100%
[5 empty] | 128.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130204.5783 | 2102364.4002 | 128.12 | 100%
[5 empty] | 128.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130227.3396 | 2102731.9197 | 128.14 | 100%
[5 empty] | 128.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130250.101 | 2103099.4393 | 128.16 | 100%
[5 empty] | 128.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130272.8624 | 2103466.9588 | 128.18 | 100%
[5 empty] | 128.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130295.6238 | 2103834.4783 | 128.2 | 100%
[5 empty] | 128.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130318.3852 | 2104201.9978 | 128.22 | 100%
[5 empty] | 128.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130341.1466 | 2104569.5173 | 128.24 | 100%
[5 empty] | 128.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130363.908 | 2104937.0369 | 128.26 | 100%
[5 empty] | 128.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130386.6693 | 2105304.5564 | 128.28 | 100%
[5 empty] | 128.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130409.4307 | 2105672.0759 | 128.3 | 100%
[5 empty] | 128.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130432.1921 | 2106039.5954 | 128.32 | 100%
[5 empty] | 128.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130454.9535 | 2106407.1149 | 128.34 | 100%
[5 empty] | 128.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130477.7149 | 2106774.6345 | 128.36 | 100%
[5 empty] | 128.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130500.4763 | 2107142.154 | 128.38 | 100%
[5 empty] | 128.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130523.2376 | 2107509.6735 | 128.4 | 100%
[5 empty] | 128.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130545.999 | 2107877.193 | 128.42 | 100%
[5 empty] | 128.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130568.7604 | 2108244.7125 | 128.44 | 100%
[5 empty] | 128.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130591.5218 | 2108612.2321 | 128.46 | 100%
[5 empty] | 128.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130614.2832 | 2108979.7516 | 128.48 | 100%
[5 empty] | 128.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130637.0446 | 2109347.2711 | 128.5 | 100%
[5 empty] | 128.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130659.8059 | 2109714.7906 | 128.52 | 100%
[5 empty] | 128.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130682.5673 | 2110082.3101 | 128.54 | 100%
[5 empty] | 128.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130705.3287 | 2110449.8297 | 128.56 | 100%
[5 empty] | 128.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130728.0901 | 2110817.3492 | 128.58 | 100%
[5 empty] | 128.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130750.8515 | 2111184.8687 | 128.6 | 100%
[5 empty] | 128.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130773.6129 | 2111552.3882 | 128.62 | 100%
[5 empty] | 128.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130796.3743 | 2111919.9077 | 128.64 | 100%
[5 empty] | 128.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130819.1356 | 2112287.4273 | 128.66 | 100%
[5 empty] | 128.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130841.897 | 2112654.9468 | 128.68 | 100%
[5 empty] | 128.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130864.6584 | 2113022.4663 | 128.7 | 100%
[5 empty] | 128.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130887.4198 | 2113389.9858 | 128.72 | 100%
[5 empty] | 128.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130910.1812 | 2113757.5053 | 128.74 | 100%
[5 empty] | 128.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130932.9426 | 2114125.0249 | 128.76 | 100%
[5 empty] | 128.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130955.7039 | 2114492.5444 | 128.78 | 100%
[5 empty] | 128.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 130978.4653 | 2114860.0639 | 128.8 | 100%
[5 empty] | 128.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131001.2267 | 2115227.5834 | 128.82 | 100%
[5 empty] | 128.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131023.9881 | 2115595.1029 | 128.84 | 100%
[5 empty] | 128.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131046.7495 | 2115962.6225 | 128.86 | 100%
[5 empty] | 128.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131069.5109 | 2116330.142 | 128.88 | 100%
[5 empty] | 128.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131092.2723 | 2116697.6615 | 128.9 | 100%
[5 empty] | 128.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131115.0336 | 2117065.181 | 128.92 | 100%
[5 empty] | 128.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131137.795 | 2117432.7005 | 128.94 | 100%
[5 empty] | 128.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131160.5564 | 2117800.2201 | 128.96 | 100%
[5 empty] | 128.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131183.3178 | 2118167.7396 | 128.98 | 100%
[5 empty] | 129 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131206.0792 | 2118535.2591 | 129 | 100%
[5 empty] | 129.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131228.8406 | 2118902.7786 | 129.02 | 100%
[5 empty] | 129.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131251.6019 | 2119270.2981 | 129.04 | 100%
[5 empty] | 129.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131274.3633 | 2119637.8177 | 129.06 | 100%
[5 empty] | 129.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131297.1247 | 2120005.3372 | 129.08 | 100%
[5 empty] | 129.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131319.8861 | 2120372.8567 | 129.1 | 100%
[5 empty] | 129.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131342.6475 | 2120740.3762 | 129.12 | 100%
[5 empty] | 129.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131365.4089 | 2121107.8957 | 129.14 | 100%
[5 empty] | 129.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131388.1702 | 2121475.4153 | 129.16 | 100%
[5 empty] | 129.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131410.9316 | 2121842.9348 | 129.18 | 100%
[5 empty] | 129.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131433.693 | 2122210.4543 | 129.2 | 100%
[5 empty] | 129.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131456.4544 | 2122577.9738 | 129.22 | 100%
[5 empty] | 129.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131479.2158 | 2122945.4933 | 129.24 | 100%
[5 empty] | 129.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131501.9772 | 2123313.0129 | 129.26 | 100%
[5 empty] | 129.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131524.7386 | 2123680.5324 | 129.28 | 100%
[5 empty] | 129.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131547.4999 | 2124048.0519 | 129.3 | 100%
[5 empty] | 129.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131570.2613 | 2124415.5714 | 129.32 | 100%
[5 empty] | 129.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131593.0227 | 2124783.0909 | 129.34 | 100%
[5 empty] | 129.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131615.7841 | 2125150.6105 | 129.36 | 100%
[5 empty] | 129.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131638.5455 | 2125518.13 | 129.38 | 100%
[5 empty] | 129.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131661.3069 | 2125885.6495 | 129.4 | 100%
[5 empty] | 129.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131684.0682 | 2126253.169 | 129.42 | 100%
[5 empty] | 129.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131706.8296 | 2126620.6885 | 129.44 | 100%
[5 empty] | 129.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131729.591 | 2126988.2081 | 129.46 | 100%
[5 empty] | 129.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131752.3524 | 2127355.7276 | 129.48 | 100%
[5 empty] | 129.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131775.1138 | 2127723.2471 | 129.5 | 100%
[5 empty] | 129.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131797.8752 | 2128090.7666 | 129.52 | 100%
[5 empty] | 129.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131820.6366 | 2128458.2861 | 129.54 | 100%
[5 empty] | 129.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131843.3979 | 2128825.8057 | 129.56 | 100%
[5 empty] | 129.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131866.1593 | 2129193.3252 | 129.58 | 100%
[5 empty] | 129.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131888.9207 | 2129560.8447 | 129.6 | 100%
[5 empty] | 129.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131911.6821 | 2129928.3642 | 129.62 | 100%
[5 empty] | 129.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131934.4435 | 2130295.8837 | 129.64 | 100%
[5 empty] | 129.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131957.2049 | 2130663.4033 | 129.66 | 100%
[5 empty] | 129.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 131979.9662 | 2131030.9228 | 129.68 | 100%
[5 empty] | 129.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132002.7276 | 2131398.4423 | 129.7 | 100%
[5 empty] | 129.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132025.489 | 2131765.9618 | 129.72 | 100%
[5 empty] | 129.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132048.2504 | 2132133.4813 | 129.74 | 100%
[5 empty] | 129.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132071.0118 | 2132501.0009 | 129.76 | 100%
[5 empty] | 129.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132093.7732 | 2132868.5204 | 129.78 | 100%
[5 empty] | 129.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132116.5345 | 2133236.0399 | 129.8 | 100%
[5 empty] | 129.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132139.2959 | 2133603.5594 | 129.82 | 100%
[5 empty] | 129.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132162.0573 | 2133971.0789 | 129.84 | 100%
[5 empty] | 129.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132184.8187 | 2134338.5985 | 129.86 | 100%
[5 empty] | 129.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132207.5801 | 2134706.118 | 129.88 | 100%
[5 empty] | 129.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132230.3415 | 2135073.6375 | 129.9 | 100%
[5 empty] | 129.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132253.1029 | 2135441.157 | 129.92 | 100%
[5 empty] | 129.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132275.8642 | 2135808.6765 | 129.94 | 100%
[5 empty] | 129.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132298.6256 | 2136176.1961 | 129.96 | 100%
[5 empty] | 129.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132321.387 | 2136543.7156 | 129.98 | 100%
[5 empty] | 130 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132344.1484 | 2136911.2351 | 130 | 100%
[5 empty] | 130.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132366.9098 | 2137278.7546 | 130.02 | 100%
[5 empty] | 130.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132389.6712 | 2137646.2741 | 130.04 | 100%
[5 empty] | 130.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132412.4325 | 2138013.7937 | 130.06 | 100%
[5 empty] | 130.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132435.1939 | 2138381.3132 | 130.08 | 100%
[5 empty] | 130.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132457.9553 | 2138748.8327 | 130.1 | 100%
[5 empty] | 130.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132480.7167 | 2139116.3522 | 130.12 | 100%
[5 empty] | 130.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132503.4781 | 2139483.8717 | 130.14 | 100%
[5 empty] | 130.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132526.2395 | 2139851.3913 | 130.16 | 100%
[5 empty] | 130.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132549.0008 | 2140218.9108 | 130.18 | 100%
[5 empty] | 130.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132571.7622 | 2140586.4303 | 130.2 | 100%
[5 empty] | 130.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132594.5236 | 2140953.9498 | 130.22 | 100%
[5 empty] | 130.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132617.285 | 2141321.4693 | 130.24 | 100%
[5 empty] | 130.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132640.0464 | 2141688.9889 | 130.26 | 100%
[5 empty] | 130.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132662.8078 | 2142056.5084 | 130.28 | 100%
[5 empty] | 130.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132685.5692 | 2142424.0279 | 130.3 | 100%
[5 empty] | 130.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132708.3305 | 2142791.5474 | 130.32 | 100%
[5 empty] | 130.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132731.0919 | 2143159.0669 | 130.34 | 100%
[5 empty] | 130.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132753.8533 | 2143526.5865 | 130.36 | 100%
[5 empty] | 130.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132776.6147 | 2143894.106 | 130.38 | 100%
[5 empty] | 130.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132799.3761 | 2144261.6255 | 130.4 | 100%
[5 empty] | 130.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132822.1375 | 2144629.145 | 130.42 | 100%
[5 empty] | 130.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132844.8988 | 2144996.6645 | 130.44 | 100%
[5 empty] | 130.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132867.6602 | 2145364.1841 | 130.46 | 100%
[5 empty] | 130.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132890.4216 | 2145731.7036 | 130.48 | 100%
[5 empty] | 130.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132913.183 | 2146099.2231 | 130.5 | 100%
[5 empty] | 130.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132935.9444 | 2146466.7426 | 130.52 | 100%
[5 empty] | 130.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132958.7058 | 2146834.2621 | 130.54 | 100%
[5 empty] | 130.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 132981.4672 | 2147201.7817 | 130.56 | 100%
[5 empty] | 130.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133004.2285 | 2147569.3012 | 130.58 | 100%
[5 empty] | 130.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133026.9899 | 2147936.8207 | 130.6 | 100%
[5 empty] | 130.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133049.7513 | 2148304.3402 | 130.62 | 100%
[5 empty] | 130.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133072.5127 | 2148671.8597 | 130.64 | 100%
[5 empty] | 130.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133095.2741 | 2149039.3793 | 130.66 | 100%
[5 empty] | 130.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133118.0355 | 2149406.8988 | 130.68 | 100%
[5 empty] | 130.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133140.7968 | 2149774.4183 | 130.7 | 100%
[5 empty] | 130.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133163.5582 | 2150141.9378 | 130.72 | 100%
[5 empty] | 130.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133186.3196 | 2150509.4573 | 130.74 | 100%
[5 empty] | 130.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133209.081 | 2150876.9769 | 130.76 | 100%
[5 empty] | 130.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133231.8424 | 2151244.4964 | 130.78 | 100%
[5 empty] | 130.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133254.6038 | 2151612.0159 | 130.8 | 100%
[5 empty] | 130.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133277.3651 | 2151979.5354 | 130.82 | 100%
[5 empty] | 130.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133300.1265 | 2152347.0549 | 130.84 | 100%
[5 empty] | 130.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133322.8879 | 2152714.5745 | 130.86 | 100%
[5 empty] | 130.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133345.6493 | 2153082.094 | 130.88 | 100%
[5 empty] | 130.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133368.4107 | 2153449.6135 | 130.9 | 100%
[5 empty] | 130.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133391.1721 | 2153817.133 | 130.92 | 100%
[5 empty] | 130.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133413.9335 | 2154184.6525 | 130.94 | 100%
[5 empty] | 130.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133436.6948 | 2154552.1721 | 130.96 | 100%
[5 empty] | 130.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133459.4562 | 2154919.6916 | 130.98 | 100%
[5 empty] | 131 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133482.2176 | 2155287.2111 | 131 | 100%
[5 empty] | 131.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133504.979 | 2155654.7306 | 131.02 | 100%
[5 empty] | 131.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133527.7404 | 2156022.2501 | 131.04 | 100%
[5 empty] | 131.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133550.5018 | 2156389.7697 | 131.06 | 100%
[5 empty] | 131.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133573.2631 | 2156757.2892 | 131.08 | 100%
[5 empty] | 131.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133596.0245 | 2157124.8087 | 131.1 | 100%
[5 empty] | 131.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133618.7859 | 2157492.3282 | 131.12 | 100%
[5 empty] | 131.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133641.5473 | 2157859.8477 | 131.14 | 100%
[5 empty] | 131.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133664.3087 | 2158227.3673 | 131.16 | 100%
[5 empty] | 131.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133687.0701 | 2158594.8868 | 131.18 | 100%
[5 empty] | 131.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133709.8314 | 2158962.4063 | 131.2 | 100%
[5 empty] | 131.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133732.5928 | 2159329.9258 | 131.22 | 100%
[5 empty] | 131.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133755.3542 | 2159697.4453 | 131.24 | 100%
[5 empty] | 131.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133778.1156 | 2160064.9649 | 131.26 | 100%
[5 empty] | 131.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133800.877 | 2160432.4844 | 131.28 | 100%
[5 empty] | 131.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133823.6384 | 2160800.0039 | 131.3 | 100%
[5 empty] | 131.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133846.3998 | 2161167.5234 | 131.32 | 100%
[5 empty] | 131.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133869.1611 | 2161535.0429 | 131.34 | 100%
[5 empty] | 131.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133891.9225 | 2161902.5625 | 131.36 | 100%
[5 empty] | 131.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133914.6839 | 2162270.082 | 131.38 | 100%
[5 empty] | 131.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133937.4453 | 2162637.6015 | 131.4 | 100%
[5 empty] | 131.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133960.2067 | 2163005.121 | 131.42 | 100%
[5 empty] | 131.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 133982.9681 | 2163372.6405 | 131.44 | 100%
[5 empty] | 131.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134005.7294 | 2163740.1601 | 131.46 | 100%
[5 empty] | 131.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134028.4908 | 2164107.6796 | 131.48 | 100%
[5 empty] | 131.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134051.2522 | 2164475.1991 | 131.5 | 100%
[5 empty] | 131.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134074.0136 | 2164842.7186 | 131.52 | 100%
[5 empty] | 131.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134096.775 | 2165210.2381 | 131.54 | 100%
[5 empty] | 131.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134119.5364 | 2165577.7577 | 131.56 | 100%
[5 empty] | 131.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134142.2978 | 2165945.2772 | 131.58 | 100%
[5 empty] | 131.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134165.0591 | 2166312.7967 | 131.6 | 100%
[5 empty] | 131.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134187.8205 | 2166680.3162 | 131.62 | 100%
[5 empty] | 131.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134210.5819 | 2167047.8357 | 131.64 | 100%
[5 empty] | 131.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134233.3433 | 2167415.3553 | 131.66 | 100%
[5 empty] | 131.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134256.1047 | 2167782.8748 | 131.68 | 100%
[5 empty] | 131.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134278.8661 | 2168150.3943 | 131.7 | 100%
[5 empty] | 131.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134301.6274 | 2168517.9138 | 131.72 | 100%
[5 empty] | 131.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134324.3888 | 2168885.4333 | 131.74 | 100%
[5 empty] | 131.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134347.1502 | 2169252.9529 | 131.76 | 100%
[5 empty] | 131.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134369.9116 | 2169620.4724 | 131.78 | 100%
[5 empty] | 131.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134392.673 | 2169987.9919 | 131.8 | 100%
[5 empty] | 131.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134415.4344 | 2170355.5114 | 131.82 | 100%
[5 empty] | 131.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134438.1957 | 2170723.0309 | 131.84 | 100%
[5 empty] | 131.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134460.9571 | 2171090.5505 | 131.86 | 100%
[5 empty] | 131.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134483.7185 | 2171458.07 | 131.88 | 100%
[5 empty] | 131.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134506.4799 | 2171825.5895 | 131.9 | 100%
[5 empty] | 131.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134529.2413 | 2172193.109 | 131.92 | 100%
[5 empty] | 131.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134552.0027 | 2172560.6285 | 131.94 | 100%
[5 empty] | 131.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134574.7641 | 2172928.1481 | 131.96 | 100%
[5 empty] | 131.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134597.5254 | 2173295.6676 | 131.98 | 100%
[5 empty] | 132 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134620.2868 | 2173663.1871 | 132 | 100%
[5 empty] | 132.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134643.0482 | 2174030.7066 | 132.02 | 100%
[5 empty] | 132.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134665.8096 | 2174398.2261 | 132.04 | 100%
[5 empty] | 132.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134688.571 | 2174765.7457 | 132.06 | 100%
[5 empty] | 132.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134711.3324 | 2175133.2652 | 132.08 | 100%
[5 empty] | 132.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134734.0937 | 2175500.7847 | 132.1 | 100%
[5 empty] | 132.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134756.8551 | 2175868.3042 | 132.12 | 100%
[5 empty] | 132.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134779.6165 | 2176235.8237 | 132.14 | 100%
[5 empty] | 132.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134802.3779 | 2176603.3433 | 132.16 | 100%
[5 empty] | 132.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134825.1393 | 2176970.8628 | 132.18 | 100%
[5 empty] | 132.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134847.9007 | 2177338.3823 | 132.2 | 100%
[5 empty] | 132.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134870.6621 | 2177705.9018 | 132.22 | 100%
[5 empty] | 132.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134893.4234 | 2178073.4213 | 132.24 | 100%
[5 empty] | 132.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134916.1848 | 2178440.9409 | 132.26 | 100%
[5 empty] | 132.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134938.9462 | 2178808.4604 | 132.28 | 100%
[5 empty] | 132.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134961.7076 | 2179175.9799 | 132.3 | 100%
[5 empty] | 132.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 134984.469 | 2179543.4994 | 132.32 | 100%
[5 empty] | 132.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135007.2304 | 2179911.0189 | 132.34 | 100%
[5 empty] | 132.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135029.9917 | 2180278.5385 | 132.36 | 100%
[5 empty] | 132.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135052.7531 | 2180646.058 | 132.38 | 100%
[5 empty] | 132.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135075.5145 | 2181013.5775 | 132.4 | 100%
[5 empty] | 132.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135098.2759 | 2181381.097 | 132.42 | 100%
[5 empty] | 132.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135121.0373 | 2181748.6165 | 132.44 | 100%
[5 empty] | 132.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135143.7987 | 2182116.1361 | 132.46 | 100%
[5 empty] | 132.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135166.56 | 2182483.6556 | 132.48 | 100%
[5 empty] | 132.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135189.3214 | 2182851.1751 | 132.5 | 100%
[5 empty] | 132.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135212.0828 | 2183218.6946 | 132.52 | 100%
[5 empty] | 132.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135234.8442 | 2183586.2141 | 132.54 | 100%
[5 empty] | 132.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135257.6056 | 2183953.7337 | 132.56 | 100%
[5 empty] | 132.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135280.367 | 2184321.2532 | 132.58 | 100%
[5 empty] | 132.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135303.1284 | 2184688.7727 | 132.6 | 100%
[5 empty] | 132.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135325.8897 | 2185056.2922 | 132.62 | 100%
[5 empty] | 132.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135348.6511 | 2185423.8117 | 132.64 | 100%
[5 empty] | 132.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135371.4125 | 2185791.3313 | 132.66 | 100%
[5 empty] | 132.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135394.1739 | 2186158.8508 | 132.68 | 100%
[5 empty] | 132.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135416.9353 | 2186526.3703 | 132.7 | 100%
[5 empty] | 132.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135439.6967 | 2186893.8898 | 132.72 | 100%
[5 empty] | 132.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135462.458 | 2187261.4093 | 132.74 | 100%
[5 empty] | 132.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135485.2194 | 2187628.9289 | 132.76 | 100%
[5 empty] | 132.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135507.9808 | 2187996.4484 | 132.78 | 100%
[5 empty] | 132.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135530.7422 | 2188363.9679 | 132.8 | 100%
[5 empty] | 132.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135553.5036 | 2188731.4874 | 132.82 | 100%
[5 empty] | 132.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135576.265 | 2189099.0069 | 132.84 | 100%
[5 empty] | 132.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135599.0263 | 2189466.5265 | 132.86 | 100%
[5 empty] | 132.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135621.7877 | 2189834.046 | 132.88 | 100%
[5 empty] | 132.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135644.5491 | 2190201.5655 | 132.9 | 100%
[5 empty] | 132.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135667.3105 | 2190569.085 | 132.92 | 100%
[5 empty] | 132.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135690.0719 | 2190936.6045 | 132.94 | 100%
[5 empty] | 132.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135712.8333 | 2191304.1241 | 132.96 | 100%
[5 empty] | 132.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135735.5947 | 2191671.6436 | 132.98 | 100%
[5 empty] | 133 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135758.356 | 2192039.1631 | 133 | 100%
[5 empty] | 133.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135781.1174 | 2192406.6826 | 133.02 | 100%
[5 empty] | 133.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135803.8788 | 2192774.2021 | 133.04 | 100%
[5 empty] | 133.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135826.6402 | 2193141.7217 | 133.06 | 100%
[5 empty] | 133.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135849.4016 | 2193509.2412 | 133.08 | 100%
[5 empty] | 133.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135872.163 | 2193876.7607 | 133.1 | 100%
[5 empty] | 133.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135894.9243 | 2194244.2802 | 133.12 | 100%
[5 empty] | 133.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135917.6857 | 2194611.7997 | 133.14 | 100%
[5 empty] | 133.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135940.4471 | 2194979.3193 | 133.16 | 100%
[5 empty] | 133.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135963.2085 | 2195346.8388 | 133.18 | 100%
[5 empty] | 133.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 135985.9699 | 2195714.3583 | 133.2 | 100%
[5 empty] | 133.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136008.7313 | 2196081.8778 | 133.22 | 100%
[5 empty] | 133.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136031.4927 | 2196449.3973 | 133.24 | 100%
[5 empty] | 133.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136054.254 | 2196816.9169 | 133.26 | 100%
[5 empty] | 133.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136077.0154 | 2197184.4364 | 133.28 | 100%
[5 empty] | 133.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136099.7768 | 2197551.9559 | 133.3 | 100%
[5 empty] | 133.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136122.5382 | 2197919.4754 | 133.32 | 100%
[5 empty] | 133.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136145.2996 | 2198286.9949 | 133.34 | 100%
[5 empty] | 133.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136168.061 | 2198654.5145 | 133.36 | 100%
[5 empty] | 133.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136190.8223 | 2199022.034 | 133.38 | 100%
[5 empty] | 133.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136213.5837 | 2199389.5535 | 133.4 | 100%
[5 empty] | 133.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136236.3451 | 2199757.073 | 133.42 | 100%
[5 empty] | 133.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136259.1065 | 2200124.5925 | 133.44 | 100%
[5 empty] | 133.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136281.8679 | 2200492.1121 | 133.46 | 100%
[5 empty] | 133.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136304.6293 | 2200859.6316 | 133.48 | 100%
[5 empty] | 133.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136327.3906 | 2201227.1511 | 133.5 | 100%
[5 empty] | 133.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136350.152 | 2201594.6706 | 133.52 | 100%
[5 empty] | 133.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136372.9134 | 2201962.1901 | 133.54 | 100%
[5 empty] | 133.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136395.6748 | 2202329.7097 | 133.56 | 100%
[5 empty] | 133.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136418.4362 | 2202697.2292 | 133.58 | 100%
[5 empty] | 133.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136441.1976 | 2203064.7487 | 133.6 | 100%
[5 empty] | 133.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136463.959 | 2203432.2682 | 133.62 | 100%
[5 empty] | 133.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136486.7203 | 2203799.7877 | 133.64 | 100%
[5 empty] | 133.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136509.4817 | 2204167.3073 | 133.66 | 100%
[5 empty] | 133.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136532.2431 | 2204534.8268 | 133.68 | 100%
[5 empty] | 133.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136555.0045 | 2204902.3463 | 133.7 | 100%
[5 empty] | 133.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136577.7659 | 2205269.8658 | 133.72 | 100%
[5 empty] | 133.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136600.5273 | 2205637.3853 | 133.74 | 100%
[5 empty] | 133.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136623.2886 | 2206004.9049 | 133.76 | 100%
[5 empty] | 133.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136646.05 | 2206372.4244 | 133.78 | 100%
[5 empty] | 133.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136668.8114 | 2206739.9439 | 133.8 | 100%
[5 empty] | 133.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136691.5728 | 2207107.4634 | 133.82 | 100%
[5 empty] | 133.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136714.3342 | 2207474.9829 | 133.84 | 100%
[5 empty] | 133.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136737.0956 | 2207842.5025 | 133.86 | 100%
[5 empty] | 133.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136759.8569 | 2208210.022 | 133.88 | 100%
[5 empty] | 133.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136782.6183 | 2208577.5415 | 133.9 | 100%
[5 empty] | 133.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136805.3797 | 2208945.061 | 133.92 | 100%
[5 empty] | 133.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136828.1411 | 2209312.5805 | 133.94 | 100%
[5 empty] | 133.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136850.9025 | 2209680.1001 | 133.96 | 100%
[5 empty] | 133.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136873.6639 | 2210047.6196 | 133.98 | 100%
[5 empty] | 134 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136896.4253 | 2210415.1391 | 134 | 100%
[5 empty] | 134.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136919.1866 | 2210782.6586 | 134.02 | 100%
[5 empty] | 134.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136941.948 | 2211150.1781 | 134.04 | 100%
[5 empty] | 134.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136964.7094 | 2211517.6977 | 134.06 | 100%
[5 empty] | 134.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 136987.4708 | 2211885.2172 | 134.08 | 100%
[5 empty] | 134.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137010.2322 | 2212252.7367 | 134.1 | 100%
[5 empty] | 134.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137032.9936 | 2212620.2562 | 134.12 | 100%
[5 empty] | 134.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137055.7549 | 2212987.7757 | 134.14 | 100%
[5 empty] | 134.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137078.5163 | 2213355.2953 | 134.16 | 100%
[5 empty] | 134.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137101.2777 | 2213722.8148 | 134.18 | 100%
[5 empty] | 134.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137124.0391 | 2214090.3343 | 134.2 | 100%
[5 empty] | 134.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137146.8005 | 2214457.8538 | 134.22 | 100%
[5 empty] | 134.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137169.5619 | 2214825.3733 | 134.24 | 100%
[5 empty] | 134.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137192.3233 | 2215192.8929 | 134.26 | 100%
[5 empty] | 134.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137215.0846 | 2215560.4124 | 134.28 | 100%
[5 empty] | 134.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137237.846 | 2215927.9319 | 134.3 | 100%
[5 empty] | 134.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137260.6074 | 2216295.4514 | 134.32 | 100%
[5 empty] | 134.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137283.3688 | 2216662.9709 | 134.34 | 100%
[5 empty] | 134.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137306.1302 | 2217030.4905 | 134.36 | 100%
[5 empty] | 134.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137328.8916 | 2217398.01 | 134.38 | 100%
[5 empty] | 134.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137351.6529 | 2217765.5295 | 134.4 | 100%
[5 empty] | 134.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137374.4143 | 2218133.049 | 134.42 | 100%
[5 empty] | 134.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137397.1757 | 2218500.5685 | 134.44 | 100%
[5 empty] | 134.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137419.9371 | 2218868.0881 | 134.46 | 100%
[5 empty] | 134.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137442.6985 | 2219235.6076 | 134.48 | 100%
[5 empty] | 134.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137465.4599 | 2219603.1271 | 134.5 | 100%
[5 empty] | 134.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137488.2212 | 2219970.6466 | 134.52 | 100%
[5 empty] | 134.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137510.9826 | 2220338.1661 | 134.54 | 100%
[5 empty] | 134.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137533.744 | 2220705.6857 | 134.56 | 100%
[5 empty] | 134.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137556.5054 | 2221073.2052 | 134.58 | 100%
[5 empty] | 134.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137579.2668 | 2221440.7247 | 134.6 | 100%
[5 empty] | 134.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137602.0282 | 2221808.2442 | 134.62 | 100%
[5 empty] | 134.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137624.7896 | 2222175.7637 | 134.64 | 100%
[5 empty] | 134.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137647.5509 | 2222543.2833 | 134.66 | 100%
[5 empty] | 134.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137670.3123 | 2222910.8028 | 134.68 | 100%
[5 empty] | 134.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137693.0737 | 2223278.3223 | 134.7 | 100%
[5 empty] | 134.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137715.8351 | 2223645.8418 | 134.72 | 100%
[5 empty] | 134.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137738.5965 | 2224013.3613 | 134.74 | 100%
[5 empty] | 134.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137761.3579 | 2224380.8809 | 134.76 | 100%
[5 empty] | 134.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137784.1192 | 2224748.4004 | 134.78 | 100%
[5 empty] | 134.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137806.8806 | 2225115.9199 | 134.8 | 100%
[5 empty] | 134.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137829.642 | 2225483.4394 | 134.82 | 100%
[5 empty] | 134.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137852.4034 | 2225850.9589 | 134.84 | 100%
[5 empty] | 134.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137875.1648 | 2226218.4785 | 134.86 | 100%
[5 empty] | 134.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137897.9262 | 2226585.998 | 134.88 | 100%
[5 empty] | 134.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137920.6875 | 2226953.5175 | 134.9 | 100%
[5 empty] | 134.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137943.4489 | 2227321.037 | 134.92 | 100%
[5 empty] | 134.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137966.2103 | 2227688.5565 | 134.94 | 100%
[5 empty] | 134.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 137988.9717 | 2228056.0761 | 134.96 | 100%
[5 empty] | 134.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138011.7331 | 2228423.5956 | 134.98 | 100%
[5 empty] | 135 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138034.4945 | 2228791.1151 | 135 | 100%
[5 empty] | 135.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138057.2559 | 2229158.6346 | 135.02 | 100%
[5 empty] | 135.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138080.0172 | 2229526.1541 | 135.04 | 100%
[5 empty] | 135.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138102.7786 | 2229893.6737 | 135.06 | 100%
[5 empty] | 135.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138125.54 | 2230261.1932 | 135.08 | 100%
[5 empty] | 135.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138148.3014 | 2230628.7127 | 135.1 | 100%
[5 empty] | 135.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138171.0628 | 2230996.2322 | 135.12 | 100%
[5 empty] | 135.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138193.8242 | 2231363.7517 | 135.14 | 100%
[5 empty] | 135.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138216.5855 | 2231731.2713 | 135.16 | 100%
[5 empty] | 135.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138239.3469 | 2232098.7908 | 135.18 | 100%
[5 empty] | 135.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138262.1083 | 2232466.3103 | 135.2 | 100%
[5 empty] | 135.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138284.8697 | 2232833.8298 | 135.22 | 100%
[5 empty] | 135.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138307.6311 | 2233201.3493 | 135.24 | 100%
[5 empty] | 135.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138330.3925 | 2233568.8689 | 135.26 | 100%
[5 empty] | 135.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138353.1539 | 2233936.3884 | 135.28 | 100%
[5 empty] | 135.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138375.9152 | 2234303.9079 | 135.3 | 100%
[5 empty] | 135.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138398.6766 | 2234671.4274 | 135.32 | 100%
[5 empty] | 135.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138421.438 | 2235038.9469 | 135.34 | 100%
[5 empty] | 135.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138444.1994 | 2235406.4665 | 135.36 | 100%
[5 empty] | 135.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138466.9608 | 2235773.986 | 135.38 | 100%
[5 empty] | 135.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138489.7222 | 2236141.5055 | 135.4 | 100%
[5 empty] | 135.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138512.4835 | 2236509.025 | 135.42 | 100%
[5 empty] | 135.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138535.2449 | 2236876.5445 | 135.44 | 100%
[5 empty] | 135.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138558.0063 | 2237244.0641 | 135.46 | 100%
[5 empty] | 135.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138580.7677 | 2237611.5836 | 135.48 | 100%
[5 empty] | 135.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138603.5291 | 2237979.1031 | 135.5 | 100%
[5 empty] | 135.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138626.2905 | 2238346.6226 | 135.52 | 100%
[5 empty] | 135.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138649.0518 | 2238714.1421 | 135.54 | 100%
[5 empty] | 135.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138671.8132 | 2239081.6617 | 135.56 | 100%
[5 empty] | 135.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138694.5746 | 2239449.1812 | 135.58 | 100%
[5 empty] | 135.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138717.336 | 2239816.7007 | 135.6 | 100%
[5 empty] | 135.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138740.0974 | 2240184.2202 | 135.62 | 100%
[5 empty] | 135.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138762.8588 | 2240551.7397 | 135.64 | 100%
[5 empty] | 135.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138785.6202 | 2240919.2593 | 135.66 | 100%
[5 empty] | 135.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138808.3815 | 2241286.7788 | 135.68 | 100%
[5 empty] | 135.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138831.1429 | 2241654.2983 | 135.7 | 100%
[5 empty] | 135.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138853.9043 | 2242021.8178 | 135.72 | 100%
[5 empty] | 135.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138876.6657 | 2242389.3373 | 135.74 | 100%
[5 empty] | 135.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138899.4271 | 2242756.8569 | 135.76 | 100%
[5 empty] | 135.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138922.1885 | 2243124.3764 | 135.78 | 100%
[5 empty] | 135.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138944.9498 | 2243491.8959 | 135.8 | 100%
[5 empty] | 135.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138967.7112 | 2243859.4154 | 135.82 | 100%
[5 empty] | 135.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 138990.4726 | 2244226.9349 | 135.84 | 100%
[5 empty] | 135.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139013.234 | 2244594.4545 | 135.86 | 100%
[5 empty] | 135.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139035.9954 | 2244961.974 | 135.88 | 100%
[5 empty] | 135.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139058.7568 | 2245329.4935 | 135.9 | 100%
[5 empty] | 135.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139081.5182 | 2245697.013 | 135.92 | 100%
[5 empty] | 135.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139104.2795 | 2246064.5325 | 135.94 | 100%
[5 empty] | 135.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139127.0409 | 2246432.0521 | 135.96 | 100%
[5 empty] | 135.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139149.8023 | 2246799.5716 | 135.98 | 100%
[5 empty] | 136 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139172.5637 | 2247167.0911 | 136 | 100%
[5 empty] | 136.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139195.3251 | 2247534.6106 | 136.02 | 100%
[5 empty] | 136.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139218.0865 | 2247902.1301 | 136.04 | 100%
[5 empty] | 136.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139240.8478 | 2248269.6497 | 136.06 | 100%
[5 empty] | 136.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139263.6092 | 2248637.1692 | 136.08 | 100%
[5 empty] | 136.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139286.3706 | 2249004.6887 | 136.1 | 100%
[5 empty] | 136.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139309.132 | 2249372.2082 | 136.12 | 100%
[5 empty] | 136.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139331.8934 | 2249739.7277 | 136.14 | 100%
[5 empty] | 136.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139354.6548 | 2250107.2473 | 136.16 | 100%
[5 empty] | 136.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139377.4161 | 2250474.7668 | 136.18 | 100%
[5 empty] | 136.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139400.1775 | 2250842.2863 | 136.2 | 100%
[5 empty] | 136.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139422.9389 | 2251209.8058 | 136.22 | 100%
[5 empty] | 136.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139445.7003 | 2251577.3253 | 136.24 | 100%
[5 empty] | 136.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139468.4617 | 2251944.8449 | 136.26 | 100%
[5 empty] | 136.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139491.2231 | 2252312.3644 | 136.28 | 100%
[5 empty] | 136.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139513.9845 | 2252679.8839 | 136.3 | 100%
[5 empty] | 136.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139536.7458 | 2253047.4034 | 136.32 | 100%
[5 empty] | 136.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139559.5072 | 2253414.9229 | 136.34 | 100%
[5 empty] | 136.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139582.2686 | 2253782.4425 | 136.36 | 100%
[5 empty] | 136.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139605.03 | 2254149.962 | 136.38 | 100%
[5 empty] | 136.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139627.7914 | 2254517.4815 | 136.4 | 100%
[5 empty] | 136.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139650.5528 | 2254885.001 | 136.42 | 100%
[5 empty] | 136.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139673.3141 | 2255252.5205 | 136.44 | 100%
[5 empty] | 136.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139696.0755 | 2255620.0401 | 136.46 | 100%
[5 empty] | 136.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139718.8369 | 2255987.5596 | 136.48 | 100%
[5 empty] | 136.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139741.5983 | 2256355.0791 | 136.5 | 100%
[5 empty] | 136.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139764.3597 | 2256722.5986 | 136.52 | 100%
[5 empty] | 136.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139787.1211 | 2257090.1181 | 136.54 | 100%
[5 empty] | 136.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139809.8824 | 2257457.6377 | 136.56 | 100%
[5 empty] | 136.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139832.6438 | 2257825.1572 | 136.58 | 100%
[5 empty] | 136.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139855.4052 | 2258192.6767 | 136.6 | 100%
[5 empty] | 136.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139878.1666 | 2258560.1962 | 136.62 | 100%
[5 empty] | 136.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139900.928 | 2258927.7157 | 136.64 | 100%
[5 empty] | 136.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139923.6894 | 2259295.2353 | 136.66 | 100%
[5 empty] | 136.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139946.4508 | 2259662.7548 | 136.68 | 100%
[5 empty] | 136.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139969.2121 | 2260030.2743 | 136.7 | 100%
[5 empty] | 136.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 139991.9735 | 2260397.7938 | 136.72 | 100%
[5 empty] | 136.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140014.7349 | 2260765.3133 | 136.74 | 100%
[5 empty] | 136.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140037.4963 | 2261132.8329 | 136.76 | 100%
[5 empty] | 136.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140060.2577 | 2261500.3524 | 136.78 | 100%
[5 empty] | 136.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140083.0191 | 2261867.8719 | 136.8 | 100%
[5 empty] | 136.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140105.7804 | 2262235.3914 | 136.82 | 100%
[5 empty] | 136.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140128.5418 | 2262602.9109 | 136.84 | 100%
[5 empty] | 136.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140151.3032 | 2262970.4305 | 136.86 | 100%
[5 empty] | 136.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140174.0646 | 2263337.95 | 136.88 | 100%
[5 empty] | 136.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140196.826 | 2263705.4695 | 136.9 | 100%
[5 empty] | 136.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140219.5874 | 2264072.989 | 136.92 | 100%
[5 empty] | 136.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140242.3488 | 2264440.5085 | 136.94 | 100%
[5 empty] | 136.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140265.1101 | 2264808.0281 | 136.96 | 100%
[5 empty] | 136.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140287.8715 | 2265175.5476 | 136.98 | 100%
[5 empty] | 137 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140310.6329 | 2265543.0671 | 137 | 100%
[5 empty] | 137.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140333.3943 | 2265910.5866 | 137.02 | 100%
[5 empty] | 137.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140356.1557 | 2266278.1061 | 137.04 | 100%
[5 empty] | 137.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140378.9171 | 2266645.6257 | 137.06 | 100%
[5 empty] | 137.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140401.6784 | 2267013.1452 | 137.08 | 100%
[5 empty] | 137.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140424.4398 | 2267380.6647 | 137.1 | 100%
[5 empty] | 137.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140447.2012 | 2267748.1842 | 137.12 | 100%
[5 empty] | 137.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140469.9626 | 2268115.7037 | 137.14 | 100%
[5 empty] | 137.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140492.724 | 2268483.2233 | 137.16 | 100%
[5 empty] | 137.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140515.4854 | 2268850.7428 | 137.18 | 100%
[5 empty] | 137.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140538.2467 | 2269218.2623 | 137.2 | 100%
[5 empty] | 137.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140561.0081 | 2269585.7818 | 137.22 | 100%
[5 empty] | 137.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140583.7695 | 2269953.3013 | 137.24 | 100%
[5 empty] | 137.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140606.5309 | 2270320.8209 | 137.26 | 100%
[5 empty] | 137.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140629.2923 | 2270688.3404 | 137.28 | 100%
[5 empty] | 137.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140652.0537 | 2271055.8599 | 137.3 | 100%
[5 empty] | 137.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140674.8151 | 2271423.3794 | 137.32 | 100%
[5 empty] | 137.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140697.5764 | 2271790.8989 | 137.34 | 100%
[5 empty] | 137.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140720.3378 | 2272158.4185 | 137.36 | 100%
[5 empty] | 137.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140743.0992 | 2272525.938 | 137.38 | 100%
[5 empty] | 137.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140765.8606 | 2272893.4575 | 137.4 | 100%
[5 empty] | 137.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140788.622 | 2273260.977 | 137.42 | 100%
[5 empty] | 137.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140811.3834 | 2273628.4965 | 137.44 | 100%
[5 empty] | 137.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140834.1447 | 2273996.0161 | 137.46 | 100%
[5 empty] | 137.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140856.9061 | 2274363.5356 | 137.48 | 100%
[5 empty] | 137.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140879.6675 | 2274731.0551 | 137.5 | 100%
[5 empty] | 137.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140902.4289 | 2275098.5746 | 137.52 | 100%
[5 empty] | 137.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140925.1903 | 2275466.0941 | 137.54 | 100%
[5 empty] | 137.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140947.9517 | 2275833.6137 | 137.56 | 100%
[5 empty] | 137.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140970.713 | 2276201.1332 | 137.58 | 100%
[5 empty] | 137.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 140993.4744 | 2276568.6527 | 137.6 | 100%
[5 empty] | 137.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141016.2358 | 2276936.1722 | 137.62 | 100%
[5 empty] | 137.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141038.9972 | 2277303.6917 | 137.64 | 100%
[5 empty] | 137.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141061.7586 | 2277671.2113 | 137.66 | 100%
[5 empty] | 137.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141084.52 | 2278038.7308 | 137.68 | 100%
[5 empty] | 137.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141107.2814 | 2278406.2503 | 137.7 | 100%
[5 empty] | 137.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141130.0427 | 2278773.7698 | 137.72 | 100%
[5 empty] | 137.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141152.8041 | 2279141.2893 | 137.74 | 100%
[5 empty] | 137.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141175.5655 | 2279508.8089 | 137.76 | 100%
[5 empty] | 137.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141198.3269 | 2279876.3284 | 137.78 | 100%
[5 empty] | 137.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141221.0883 | 2280243.8479 | 137.8 | 100%
[5 empty] | 137.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141243.8497 | 2280611.3674 | 137.82 | 100%
[5 empty] | 137.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141266.611 | 2280978.8869 | 137.84 | 100%
[5 empty] | 137.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141289.3724 | 2281346.4065 | 137.86 | 100%
[5 empty] | 137.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141312.1338 | 2281713.926 | 137.88 | 100%
[5 empty] | 137.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141334.8952 | 2282081.4455 | 137.9 | 100%
[5 empty] | 137.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141357.6566 | 2282448.965 | 137.92 | 100%
[5 empty] | 137.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141380.418 | 2282816.4845 | 137.94 | 100%
[5 empty] | 137.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141403.1794 | 2283184.0041 | 137.96 | 100%
[5 empty] | 137.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141425.9407 | 2283551.5236 | 137.98 | 100%
[5 empty] | 138 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141448.7021 | 2283919.0431 | 138 | 100%
[5 empty] | 138.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141471.4635 | 2284286.5626 | 138.02 | 100%
[5 empty] | 138.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141494.2249 | 2284654.0821 | 138.04 | 100%
[5 empty] | 138.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141516.9863 | 2285021.6017 | 138.06 | 100%
[5 empty] | 138.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141539.7477 | 2285389.1212 | 138.08 | 100%
[5 empty] | 138.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141562.509 | 2285756.6407 | 138.1 | 100%
[5 empty] | 138.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141585.2704 | 2286124.1602 | 138.12 | 100%
[5 empty] | 138.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141608.0318 | 2286491.6797 | 138.14 | 100%
[5 empty] | 138.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141630.7932 | 2286859.1993 | 138.16 | 100%
[5 empty] | 138.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141653.5546 | 2287226.7188 | 138.18 | 100%
[5 empty] | 138.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141676.316 | 2287594.2383 | 138.2 | 100%
[5 empty] | 138.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141699.0773 | 2287961.7578 | 138.22 | 100%
[5 empty] | 138.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141721.8387 | 2288329.2773 | 138.24 | 100%
[5 empty] | 138.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141744.6001 | 2288696.7969 | 138.26 | 100%
[5 empty] | 138.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141767.3615 | 2289064.3164 | 138.28 | 100%
[5 empty] | 138.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141790.1229 | 2289431.8359 | 138.3 | 100%
[5 empty] | 138.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141812.8843 | 2289799.3554 | 138.32 | 100%
[5 empty] | 138.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141835.6457 | 2290166.8749 | 138.34 | 100%
[5 empty] | 138.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141858.407 | 2290534.3945 | 138.36 | 100%
[5 empty] | 138.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141881.1684 | 2290901.914 | 138.38 | 100%
[5 empty] | 138.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141903.9298 | 2291269.4335 | 138.4 | 100%
[5 empty] | 138.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141926.6912 | 2291636.953 | 138.42 | 100%
[5 empty] | 138.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141949.4526 | 2292004.4725 | 138.44 | 100%
[5 empty] | 138.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141972.214 | 2292371.9921 | 138.46 | 100%
[5 empty] | 138.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 141994.9753 | 2292739.5116 | 138.48 | 100%
[5 empty] | 138.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142017.7367 | 2293107.0311 | 138.5 | 100%
[5 empty] | 138.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142040.4981 | 2293474.5506 | 138.52 | 100%
[5 empty] | 138.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142063.2595 | 2293842.0701 | 138.54 | 100%
[5 empty] | 138.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142086.0209 | 2294209.5897 | 138.56 | 100%
[5 empty] | 138.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142108.7823 | 2294577.1092 | 138.58 | 100%
[5 empty] | 138.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142131.5436 | 2294944.6287 | 138.6 | 100%
[5 empty] | 138.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142154.305 | 2295312.1482 | 138.62 | 100%
[5 empty] | 138.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142177.0664 | 2295679.6677 | 138.64 | 100%
[5 empty] | 138.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142199.8278 | 2296047.1873 | 138.66 | 100%
[5 empty] | 138.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142222.5892 | 2296414.7068 | 138.68 | 100%
[5 empty] | 138.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142245.3506 | 2296782.2263 | 138.7 | 100%
[5 empty] | 138.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142268.112 | 2297149.7458 | 138.72 | 100%
[5 empty] | 138.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142290.8733 | 2297517.2653 | 138.74 | 100%
[5 empty] | 138.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142313.6347 | 2297884.7849 | 138.76 | 100%
[5 empty] | 138.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142336.3961 | 2298252.3044 | 138.78 | 100%
[5 empty] | 138.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142359.1575 | 2298619.8239 | 138.8 | 100%
[5 empty] | 138.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142381.9189 | 2298987.3434 | 138.82 | 100%
[5 empty] | 138.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142404.6803 | 2299354.8629 | 138.84 | 100%
[5 empty] | 138.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142427.4416 | 2299722.3825 | 138.86 | 100%
[5 empty] | 138.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142450.203 | 2300089.902 | 138.88 | 100%
[5 empty] | 138.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142472.9644 | 2300457.4215 | 138.9 | 100%
[5 empty] | 138.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142495.7258 | 2300824.941 | 138.92 | 100%
[5 empty] | 138.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142518.4872 | 2301192.4605 | 138.94 | 100%
[5 empty] | 138.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142541.2486 | 2301559.9801 | 138.96 | 100%
[5 empty] | 138.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142564.01 | 2301927.4996 | 138.98 | 100%
[5 empty] | 139 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142586.7713 | 2302295.0191 | 139 | 100%
[5 empty] | 139.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142609.5327 | 2302662.5386 | 139.02 | 100%
[5 empty] | 139.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142632.2941 | 2303030.0581 | 139.04 | 100%
[5 empty] | 139.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142655.0555 | 2303397.5777 | 139.06 | 100%
[5 empty] | 139.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142677.8169 | 2303765.0972 | 139.08 | 100%
[5 empty] | 139.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142700.5783 | 2304132.6167 | 139.1 | 100%
[5 empty] | 139.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142723.3396 | 2304500.1362 | 139.12 | 100%
[5 empty] | 139.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142746.101 | 2304867.6557 | 139.14 | 100%
[5 empty] | 139.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142768.8624 | 2305235.1753 | 139.16 | 100%
[5 empty] | 139.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142791.6238 | 2305602.6948 | 139.18 | 100%
[5 empty] | 139.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142814.3852 | 2305970.2143 | 139.2 | 100%
[5 empty] | 139.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142837.1466 | 2306337.7338 | 139.22 | 100%
[5 empty] | 139.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142859.9079 | 2306705.2533 | 139.24 | 100%
[5 empty] | 139.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142882.6693 | 2307072.7729 | 139.26 | 100%
[5 empty] | 139.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142905.4307 | 2307440.2924 | 139.28 | 100%
[5 empty] | 139.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142928.1921 | 2307807.8119 | 139.3 | 100%
[5 empty] | 139.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142950.9535 | 2308175.3314 | 139.32 | 100%
[5 empty] | 139.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142973.7149 | 2308542.8509 | 139.34 | 100%
[5 empty] | 139.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 142996.4763 | 2308910.3705 | 139.36 | 100%
[5 empty] | 139.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143019.2376 | 2309277.89 | 139.38 | 100%
[5 empty] | 139.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143041.999 | 2309645.4095 | 139.4 | 100%
[5 empty] | 139.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143064.7604 | 2310012.929 | 139.42 | 100%
[5 empty] | 139.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143087.5218 | 2310380.4485 | 139.44 | 100%
[5 empty] | 139.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143110.2832 | 2310747.9681 | 139.46 | 100%
[5 empty] | 139.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143133.0446 | 2311115.4876 | 139.48 | 100%
[5 empty] | 139.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143155.8059 | 2311483.0071 | 139.5 | 100%
[5 empty] | 139.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143178.5673 | 2311850.5266 | 139.52 | 100%
[5 empty] | 139.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143201.3287 | 2312218.0461 | 139.54 | 100%
[5 empty] | 139.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143224.0901 | 2312585.5657 | 139.56 | 100%
[5 empty] | 139.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143246.8515 | 2312953.0852 | 139.58 | 100%
[5 empty] | 139.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143269.6129 | 2313320.6047 | 139.6 | 100%
[5 empty] | 139.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143292.3743 | 2313688.1242 | 139.62 | 100%
[5 empty] | 139.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143315.1356 | 2314055.6437 | 139.64 | 100%
[5 empty] | 139.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143337.897 | 2314423.1633 | 139.66 | 100%
[5 empty] | 139.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143360.6584 | 2314790.6828 | 139.68 | 100%
[5 empty] | 139.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143383.4198 | 2315158.2023 | 139.7 | 100%
[5 empty] | 139.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143406.1812 | 2315525.7218 | 139.72 | 100%
[5 empty] | 139.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143428.9426 | 2315893.2413 | 139.74 | 100%
[5 empty] | 139.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143451.7039 | 2316260.7609 | 139.76 | 100%
[5 empty] | 139.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143474.4653 | 2316628.2804 | 139.78 | 100%
[5 empty] | 139.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143497.2267 | 2316995.7999 | 139.8 | 100%
[5 empty] | 139.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143519.9881 | 2317363.3194 | 139.82 | 100%
[5 empty] | 139.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143542.7495 | 2317730.8389 | 139.84 | 100%
[5 empty] | 139.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143565.5109 | 2318098.3585 | 139.86 | 100%
[5 empty] | 139.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143588.2722 | 2318465.878 | 139.88 | 100%
[5 empty] | 139.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143611.0336 | 2318833.3975 | 139.9 | 100%
[5 empty] | 139.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143633.795 | 2319200.917 | 139.92 | 100%
[5 empty] | 139.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143656.5564 | 2319568.4365 | 139.94 | 100%
[5 empty] | 139.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143679.3178 | 2319935.9561 | 139.96 | 100%
[5 empty] | 139.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143702.0792 | 2320303.4756 | 139.98 | 100%
[5 empty] | 140 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143724.8406 | 2320670.9951 | 140 | 100%
[5 empty] | 140.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143747.6019 | 2321038.5146 | 140.02 | 100%
[5 empty] | 140.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143770.3633 | 2321406.0341 | 140.04 | 100%
[5 empty] | 140.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143793.1247 | 2321773.5537 | 140.06 | 100%
[5 empty] | 140.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143815.8861 | 2322141.0732 | 140.08 | 100%
[5 empty] | 140.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143838.6475 | 2322508.5927 | 140.1 | 100%
[5 empty] | 140.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143861.4089 | 2322876.1122 | 140.12 | 100%
[5 empty] | 140.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143884.1702 | 2323243.6317 | 140.14 | 100%
[5 empty] | 140.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143906.9316 | 2323611.1513 | 140.16 | 100%
[5 empty] | 140.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143929.693 | 2323978.6708 | 140.18 | 100%
[5 empty] | 140.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143952.4544 | 2324346.1903 | 140.2 | 100%
[5 empty] | 140.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143975.2158 | 2324713.7098 | 140.22 | 100%
[5 empty] | 140.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 143997.9772 | 2325081.2293 | 140.24 | 100%
[5 empty] | 140.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144020.7385 | 2325448.7489 | 140.26 | 100%
[5 empty] | 140.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144043.4999 | 2325816.2684 | 140.28 | 100%
[5 empty] | 140.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144066.2613 | 2326183.7879 | 140.3 | 100%
[5 empty] | 140.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144089.0227 | 2326551.3074 | 140.32 | 100%
[5 empty] | 140.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144111.7841 | 2326918.8269 | 140.34 | 100%
[5 empty] | 140.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144134.5455 | 2327286.3465 | 140.36 | 100%
[5 empty] | 140.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144157.3069 | 2327653.866 | 140.38 | 100%
[5 empty] | 140.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144180.0682 | 2328021.3855 | 140.4 | 100%
[5 empty] | 140.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144202.8296 | 2328388.905 | 140.42 | 100%
[5 empty] | 140.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144225.591 | 2328756.4245 | 140.44 | 100%
[5 empty] | 140.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 804418.56 | 1102558.56 | 144248.3524 | 2329123.9441 | 140.46 | 100%

## RadCompList (hidden)
Column Radiators
| Sq Ft Radiation Per Section | Columns |  |  |  |  | FALSE |  |  |  | Rad Types | ft3/edr
Rad Type | Column | 1 | 2 | 3 | 4 | 5 | 1 |  |  |  | Column | 0.025
Column | 13 | - | - | - | - | 3 | 2 |  |  |  | Tube | 0.013
Column | 16 | - | - | - | - | 3.75 | 3 |  |  |  | Cast Rad/Conv | 0.0003
Column | 18 | - | - | 2.25 | 3 | 4.25 | 4 |  |  |  | Copper Cabinet | 0.0003
Column | 20 | 1.5 | 2 | - | - | 5 | 5
Column | 22 | - | - | 3 | 4 | - | 6
Column | 23 | 1.66 | 2.33 | - | - | - | 7
Column | 26 | 2 | 2.66 | 3.75 | 5 | - | 8 |  |  |  |  | Sections list
Column | 32 | 2.5 | 3.33 | 4.5 | 6.5 | - | 9 |  |  |  |  | 1
Column | 38 | 3 | 4 | 5 | 8 | - | 10 |  |  |  |  | 2
Column | 45 | - | 5 | 6 | 10 | - | 11 |  |  |  |  | 3
|  | Columns 1: Tubes |  |  |  |  | 4
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 |  |  | 5
Tube | 13 | , | - | - | - | - | - | 2.625 | 2 |  |  | 6
Tube | 16.5 | - | - | - | - | - | - | 3.5 | 3 |  |  | 7
Tube | 20 | - | - | 1.75 | 2.25 | 2.66 | 3 | 4.25 | 4 |  |  | 8
Tube | 23 | - | - | 2 | 2.5 | 3 | 3.5 | - | 5 |  |  | 9
Tube | 26 | - | - | 2.11 | 2.75 | 3.5 | 4 | - | 6 |  |  | 10
Tube | 32 | - | - | 3 | 3.5 | 4.33 | 5 | - | 7
Tube | 37 | - | - | 3.5 | 4.125 | 5 | 6 | - | 8
Width
|  | 5 | 7.5
Cast Rad/Conv | 20 | Tubes 1: 2.25; Tubes 2: 3.4
10-1/2 X 20-1/2
|  | 10-1/2 X 20-1/2 |  | 1
|  | 18 | #N/A | 31
Height
| Cabinet Depth | Cabinet Length | Dimensions | 18 | 20 | 24 | 26 | 32 | 38
Copper Cabinet | 4-1/2" | 20-1/2" | 4-1/2 X 20-1/2 | 10.4 | 11.3 | 13.1 | 13.4 | 14 | 14.6
Copper Cabinet | 4-1/2" | 24-1/2" | 4-1/2 X 24-1/2 | 12.8 | 13.9 | 16.1 | 16.4 | 17.2 | 18
Copper Cabinet | 4-1/2" | 28-1/2" | 4-1/2 X 28-1/2 | 15.2 | 16.5 | 19.2 | 19.5 | 20.4 | 21.3
Copper Cabinet | 4-1/2" | 32-1/2" | 4-1/2 X 32-1/2 | 17.6 | 19.1 | 22.2 | 22.5 | 23.6 | 24.6
Copper Cabinet | 4-1/2" | 36-1/2" | 4-1/2 X 36-1/2 | 19.7 | 21.7 | 25.2 | 25.6 | 26.8 | 28
Copper Cabinet | 4-1/2" | 40-1/2" | 4-1/2 X 40-1/2 | 22.3 | 24.3 | 28.2 | 28.6 | 30 | 31.3
Copper Cabinet | 4-1/2" | 44-1/2" | 4-1/2 X 44-1/2 | 24.7 | 26.9 | 31.2 | 31.7 | 33.2 | 34.7
Copper Cabinet | 4-1/2" | 48-1/2" | 4-1/2 X 48-1/2 | 27.1 | 29.5 | 34.2 | 34.7 | 36.4 | 38
Copper Cabinet | 4-1/2" | 56-1/2" | 4-1/2 X 56-1/2 | 31.9 | 34.7 | 40.2 | 40.8 | 42.8 | 44.7
Copper Cabinet | 4-1/2" | 64-1/2" | 4-1/2 X 64-1/2 | 36.6 | 39.9 | 46.2 | 46.9 | 49.2 | 51.7
Copper Cabinet | 6-1/2" | 20-1/2" | 6-1/2 X 20-1/2 | 15.3 | 16.3 | 18.4 | 18.8 | 19.6 | 20.6
Copper Cabinet | 6-1/2" | 24-1/2" | 6-1/2 X 24-1/2 | 18.8 | 20.1 | 22.6 | 23.1 | 24.1 | 25.3
Copper Cabinet | 6-1/2" | 28-1/2" | 6-1/2 X 28-1/2 | 22.3 | 23.8 | 26.9 | 27.4 | 28.6 | 30.1
Copper Cabinet | 6-1/2" | 32-1/2" | 6-1/2 X 32-1/2 | 25.8 | 27.6 | 31.1 | 31.7 | 33.2 | 34.8
Copper Cabinet | 6-1/2" | 36-1/2" | 6-1/2 X 36-1/2 | 29.3 | 31.3 | 35.4 | 36 | 37.7 | 39.6
Copper Cabinet | 6-1/2" | 40-1/2" | 6-1/2 X 40-1/2 | 32.8 | 35.1 | 39.6 | 40.3 | 42.2 | 44.3
Copper Cabinet | 6-1/2" | 44-1/2" | 6-1/2 X 44-1/2 | 36.3 | 38.9 | 43.8 | 44.6 | 48.7 | 49.9 | Cabinet Depth
Copper Cabinet | 6-1/2" | 48-1/2" | 6-1/2 X 48-1/2 | 39.8 | 42.6 | 48.1 | 48.9 | 51.2 | 53.8 | 4-1/2"
Copper Cabinet | 6-1/2" | 56-1/2" | 6-1/2 X 56-1/2 | 46.8 | 50.1 | 56.6 | 57.5 | 60.6 | 63.3 | 6-1/2"
Copper Cabinet | 6-1/2" | 64-1/2" | 6-1/2 X 64-1/2 | 53.9 | 57.7 | 65 | 66.2 | 69.3 | 72.7 | 8-1/2"
Copper Cabinet | 8-1/2" | 20-1/2" | 8-1/2 X 20-1/2 | 18.7 | 20 | 22.5 | 23 | 24.4 | 25.8 | 10-1/2"
Copper Cabinet | 8-1/2" | 24-1/2" | 8-1/2 X 24-1/2 | 22.9 | 24.5 | 27.7 | 28.8 | 30 | 3.7
Copper Cabinet | 8-1/2" | 28-1/2" | 8-1/2 X 28-1/2 | 27.2 | 20.1 | 32.8 | 33.5 | 35.6 | 37.7
Copper Cabinet | 8-1/2" | 32-1/2" | 8-1/2 X 32-1/2 | 31.5 | 33.7 | 38 | 38.8 | 41.2 | 43.6
Copper Cabinet | 8-1/2" | 36-1/2" | 8-1/2 X 36-1/2 | 35.8 | 38.3 | 43.2 | 44.1 | 46.8 | 49.5
Copper Cabinet | 8-1/2" | 40-1/2" | 8-1/2 X 40-1/2 | 40.1 | 42.9 | 48.3 | 49.4 | 52.4 | 55.5
Copper Cabinet | 8-1/2" | 44-1/2" | 8-1/2 X 44-1/2 | 44.3 | 47.4 | 53.3 | 54.6 | 58 | 61.4
Copper Cabinet | 8-1/2" | 48-1/2" | 8-1/2 X 48-1/2 | 48.6 | 52 | 58.7 | 59.9 | 63.6 | 67.3
Copper Cabinet | 8-1/2" | 56-1/2" | 8-1/2 X 56-1/2 | 57.2 | 61.2 | 69 | 70.5 | 74.8 | 79.2
Copper Cabinet | 8-1/2" | 64-1/2" | 8-1/2 X 64-1/2 | 65.7 | 70.3 | 79.4 | 81 | 86 | 91
Copper Cabinet | 10-1/2" | 20-1/2" | 10-1/2 X 20-1/2 | 20.4 | 22 | 25 | 25.7 | 27.4 | 29.3
Copper Cabinet | 10-1/2" | 24-1/2" | 10-1/2 X 24-1/2 | 25.2 | 27.1 | 30.9 | 31.7 | 33.8 | 36.2
Copper Cabinet | 10-1/2" | 28-1/2" | 10-1/2 X 28-1/2 | 30 | 32.3 | 36.8 | 37.7 | 40.2 | 43.1
Copper Cabinet | 10-1/2" | 32-1/2" | 10-1/2 X 32-1/2 | 34.8 | 37.4 | 42.6 | 43.7 | 46.6 | 50
Copper Cabinet | 10-1/2" | 36-1/2" | 10-1/2 X 36-1/2 | 39.6 | 42.6 | 48.5 | 49.8 | 53.1 | 56.9
Copper Cabinet | 10-1/2" | 40-1/2" | 10-1/2 X 40-1/2 | 44.4 | 47.7 | 54.4 | 55.8 | 59.5 | 63.7
Copper Cabinet | 10-1/2" | 44-1/2" | 10-1/2 X 44-1/2 | 49.2 | 52.9 | 60.3 | 61.8 | 65.9 | 70.6
Copper Cabinet | 10-1/2" | 48-1/2" | 10-1/2 X 48-1/2 | 53.9 | 58 | 66.1 | 67.8 | 72.3 | 77.5
Copper Cabinet | 10-1/2" | 56-1/2" | 10-1/2 X 56-1/2 | 63.5 | 68.3 | 77.9 | 79.9 | 85.2 | 91.2
Copper Cabinet | 10-1/2" | 64-1/2" | 10-1/2 X 64-1/2 | 73.1 | 78.6 | 89.6 | 91.9 | 98 | 105

## VentList (hidden)
MAIN VENTS | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM | Vent Lines
- | 0 | 0 | 0
Open 1/8" Steel Pipe | 1.2 | 2 | 2.5
Open 1/2" Steel Pipe | 2.6 | 3.4 | 4.8 | A
Open 3/4" Steel Pipe | Note 1 | Note 1 | 9.5 | B
Open 1" Steel Pipe | Note 1 | Note 1 | 11 | C
American Radiator Co. Ideal Vac-Vent #822 - (obsolete) | 0.1 | 0.158 | 0.2 | D
Barnes & Jones QV 1 (obsolete) | 0.583 | 1.58 | 2 | E
Barnes & Jones Ventrite #75-- (obsolete) | 0.116 | 0.175 | 0.225 | F
Detroit Controls #841 Quick Vent (obsolete) | 0.333 | 0.55 | 0.7 | G
Dole #5 Quick Vent | 0.066 | 0.116 | 0.15 | H
Gorton #1 | 0.33 | 0.54 | 0.7 | I
Gorton #2 | 1.1 | 1.75 | 2.2 | J
Hoffman #4 | 0.06 | 0.11 | 0.13 | K
Hoffman #4A | 0.133 | 0.216 | 0.266 | L
Hoffman #6 Vacuum Valve (obsolete) | 0.033 | 0.083 | 0.108 | M
Hoffman #10 Vapor Vent - (obsolete) | 2.033 | 2.5 | 3.7 | N
Hoffman #11 Vapor Vacuum Vent (obsolete) | 1 | 2.41 | 3.33 | O
Hoffman #15 Vacuum Vent (obsolete) Differential Loop | 1.283 | 2.75 | 3.416 | Single Pipe
Hoffman #16 Vacuum Valve (obsolete) | 0.066 | 0.116 | 0.15
Hoffman #16A Vacuum Valve (obsolete) | 0.1 | 0.183 | 0.241
Hoffman #75 | 0.5 | 0.75 | 0.96
Hoffman #76 Vacuum Valve | 0.383 | 0.666 | 0.833
Ideal Htg. Co. "Wafer Style" - - (obsolete) | 0.09 | 0.13 | 0.166
Maid-O-Mist #1 Straight Pattern | 0.333 | 0.59 | 0.766
Marsh #55 | 0.01 | 0.021 | 0.033
Mouat Cast Iron 'Bullet' Style (obsolete) | 0.53 | 0.91 | 1.11
Mouat Tri Tube (obsolete) | 1.16 | 1.8 | 2
Squires Co. Mouat Series Cast Iron Bullet Style (obsolete) | 0.53 | 0.91 | 1.11
Trane Cast Iron Bullet Style (obsolete) | 0.78 | 1.33 | 1.7
Vent Rite #35 | 0.11 | 0.2 | 0.25
Vent Rite #75 (Barnes & Jones Issue) (obsolete) | 0.116 | 0.175 | 0.225
Vent Rite #77 | 0.19 | 0.31 | 0.4
Watts SVS-3 | 0.07 | 0.116 | 0.15
Warco #3(obsolete) | 0.05 | 0.108 | 0.15
Warco #87 (obsolete) | 0.108 | 0.175 | 0.233
Warren Webster #40-15 Vent Trap (obsolete) | 1.166 | 1.866 | 2.366
Radiator Vents | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM
- | 0 | 0 | 0
#1 (obsolete) Airmatic | 0.045 | 0.222 | 0.1
American Radiator Co. Detroit Controls #500 Airid (obsolete) | 0.036 | 0.061 | 0.08
ARCO Detroit Controls Multiport Setting 1-- (obsolete) | Note 3 | Note 3 | Note 3
ARCO Detroit Controls Multiport Setting 2 (obsolete) | Note 3 | Note 3 | Note 3
ARCO Detroit Controls Multiport Setting 3- (obsolete) | Note 3 | Note 3 | 0.011
Detroit Controls Multiport Setting 4 (obsolete) ARCO | 0.021 | 0.028 | 0.038
ARCO Detroit Controls Multiport Setting 5 (obsolete) | 0.045 | 0.075 | 0.1
ARCO Detroit Controls Multiport Setting 6 (obsolete) | 0.05 | 0.108 | 0.141
ARCO Detroit Controls Multiport Setting 7-- (obsolete) | 0.066 | 0.116 | 0.158
Detroit Controls Multiport Setting 8 (obsolete) ARCO | 0.083 | 0.141 | 0.191
ARCO Detroit Controls Multiport Setting 9 (obsolete) | 0.1 | 0.158 | 0.208
ARCO Detroit Controls Multiport Setting 10- (obsolete) | 0.116 | 0.183 | 0.241
Detroit Controls #5000 Airid Variport (obsolete) Low setting | NONE | 0.011 | 0.016
Detroit Controls #5000 Airid Variport (obsolete) Med setting | 0.036 | 0.051 | 0.061
Detroit Controls #5000 Airid Variport (obsolete) High setting | 0.066 | 0.125 | 0.166
Dole 1933 | 0.033 | 0.055 | 0.07
Dole 1A Setting 1 | 0.045 | 0.071 | 0.125
Dole 1A Setting 2 | 0.068 | 0.116 | 0.15
Dole 1A Setting 3 | 0.083 | 0.125 | 0.166
Dole 1A Setting 4 | 0.091 | 0.15 | 0.191
Dole 1A Setting 5 | 0.125 | 0.208 | 0.266
Dole 1A Setting 6 | 0.133 | 0.216 | 0.283
Dole 1A Setting 1 Modern Version W/Plastic Tongue *Note 4 | 0.061 | 0.111 | 0.148
Dole 1A Setting 2 Modern Version W/Plastic Tongue *Note 4 | 0.084 | 0.141 | 0.186
Dole 1A Setting 3 Modern Version W/Plastic Tongue *Note 4 | 0.108 | 0.183 | 0.228
Dole 1A Setting 4 Modern Version W/Plastic Tongue *Note 4 | 0.116 | 0.201 | 0.254
Dole 1A Setting 5 Modern Version W/Plastic Tongue *Note 4 | 0.129 | 0.21 | 0.266
Dole 1A Setting 6 Modern Version W/Plastic Tongue *Note 4 | 0.133 | 0.22 | 0.274
Dole 1A Setting 7 Modern Version W/Plastic Tongue *Note 4 | 0.143 | 0.233 | 0.295
Dole 1A Setting 8 Modern Version W/Plastic Tongue *Note 4 | 0.147 | 0.245 | 0.283
Dole 1A Setting 9 Modern Version W/Plastic Tongue *Note 4 | 0.152 | 0.268 | 0.289
Dole 1A Setting 10 Modern Version W/Plastic Tongue *Note 4 | 0.152 | 0.269 | 0.289
Dole 1A Cap Removed Modern Version W/Plastic Tongue | 0.212 | 0.339 | 0.431
Flair #51 - - (obsolete) | 0.116 | 0.191 | 0.25
Gorton 4 | 0.025 | 0.04 | 0.055
Gorton 5 | 0.08 | 0.13 | 0.16
Gorton 6 | 0.15 | 0.235 | 0.3
Gorton C | 0.27 | 0.45 | 0.57
Gorton D | 0.33 | 0.54 | 0.7
Heat Timer Varivalve Min Setting Angle Pattern | 0.065 | 0.158 | 0.2
Heat Timer Varivalve 50% Setting Angle Pattern | 0.34 | 0.58 | 0.766
Heat Timer Varivalve Max Setting Angle Pattern | 0.516 | 0.85 | 1.13
Heat Timer Varivalve Min Setting Straight Pattern | 0.06 | 0.083 | 0.33
Heat Timer Varivalve 50% Setting Straight Pattern | 0.53 | 0.8 | 1.03
Heat Timer Varivalve Max Setting Straight Pattern | 0.66 | 1.08 | 1.36
Hoffman #1 - - (obsolete) | 0.016 | 0.075 | 0.1
Hoffman 1A Setting 1 | 0.02 | 0.026 | 0.033
Hoffman 1A Setting 2 | 0.026 | 0.043 | 0.056
Hoffman 1A Setting 3 | 0.1 | 0.158 | 0.2
Hoffman 1A Setting 4 | 0.108 | 0.16 | 0.21
Hoffman 1A Setting 5 | 0.14 | 0.22 | 0.29
Hoffman 1A Setting 6 | 0.145 | 0.225 | 0.3
Hoffman #2 Vacuum Vent Non Adjustable - - (obsolete) | 0.016 | 0.066 | 0.1
Hoffman #2 Vacuum Vent Setting 1 - - (obsolete) | 0.001 | 0.021 | 0.025
Hoffman #2 Vacuum Vent Setting 2 - - (obsolete) | 0.006 | 0.024 | 0.028
Hoffman #2 Vacuum Vent Setting 3 - - (obsolete) | 0.008 | 0.025 | 0.033
Hoffman #2 Vacuum Vent Setting 4 - - (obsolete) | 0.01 | 0.026 | 0.036
Hoffman #2 Vacuum Vent Setting 5 - - (obsolete) | 0.013 | 0.029 | 0.04
Hoffman #2 Vacuum Vent Setting 6 - - (obsolete) | 0.016 | 0.031 | 0.045
Hoffman #2A Vacuum Vent Setting 1 - - (obsolete) | 0.001 | 0.023 | 0.025
Hoffman #2A Vacuum Vent Setting 2 - - (obsolete) | 0.018 | 0.03 | 0.043
Hoffman #2A Vacuum Vent Setting 3 - - (obsolete) | 0.021 | 0.038 | 0.053
Hoffman #2A Vacuum Vent Setting 4 - - (obsolete) | 0.028 | 0.058 | 0.068
Hoffman #2A Vacuum Vent Setting 5 - - (obsolete) | 0.036 | 0.063 | 0.088
Hoffman #2A Vacuum Vent Setting 6 - - (obsolete) | 0.041 | 0.083 | 0.116
Hoffman #3 (Paul Vent) | 0.175 | 0.283 | 0.416
Hoffman 40 | 0.042 | 0.067 | 0.087
Hoffman 41 | 0.058 | 0.1 | 0.125
Hoffman #70 Airport Non Adjustable - - (obsolete) | 0.05 | 0.108 | 0.141
Hoffman #70 Airport Setting #1 - - (obsolete) | 0.045 | 0.078 | 0.125
Hoffman #70 Airport Setting #2 - - (obsolete) | 0.05 | 0.087 | 0.15
Hoffman #70 Airport Setting #3 - - (obsolete) | 0.053 | 0.116 | 0.166
Hoffman #70 Airport Setting #4 - - (obsolete) | 0.056 | 0.141 | 0.183
Hoffman #70 Airport Setting #5 - - (obsolete) | 0.06 | 0.15 | 0.191
Hoffman #70 Airport Setting #6 - - (obsolete) | 0.066 | 0.15 | 0.191
Hoffman #74 Unit Heater Vent | 0.033 | 0.083 | 0.108
Hoffman #500 | 0.066 | 0.112 | 0.142
Homart #775.8812 | 0.083 | 0.133 | 0.175
Marsh Paul Vent (circa 1901) - - (obsolete) | 0.35 | 0.583 | 0.75
Marsh #3 (Paul Vent) - - (obsolete) | 0.183 | 0.295 | 0.375
Maid-O-Mist 4 | 0.028 | 0.045 | 0.06
Maid-O-Mist 5 | 0.1 | 0.158 | 0.2
Maid-O-Mist 6 | 0.15 | 0.241 | 0.3
Maid-O-Mist C | 0.283 | 0.45 | 0.583
Maid-O-Mist D | 0.341 | 0.6 | 0.783
M.S. Little Co. #L-15 - - (obsolete) | 0.026 | 0.045 | 0.055
National Steam Specialty Co. Paul Vent - - (obsolete) | 0.15 | 0.266 | 0.333
U.S. Radiator #3 Triton - - (obsolete) | 0.023 | 0.033 | 0.041
Ventrite #1 Setting 1 | Off | Off | Off
Ventrite #1 Setting 2 | 0.033 | 0.02 | 0.021
Ventrite #1 Setting 3 | 0.025 | 0.036 | 0.046
Ventrite #1 Setting 4 | 0.03 | 0.053 | 0.066
Ventrite #1 Setting 5 | 0.045 | 0.071 | 0.091
Ventrite #1 Setting 6 | 0.056 | 0.091 | 0.116
Ventrite #1 Setting 7 | 0.07 | 0.108 | 0.133
Ventrite #1 Setting 8 | 0.083 | 0.125 | 0.158
Ventrite #2 IVS (obsolete Anderson Manufacturing) | 0.028 | 0.053 | 0.078
Ventrite #11 | 0.06 | 0.1 | 0.116
Watts SV | 0.066 | 0.108 | 0.133
Watts SVA setting 1/8 | 0.03 | 0.063 | 0.075
Watts SVA setting 1/4 | 0.066 | 0.108 | 0.133
Watts SVA setting 1/2 ** | 0.066 | 0.108 | 0.133
Watts SVA setting 3/4 ** | 0.066 | 0.108 | 0.133
Watts SVA setting 7/8 ** | 0.066 | 0.108 | 0.133
Watts SVA setting Full ** | 0.066 | 0.108 | 0.133
STEAM TRAPS | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM
Barnes & Jones 1/2" #122 | 1.5 | 1.8 | 2.7
Dunham #1 1/2" - - (obsolete) | 1.45 | 2.41 | 3
Dunham #1 W/B&J Cage Unit | 0.73 | 1.16 | 1.5
Dunham - Bush #1E - - (obsolete) | 1.08 | 1.8 | 2.25
Dunham - Bush #1E W/B&J Cage Unit | 0.71 | 1.13 | 1.41
Hoffman 17C 1/2" W/Dura-Stat Capsule | 0.53 | 0.85 | 1.1
Hoffman 17C W/B&J Cage Unit | 1.3 | 2.116 | 2.7
Hoffman 17D 1/2" Model 1939 - - (obsolete) | 1.45 | 2.38 | 3
Ideal Heating Co. Thermostatic 1/2" - - (obsolete) | 1.53 | 2.33 | 3.08
Ideal W/B&J Cage Unit Installed | 1.25 | 2 | 2.58
Illinois 1/2" #1G | 0.86 | 1.2 | 1.6
Marsh #1 Reflux - - (obsolete) | 1.13 | 1.83 | 2.36
Marsh #1 Reflux W/B&J Cage Unit | 0.73 | 1.16 | 1.5
Marsh 1N 1/2" | 0.53 | 0.91 | 1.16
Mepco 1/2" #1E | 1.08 | 1.4 | 1.9
Mepco 1/2" #1R | 1.08 | 1.4 | 1.9
Milvaco Model #0 - - (obsolete) | 1.08 | 1.71 | 2.13
Milvaco Model #0 W/B&J Cage Unit | 1 | 1.58 | 1.966
Monash #30 1/2" | 0.86 | 1.2 | 1.6
Monash #34 1/2" | 1.21 | 2 | 2.5
Monash #38 1/2" | 1.45 | 2.45 | 3.08
Mouat Model 1924 Thermostatic 1/2" - - (obsolete) | 1.53 | 2.33 | 3.08
Mouat 1924 W/B&J Cage Unit Installed | 1.25 | 2 | 2.58
Mouat #35 1/2" - - (Obsolete) | 1.33 | 1.66 | 2.08
Mouat #35 1/2" W/B&J Cage Unit Installed | 1.366 | 2.33 | 2.91
Mouat #36 1/2" - - (Obsolete) | 1.083 | 1.533 | 1.83
Mouat #36 1/2" W/B&J Cage Unit Installed | 1.266 | 2 | 2.5
Mouat Water Seal Trap 1/2" Oval - - (obsolete) | 2 | 2.4 | 3.4
Mouat Water Seal Trap 1/2" Round - - (obsolete) | 2 | 2.4 | 3.6
Nicholson #N125 | 1.53 | 2.53 | 3.08
Sarco A125 1/2" | 0.5 | 0.78 | 1
Sterling 7-50-A-1/2" | 1.08 | 1.75 | 2.16
Trane B1 W/Original Bellows - - (obsolete) | 0.5 | 0.75 | 1
Trane B1 W/Modern Trane Element | 0.78 | 1.25 | 1.58
Trane B1 W/B&J Cage Unit | 0.75 | 1.2 | 1.5
Trane 1/2" (no number) - - (obsolete) | 1.58 | 2.66 | 3.33
Warren Webster 02H 1/2" W/B&J Cage Unit | 0.783 | 1.333 | 1.75
Warren Webster 02H 1/2" W/Tunstall Capsule | 0.616 | 0.966 | 1.21
Warren Webster 512H 1/2" W/512A seat (5/16") - - (obsolete) | 1.08 | 1.75 | 2.25
Warren Webster 512H 1/2" W/512S seat (1/4") - - (obsolete) | 0.783 | 1.28 | 1.66
Warren Webster 512H 1/2" W/B&J Cage Unit | 1.36 | 2.25 | 2.83
Warren Webster 712HB 1/2" W/H57 Seat (.368") - - (obsolete) | 0.75 | 1.233 | 1.433
Warren Webster 712 HB 1/2" W/522S Seat (.332") - - (obsolete) | 0.5 | 0.8 | 1.25
Warren Webster 712 HB 1/2" W/B&J Cage Unit | 1.55 | 2.55 | 3.216
Barnes & Jones 3/4" #134A | 1.36 | 2.28 | 2.88
Hoffman 8C 3/4" | 1 | 1.58 | 2
Mepco 3/4" 2E | 1.53 | 2.55 | 3.16
Monash #48 3/4" | 2.16 | 3.5 | 5
Sterling 3/4" #753A | 1.25 | 2 | 2.58
Spirax Sarco F&T Traps (FT-15, FT-30, etc.) | 0.5 | 0.75 | 0.966
Hoffman F&T Traps (FT015H, FT015C, etc.) | 0.5 | 0.75 | 0.95
Sterling F&T Traps (vac. to 15 lb.) | 1.3 | 2.083 | 2.666
Barnes & Jones F&T Traps (vac. to 15 lb.) | 0.75 | 1.2 | 1.5

## Radiators
Heat Load(%) | Radiator Type | Height(In) | Cols/Tubes/(WxL) | Sections | Upfeed Length(ft) | Vent/Trap Type | EDR Sqft | Btu/hr | Vent Capacity(3oz) | Radiator Vol(ft3) | Supply Pipe Size | Radiator Pressure(PSI) | Condensate(lb/hr) | Pipe Radiation(BTU/hr) | Pipe Volume(ft3) | Pipe Condensate(lb/hr) | Radiator Weight(lbs) | Pipe weight(lbs) | Total BTUs Radiation | Total EDR | Min PSI
92% | Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58 | 1047958.56 | 4657.95 | 0.069325
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | 36.8 | 8125.44 | 0.86 | 0.92 | 1 | 0.069325 | 8.1499 | 2460 | 0.10914 | 8.3767 | 280 | 33.58
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 3/4 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0

## REPORT
Address:
Boiler Information |  | Relavent Calculations
Boiler Manufacturer | Weil-Mclain | Water @ Waterline(gal) | 69.1
Boiler Model | LGB-12 | Time to Steam(minutes) | 9
Rated Power Input(BTU/HR) | 1430000 | Time to Vent(minutes) | 19
Gross Power Output(BTU/HR) | 1144000 | Time to Steady State(min) | 49.9233
Water @ Waterline(gal) | 69.1
Radiator Calcuations |  | System Status
TOTAL RADIATION (BTU/HR) | 1102558.56 | Trap Operating %
Radiator Output(EDR) | 3643.2 | Actual Steam Time(min)
Steam Main Output(EDR) | 227.5 | Actual Vent Time(min)
Steam Upfeed Output(EDR) | 1014.75 | Boiler Status
Column Radiators | 99
Tube Radiators | 0
Convectors | 0
Copper Cabinets | 0
NOTES

## Boiler List (hidden)
Manufacturer | Boiler Model | Input MBH (Note 2) | Gross Output MBH (Note 2) | Sq. Ft. Steam | Boiler Water Content Gallons (Steam to Waterline) | Approx. Shipping Weight (lbs.) |  | Manufactuer List
Weil-Mclain | LGB-4 | 400 | 312 | 975 | 23.2 | 1185 | Weil-Mclain
Weil-Mclain | LGB-5 | 520 | 409 | 1279 | 28.9 | 1455 | Weil-Mclain | Weil-Mclain
Weil-Mclain | LGB-6 | 650 | 514 | 1607 | 34.6 | 1725 | Weil-Mclain | Burnham
Weil-Mclain | LGB-7 | 780 | 619 | 1936 | 40.3 | 2005 | Weil-Mclain | Peerless
Weil-Mclain | LGB-8 | 910 | 724 | 2264 | 46 | 2290 | Weil-Mclain | Green Mountain
Weil-Mclain | LGB-9 | 1040 | 829 | 2591 | 51.9 | 2560 | Weil-Mclain
Weil-Mclain | LGB-10 | 1170 | 934 | 2918 | 57.6 | 2800 | Weil-Mclain
Weil-Mclain | LGB-11 | 1300 | 1039 | 3246 | 63.4 | 3105 | Weil-Mclain
Weil-Mclain | LGB-12 | 1430 | 1144 | 3576 | 69.1 | 3365 | Weil-Mclain
Weil-Mclain | LGB-13 | 1560 | 1239 | 3868 | 74.9 | 3785 | Weil-Mclain
Weil-Mclain | LGB-14 | 1690 | 1344 | 4228 | 80.7 | 4085 | Weil-Mclain
Weil-Mclain | LGB-15 | 1820 | 1449 | 4592 | 86.4 | 4355 | Weil-Mclain
Weil-Mclain | LGB-16 | 1950 | 1552 | 4950 | 92.2 | 4725 | Weil-Mclain
Weil-Mclain | LGB-17 | 2080 | 1658 | 5316 | 98 | 4975 | Weil-Mclain
Weil-Mclain | LGB-18 | 2210 | 1764 | 5682 | 103.6 | 5270 | Weil-Mclain
Weil-Mclain | LGB-19 | 2340 | 1867 | 6034 | 109.5 | 5540 | Weil-Mclain
Weil-Mclain | LGB-20 | 2470 | 1974 | 6384 | 115.3 | 5820 | Weil-Mclain
Weil-Mclain | LGB-21 | 2600 | 2077 | 6720 | 121 | 6080 | Weil-Mclain
Weil-Mclain | LGB-22 | 2730 | 2184 | 7065 | 126.8 | 6365 | Weil-Mclain
Weil-Mclain | LGB-23 | 2860 | 2288 | 7402 | 132.5 | 6625 | Weil-Mclain
Weil-Mclain | Series 80 - 380 | 346 | 278 | 867 | 27.5 | 1058 | Weil-Mclain
Weil-Mclain | Series 80 - 480 | 491 | 396 | 1238 | 36 | 1203 | Weil-Mclain
Weil-Mclain | Series 80 - 580 | 639 | 515 | 1608 | 44.5 | 1448 | Weil-Mclain
Weil-Mclain | Series 80 - 680 | 787 | 634 | 1983 | 53 | 1843 | Weil-Mclain
Weil-Mclain | Series 80 - 780 | 935 | 753 | 2354 | 61.5 | 2088 | Weil-Mclain
Weil-Mclain | Series 80 - 880 | 1082 | 872 | 2725 | 70 | 2317 | Weil-Mclain
Weil-Mclain | Series 80 - 980 | 1230 | 991 | 3096 | 78.5 | 2678 | Weil-Mclain
Weil-Mclain | Series 80 - 1080 | 1378 | 1110 | 3471 | 87 | 2923 | Weil-Mclain
Weil-Mclain | Series 80 - 1180 | 1526 | 1229 | 3842 | 95.5 | 3068 | Weil-Mclain
Weil-Mclain | Series 80 - 1280 | 1674 | 1348 | 4242 | 104 | 3313 | Weil-Mclain
Weil-Mclain | Series 88 - 488R | 996 | 827 | 2583 | 109 | 2860 | Weil-Mclain
Weil-Mclain | Series 88 - 488 | 1010 | 839 | 2621 | 109 | 2860 | Weil-Mclain
Weil-Mclain | Series 88 - 588 | 1356 | 1126 | 3521 | 132 | 3340 | Weil-Mclain
Weil-Mclain | Series 88 - 688 | 1701 | 1413 | 4469 | 155 | 3820 | Weil-Mclain
Weil-Mclain | Series 88 - 788 | 2046 | 1700 | 5463 | 178 | 4345 | Weil-Mclain
Weil-Mclain | Series 88 - 788R | 1999 | 1661 | 5463 | 178 | 4345 | Weil-Mclain
Weil-Mclain | Series 88 - 888 | 2382 | 1987 | 6427 | 201 | 4925 | Weil-Mclain
Weil-Mclain | Series 88 - 988R | 2482 | 2062 | 6671 | 224 | 5600 | Weil-Mclain
Weil-Mclain | Series 88 - 988 | 2737 | 2274 | 7358 | 224 | 5600 | Weil-Mclain
Weil-Mclain | Series 88 - 1088R | 2887 | 2399 | 7763 | 247 | 6130 | Weil-Mclain
Weil-Mclain | Series 88 - 1088 | 3082 | 2561 | 8283 | 247 | 6130 | Weil-Mclain
Weil-Mclain | Series 88 - 1188 | 3428 | 2848 | 9213 | 270 | 6695 | Weil-Mclain
Weil-Mclain | Series 88 - 1288 | 3773 | 3135 | 10147 | 293 | 7260 | Weil-Mclain
Weil-Mclain | Series 88 - 1388 | 4119 | 3422 | 11071 | 316 | 7890 | Weil-Mclain
Weil-Mclain | Series 88 - 1488 | 4464 | 3709 | 12000 | 339 | 8410 | Weil-Mclain
Weil-Mclain | Series 88 - 1588 | 4809 | 3996 | 12925 | 362 | 9005 | Weil-Mclain
Weil-Mclain | Series 88 - 1688R | 4979 | 4137 | 13383 | 385 | 9525 | Weil-Mclain
Weil-Mclain | Series 88 - 1688 | 5155 | 4283 | 13854 | 385 | 9525 | Weil-Mclain
Weil-Mclain | Series 88 - 1788 | 5494 | 4570 | 14783 | 408 | 9780 | Weil-Mclain
Weil-Mclain | Series 88 - 1888 | 5845 | 4857 | 15713 | 431 | 10775 | Weil-Mclain
Weil-Mclain | Series 94 - H-1094 | 3247 | 2607 | 8435 | 329.8 | 12320 | Weil-Mclain
Weil-Mclain | Series 94 - H-1194 | 3608 | 2897 | 9372 | 357.5 | 13162 | Weil-Mclain
Weil-Mclain | Series 94 - H-1294 | 3969 | 3187 | 10310 | 385.2 | 14004 | Weil-Mclain
Weil-Mclain | Series 94 - H-1394 | 4330 | 3481 | 11262 | 413 | 14846 | Weil-Mclain
Weil-Mclain | Series 94 - H-1494 | 4691 | 3772 | 12201 | 440.7 | 15688 | Weil-Mclain
Weil-Mclain | Series 94 - H-1594 | 5052 | 4062 | 13140 | 468.4 | 16530 | Weil-Mclain
Weil-Mclain | Series 94 - H-1694 | 5412 | 4351 | 14076 | 496.2 | 17372 | Weil-Mclain
Weil-Mclain | Series 94 - H-1794 | 5773 | 4641 | 15015 | 523.9 | 19014 | Weil-Mclain
Weil-Mclain | Series 94 - H-1894 | 6134 | 4938 | 15974 | 551.6 | 19856 | Weil-Mclain
Weil-Mclain | Series 94 - H-1994 | 6495 | 5228 | 16914 | 579.4 | 20698 | Weil-Mclain
Weil-Mclain | Series 94 - H-2094 | 6856 | 5519 | 17854 | 607.1 | 21540 | Weil-Mclain
Weil-Mclain | Series 94 - H-2194 | 7216 | 5809 | 18792 | 634.8 | 22552 | Weil-Mclain
Weil-Mclain | Series 94 - H-2294 | 7649 | 6157 | 19919 | 662.6 | 23419 | Weil-Mclain
Weil-Mclain | Series 94 - H-2394 | 7938 | 6390 | 20672 | 690.3 | 24286 | Weil-Mclain
Weil-Mclain | Series 94 - H-2494 | 8371 | 6739 | 21799 | 718 | 25153 | Weil-Mclain
Weil-Mclain | Series 94 - H-2594 | 8660 | 6971 | 22552 | 745.8 | 26020 | Weil-Mclain
Weil-Mclain | Series 94 - H-894 | 2540 | 2040 | 6598 | 274.3 | 10636 | Weil-Mclain
Weil-Mclain | Series 94 - H-994 | 2887 | 2318 | 7500 | 302 | 11478 | Weil-Mclain
Weil-Mclain | *EG-30- | 75 | 62 | 196 | 8.4 | 430 | Weil-Mclain
Weil-Mclain | *EG-35- | 100 | 82 | 258 | 8.4 | 430 | Weil-Mclain
Weil-Mclain | *EG-40- | 125 | 103 | 321 | 9.8 | 505 | Weil-Mclain
Weil-Mclain | *EG-45- | 150 | 124 | 388 | 9.8 | 505 | Weil-Mclain
Weil-Mclain | *EG-50- | 175 | 145 | 454 | 11.2 | 585 | Weil-Mclain
Weil-Mclain | *EG-55- | 200 | 166 | 521 | 11.2 | 585 | Weil-Mclain
Weil-Mclain | *EG-65- | 238 | 198 | 621 | 12.6 | 660 | Weil-Mclain
Weil-Mclain | EG-75- | 282 | 234 | 733 | 14 | 735 | Weil-Mclain
Weil-Mclain | EGH-85-S | 315 | 240.24 | 760 | 15.4 | 825 | Weil-Mclain
Weil-Mclain | EGH-95-S | 360 | 275.88 | 868 | 16.8 | 915 | Weil-Mclain
Weil-Mclain | EGH-105-S | 405 | 308.88 | 977 | 18.2 | 1005 | Weil-Mclain
Weil-Mclain | EGH-115-S | 450 | 343.2 | 1085 | 19.6 | 1095 | Weil-Mclain
Weil-Mclain | EGH-125-S | 495 | 378.84 | 1193 | 21 | 1185 | Weil-Mclain
Burnham | V1104H | 837 | 674 | 2106 | 59 | 2103.94 | Burnham
Burnham | V1105H | 1068 | 862 | 2694 | 68 | 2508.88 | Burnham
Burnham | V1106H | 1328 | 1074 | 3358 | 77 | 2918.82 | Burnham
Burnham | V1107H | 1588 | 1288 | 4036 | 87 | 3324.42 | Burnham
Burnham | V1108H | 1876 | 1525 | 4857 | 96 | 3732.36 | Burnham
Burnham | V1109H | 2136 | 1741 | 5604 | 105 | 4146.3 | Burnham
Burnham | V1110H | 2396 | 1958 | 6333 | 115 | 4555.9 | Burnham
Burnham | V1111H | 2656 | 2175 | 7037 | 124 | 4962.84 | Burnham
Burnham | V1112H | 2887 | 2370 | 7668 | 133 | 5372.78 | Burnham
Burnham | V1113H | 3103 | 2546 | 8236 | 143 | 5769.38 | Burnham
Burnham | V1114H | 3392 | 2781 | 8997 | 152 | 6182.32 | Burnham
Burnham | V1115H | 3680 | 3015 | 9754 | 161 | 6599.26 | Burnham
Burnham | V1116H | 3897 | 3191 | 10323 | 171 | 7005.86 | Burnham
Burnham | V1117H | 4186 | 3425 | 11081 | 180 | 7414.8 | Burnham
Burnham | V1118H | 4474 | 3659 | 11835 | 189 | 7820.74 | Burnham
Burnham | V1119H | 4691 | 3833 | 12401 | 199 | 8229.34 | Burnham
Burnham | V1120H | 4979 | 4066 | 13154 | 208 | 8636.28 | Burnham
Burnham | V1121H | 5268 | 4299 | 13908 | 217 | 9051.22 | Burnham
Burnham | V1122H | 5485 | 4473 | 14471 | 227 | 9453.82 | Burnham
Burnham | V1123H | 5773 | 4705 | 15221 | 236 | 9862.76 | Burnham
Burnham | V903A | 447 | 347 | 1083 | 44.5 | 1067.87 | Burnham
Burnham | V904A | 606 | 483 | 1508 | 53 | 1368.98 | Burnham
Burnham | V905A | 808 | 646 | 2021 | 61.5 | 1671.09 | Burnham
Burnham | V906A | 1010 | 808 | 2525 | 70 | 1973.2 | Burnham
Burnham | V907A | 1198 | 959 | 2996 | 78.5 | 2275.31 | Burnham
Burnham | V908A | 1386 | 1110 | 3471 | 87 | 2577.42 | Burnham
Burnham | V909A | 1674 | 1342 | 4225 | 95.5 | 2879.53 | Burnham
Burnham | V910A | 1905 | 1528 | 4867 | 104 | 3180.64 | Burnham
Burnham | V911A | 2136 | 1714 | 5513 | 112.5 | 3482.75 | Burnham
Burnham | V912A | 2367 | 1900 | 6142 | 121 | 3784.86 | Burnham
Burnham | STMX075 | 75 | 62 | 169 | 6.8 | 484 | Burnham
Burnham | STMX100 | 100 | 82 | 258 | 6.8 | 484 | Burnham
Burnham | STMX125 | 125 | 103 | 321 | 9 | 600 | Burnham
Burnham | STMX150 | 150 | 124 | 388 | 9 | 600 | Burnham
Burnham | STMX175 | 175 | 144 | 450 | 11.2 | 729 | Burnham
Burnham | STMX200 | 200 | 165 | 517 | 11.2 | 729 | Burnham
Burnham | STMX250 | 250 | 206 | 646 | 13.2 | 842 | Burnham
Burnham | STMX299 | 299 | 246 | 771 | 15.6 | 881 | Burnham
Burnham | STMX350 | 350 | 284 | 892 | 27.8 | 1008 | Burnham
Burnham | STMX399 | 399 | 323 | 1013 | 20.1 | 1123 | Burnham
Burnham | STMX450 | 450 | 365 | 1142 | 22.2 | 1239 | Burnham
Burnham | STMX500 | 500 | 405 | 1271 | 24.4 | 1354 | Burnham
Burnham | STMX550 | 550 | 446 | 1396 | 26.6 | 1469 | Burnham
Burnham | Independence3 | 62 | 51 | 158 | 5.1 | 350 | Burnham
Burnham | Independence4 | 105 | 87 | 271 | 6.5 | 420 | Burnham
Burnham | Independence5 | 140 | 115 | 358 | 7.9 | 485 | Burnham
Burnham | Independence6 | 175 | 144 | 450 | 9.3 | 555 | Burnham
Burnham | Independence7 | 210 | 173 | 542 | 10.7 | 620 | Burnham
Burnham | Independence8 | 245 | 202 | 633 | 12.1 | 690 | Burnham
Burnham | Independence9 | 280 | 231 | 721 | 13.5 | 760 | Burnham
Peerless | 63-03L | 88.5 | 74 | 233 | 9.3 | 465 | Peerless
Peerless | 63-03 | 118 | 98 | 308 | 9.3 | 465 | Peerless
Peerless | 63-04L | 147.5 | 123 | 383 | 10.8 | 576 | Peerless
Peerless | 63-04 | 177 | 147 | 458 | 10.8 | 576 | Peerless
Peerless | 63-05L | 206.5 | 171 | 533 | 12.4 | 700 | Peerless
Peerless | 63-05 | 236 | 196 | 613 | 12.4 | 700 | Peerless
Peerless | 63-06 | 287.5 | 238 | 746 | 13.9 | 812 | Peerless
Peerless | SC(T)-05 | 404 | 327 | 1022 | 20.4 | 815 | Peerless
Peerless | SC(T)-06 | 505 | 409 | 1278 | 23.52 | 910 | Peerless
Peerless | SC(T)-07 | 577 | 468 | 1463 | 26.64 | 1005 | Peerless
Peerless | SC(T)-08 | 649 | 527 | 1647 | 29.76 | 1100 | Peerless
Peerless | SC(T)-09 | 722 | 586 | 1832 | 32.88 | 1195 | Peerless
Peerless | SC(T)-10 | 794 | 645 | 2016 | 36 | 1280 | Peerless
Peerless | 64-07 | 345 | 274 | 858 | 15.5 | 945 | Peerless
Peerless | 64-08 | 399 | 318 | 996 | 17 | 1081 | Peerless
Peerless | 64-09 | 460 | 367 | 1146 | 18.6 | 1218 | Peerless
Peerless | 64-10 | 517.5 | 413 | 1292 | 20.1 | 1354 | Peerless
Peerless | 64-11 | 575 | 459 | 1433 | 21.7 | 1490 | Peerless
Peerless | 64-12 | 632.5 | 506 | 1583 | 23.2 | 1527 | Peerless
Peerless | TCII-04 | 1143 | 931 | 2908 | 104 | 3185.844 | Peerless
Peerless | TCII-05 | 1458 | 1194 | 3733 | 126 | 3784.498 | Peerless
Peerless | TCII-06 | 1773 | 1458 | 4625 | 148 | 4383.152 | Peerless
Peerless | TCII-07 | 2088 | 1722 | 5542 | 169 | 4981.806 | Peerless
Peerless | TCII-08 | 2403 | 1985 | 6421 | 192 | 5580.46 | Peerless
Peerless | TCII-09 | 2718 | 2249 | 7275 | 214 | 6180.114 | Peerless
Peerless | TCII-10 | 3033 | 2513 | 8129 | 236 | 6793.768 | Peerless
Peerless | TCII-11 | 3348 | 2776 | 8979 | 258 | 7392.422 | Peerless
Peerless | TCII-12 | 3663 | 3040 | 9833 | 280 | 7991.076 | Peerless
Peerless | TCII-13 | 3978 | 3304 | 10688 | 302 | 8600.73 | Peerless
Peerless | TCII-14 | 4293 | 3567 | 11538 | 324 | 9194.384 | Peerless
Peerless | TCII-15 | 4608 | 3851 | 12392 | 346 | 10014.038 | Peerless
Peerless | TCII-16 | 4923 | 4095 | 13246 | 368 | 10653.692 | Peerless
Peerless | TCII-17 | 5238 | 4358 | 14100 | 390 | 11293.346 | Peerless
Peerless | TCII-18 | 5553 | 4622 | 14954 | 412 | 11933 | Peerless
Peerless | LC-04 | 686 | 1708 | 410 | 40.57 | 890 | Peerless
Peerless | LC-05R | 808 | 2029 | 487 | 47.29 | 1080 | Peerless
Peerless | LC-05 | 881 | 2208 | 530 | 47.29 | 1080 | Peerless
Peerless | LC-06 | 1077 | 2713 | 651 | 54.01 | 1270 | Peerless
Peerless | LC-07 | 1273 | 3217 | 772 | 60.73 | 1460 | Peerless
Peerless | LC-08 | 1469 | 3717 | 892 | 67.45 | 1650 | Peerless
Peerless | LC-09 | 1664 | 4250 | 1020 | 74.17 | 1840 | Peerless
Peerless | LC-10 | 1860 | 4804 | 1153 | 80.89 | 2030 | Peerless
Peerless | LC-11 | 2056 | 5367 | 1288 | 87.61 | 2220 | Peerless
Peerless | LC-12 | 2252 | 5917 | 1420 | 94.33 | 2410 | Peerless
Peerless | LCE-13 | 2464 | 6358 | 1526 | 101.05 | 2600 | Peerless
Peerless | LCE-14 | 2657 | 6875 | 1650 | 107.77 | 2790 | Peerless
Peerless | LCE-15 | 2850 | 7388 | 1773 | 114.49 | 2980 | Peerless
Peerless | LCE-16 | 3043 | 7908 | 1898 | 121.21 | 3170 | Peerless
Peerless | LCE-17 | 3236 | 8421 | 2021 | 127.93 | 3360 | Peerless
Peerless | LCE-18 | 3429 | 8938 | 2145 | 134.65 | 3550 | Peerless
Peerless | LCE-19 | 3622 | 9454 | 2269 | 141.37 | 3740 | Peerless
Peerless | LCE-20 | 3815 | 9971 | 2393 | 148.09 | 3930 | Peerless
Peerless | LCE-21 | 4027 | 10533 | 2528 | 154.81 | 4120 | Peerless
Peerless | LCE-22 | 4239 | 11096 | 2663 | 161.53 | 4310 | Peerless
Peerless | LCE-23 | 4451 | 11658 | 2798 | 168.25 | 4500 | Peerless
Peerless | LCE-24 | 4663 | 12217 | 2932 | 174.97 | 4690 | Peerless
Peerless | CC-03 | 375 | 308 | 963 | 33 | 1440.78 | Peerless
Peerless | CC-04 | 520 | 421 | 1316 | 41 | 1780.06 | Peerless
Peerless | CC-05 | 722 | 587 | 1725 | 49 | 2119.34 | Peerless
Peerless | CC-06 | 938 | 762 | 2382 | 56 | 2465.96 | Peerless
Peerless | CC-07 | 1140 | 924 | 2888 | 64 | 2805.24 | Peerless
Peerless | CC-08 | 1342 | 1087 | 3398 | 72 | 3144.52 | Peerless
Peerless | CC-09 | 1559 | 1262 | 3947 | 80 | 3482.8 | Peerless
Peerless | CC-10 | 1761 | 1424 | 4506 | 88 | 3821.08 | Peerless
Peerless | CC-11 | 1963 | 1587 | 5071 | 96 | 4159.36 | Peerless
Peerless | CC-12 | 2165 | 1750 | 5635 | 104 | 4498.64 | Peerless
Peerless | 211A-04 | 630 | 486 | 1521 | 15.1 | 2523 | Peerless
Peerless | 211A-05 | 840 | 664 | 2075 | 18.2 | 2900 | Peerless
Peerless | 211A-06 | 1050 | 830 | 2596 | 21.3 | 3450 | Peerless
Peerless | 211A-07 | 1260 | 995 | 3108 | 24.4 | 3900 | Peerless
Peerless | 211A-08 | 1470 | 1161 | 3629 | 27.5 | 4390 | Peerless
Peerless | 211A-09 | 1680 | 1327 | 4146 | 30.6 | 4875 | Peerless
Peerless | 211A-10 | 1890 | 1493 | 4667 | 33.7 | 5320 | Peerless
Peerless | 211A-11 | 2100 | 1659 | 5183 | 36.8 | 5900 | Peerless
Peerless | 211A-12 | 2310 | 1825 | 5704 | 39.9 | 6370 | Peerless
Peerless | 211A-13 | 2520 | 1958 | 6333 | 43 | 7150 | Peerless
Peerless | 211A-14 | 2730 | 2124 | 6871 | 46.1 | 7700 | Peerless
Peerless | 211A-15 | 2940 | 2290 | 7408 | 49.2 | 8250 | Peerless
Peerless | 211A-16 | 3150 | 2454 | 7938 | 52.3 | 8800 | Peerless
Peerless | 211A-17 | 3360 | 2621 | 8479 | 55.4 | 9350 | Peerless
Peerless | 211A-18 | 3570 | 2785 | 9008 | 58.5 | 9900 | Peerless
Peerless | 211A-19 | 3780 | 2952 | 9550 | 61.75 | 10450 | Peerless
Peerless | 211A-20 | 3990 | 3116 | 10079 | 65 | 11000 | Peerless
Peerless | 211A-21 | 4200 | 3280 | 10613 | 68.25 | 11550 | Peerless
Peerless | 211A-22 | 4410 | 3449 | 11158 | 71.5 | 12100 | Peerless
Peerless | 211A-23 | 4620 | 3599 | 11642 | 74.75 | 12650 | Peerless
Peerless | 211A-24 | 4830 | 3763 | 12175 | 78 | 13200 | Peerless
Peerless | 211A-25 | 5040 | 3931 | 12717 | 81.25 | 13750 | Peerless
Peerless | 211A-26 | 5250 | 4095 | 13246 | 84.5 | 14300 | Peerless
Peerless | 211A-27 | 5460 | 4259 | 13779 | 87.75 | 14850 | Peerless
Peerless | 211A-28 | 5670 | 4428 | 14325 | 91 | 15400 | Peerless
Peerless | 211A-29 | 5880 | 4592 | 14854 | 94.25 | 15950 | Peerless
Peerless | 211A-30 | 6090 | 4756 | 15388 | 97.5 | 16500 | Peerless
Peerless | 211A-31 | 6300 | 4920 | 15917 | 100.75 | 17050 | Peerless
Peerless | 211A-32 | 6510 | 5084 | 16446 | 104 | 17600 | Peerless
Peerless | 211A-33 | 6720 | 5255 | 17000 | 107.25 | 18150 | Peerless
Peerless | 211A-34 | 6930 | 5419 | 17529 | 110.5 | 18700 | Peerless
Peerless | 211A-35 | 7140 | 5583 | 18063 | 113.75 | 19250 | Peerless
Peerless | 211A-36 | 7350 | 5748 | 18596 | 117 | 19800 | Peerless
Peerless | 211A-37 | 7560 | 5904 | 19100 | 120.25 | 20350 | Peerless
Peerless | EC(T)-e-03 | 105 | 92 | 288 | 14.16 | 570 | Peerless
Peerless | EC(T)-e-03 | 140 | 121 | 379 | 14.16 | 570 | Peerless
Peerless | EC(T)-e-04 | 175 | 152 | 475 | 17.28 | 710 | Peerless
Peerless | EC(T)-e-04 | 210 | 181 | 567 | 17.28 | 710 | Peerless
Peerless | EC(T)-e-05 | 245 | 213 | 667 | 20.4 | 840 | Peerless
Peerless | EC(T)-e-05 | 280 | 242 | 758 | 20.4 | 840 | Peerless
Peerless | EC(T)-05† | 336 | 279 | 874 | 20.4 | 840 | Peerless
Peerless | EC(T)-e-06† | 308 | 259 | 811 | 23.52 | 990 | Peerless
Peerless | EC(T)-e-06† | 336 | 282 | 883 | 23.52 | 990 | Peerless
Peerless | EC(T)-06† | 385 | 321 | 1006 | 23.52 | 990 | Peerless
Peerless | EC(T)-06† | 420 | 347 | 1087 | 23.52 | 990 | Peerless
Peerless | WBV-e-03-085-S | 119 | 104 | 325 | 12 | 584 | Peerless
Peerless | WBV-e-03-105-S | 147 | 127 | 396 | 12 | 584 | Peerless
Peerless | WBV-e-04-125-S | 175 | 152 | 475 | 14.87 | 685 | Peerless
Peerless | WBV-e-04-150-S | 210 | 180 | 563 | 14.87 | 685 | Peerless
Peerless | 63-03L | 88.5 | 74 | 233 | 9.3 | 465 | Peerless
Peerless | 63-03 | 118 | 98 | 308 | 9.3 | 465 | Peerless
Peerless | 63-04L | 147.5 | 123 | 383 | 10.8 | 576 | Peerless
Peerless | 63-04 | 177 | 147 | 458 | 10.8 | 576 | Peerless
Peerless | 63-05L | 206.5 | 171 | 533 | 12.4 | 700 | Peerless
Peerless | 63-05 | 236 | 196 | 613 | 12.4 | 700 | Peerless
Peerless | 63-06 | 287.5 | 238 | 746 | 13.9 | 812 | Peerless
Peerless | 63-x-03 | 100 | 82 | 258 | 7 | 480 | Peerless
Peerless | 63-x-04 | 150 | 124 | 388 | 9 | 595 | Peerless
Peerless | 63-x-05 | 200 | 165 | 517 | 11 | 725 | Peerless
Peerless | 63-x-06 | 250 | 206 | 646 | 13 | 840 | Peerless
Green Mountain | GMGS-75 | 75 | 62 | 195 | 1.8 | 297 | Green Mountain
Green Mountain | GMGS-112 | 112.5 | 91 | 283 | 2.7 | 368 | Green Mountain
Green Mountain | GMGS-150 | 150 | 122 | 383 | 3.7 | 440 | Green Mountain
Green Mountain | GMGS-187 | 187.5 | 153 | 479 | 4.7 | 512 | Green Mountain
Green Mountain | GMGS-225 | 225 | 183 | 570 | 5.7 | 584 | Green Mountain
Green Mountain | GMGS-262 | 262.5 | 214 | 670 | 6.7 | 659 | Green Mountain
Green Mountain | GMGS-299 | 299 | 245 | 766 | 7.7 | 736 | Green Mountain

## Calculations (hidden)
Schd 40 Pipe stats
| ID(in) | Area(ft2) | BTU/ft @ 210°F | linear ft3/ft | Lb/ft | List generator
1/2 | 0.662 | 0.0023903 | 82 | 0.0013657 | 0.851
3/4 | 0.824 | 0.0037032 | 100 | 0.0030671 | 1.131 | 1
1 | 1.049 | 0.0060018 | 123 | 0.0054572 | 1.679 | 2
1 1/4 | 1.38 | 0.010387 | 152 | 0.0085069 | 2.273 | 3
1 1/2 | 1.61 | 0.014138 | 173 | 0.012269 | 2.718 | 4
2 | 2.067 | 0.023303 | 212 | 0.021817 | 3.653 | 5
2 1/2 | 2.469 | 0.033248 | 252 | 0.034086 | 5.793 | 6
3 | 3.068 | 0.051338 | 303 | 0.049074 | 7.576 | 7
3 1/2 | 3.548 | 0.068659 | 342 | 0.068171 | 9.183 | 8
4 | 4.026 | 0.088405 | 381 | 0.087269 | 10.79 | 9
5 | 5.047 | 0.13893 | 464 | 0.13634 | 14.882 | 10
6 | 6.065 | 0.20063 | 546 | 0.19635 | 18.974

## SteamProperties (hidden)
Gauge Pressure | Temperature | Specific Volume Saturated Vapor | Enthalpy
(psig) | (oF) | (ft3/lb) | Saturated Liquid | Evaporated | Saturated Vapor
PSI | F | ft3/lb | (Btu/lb) | (Btu/lb) | (Btu/lb)
-2.456 | 203 | 31.8 | 171 | 976 | 1147 |  | 0.039683 | 1 | 0.92016
0 | 212 | 26.8 | 180 | 970 | 1150 |  | 0.042553 | 2 | 2.0884
1 | 215 | 25.2 | 183 | 968 | 1151
2 | 219 | 23.5 | 187 | 966 | 1153
3 | 222 | 22.3 | 190 | 964 | 1154
4 | 224 | 21.4 | 192 | 962 | 1154
5 | 227 | 20.1 | 195 | 960 | 1155
6 | 230 | 19.4 | 198 | 959 | 1157
Pipe Size | BTU/linear ft | [7 empty] | Branch Supply List | Supply Line List
| 100°F | 120°F | 150°F | 180°F | 210°F | 240°F | in3/ft | ID(in)
1/2 | 13 | 22 | 40 | 60 | 82 | 106 | 2.36 | 0.622 | AA | A
3/4 | 15 | 27 | 50 | 74 | 100 | 131 | 5.3 | 0.824 | BB | B
1 | 19 | 34 | 61 | 90 | 123 | 160 | 9.43 | 1.049 | CC | C
1 1/4 | 23 | 42 | 75 | 111 | 152 | 198 | 14.7 | 1.38 | DD | D
1 1/2 | 27 | 48 | 85 | 126 | 173 | 224 | 21.2 | 1.61 | EE | E
2 | 33 | 59 | 104 | 154 | 212 | 275 | 37.7 | 2.067 | FF | F
2 1/2 | 39 | 70 | 123 | 184 | 252 | 327 | 58.9 | 2.469 | GG | G
3 | 46 | 84 | 148 | 221 | 303 | 393 | 84.8 | 3.068 | HH | H
3 1/2 | 52 | 95 | 168 | 250 | 342 | 444 | 117.8 | 3.548 | II | I
4 | 59 | 106 | 187 | 278 | 381 | 496 | 150.8 | 4.026 | JJ
5 | 71 | 129 | 227 | 339 | 464 | 603 | 235.6 | 5.047 | KK
6 | 84 | 151 | 267 | 398 | 546 | 709 | 339.3 | 6.065 | LL
8 | 107 | 194 | 341 | 509 | 697 | 906
10 | 132 | 238 | 420 | 626 | 857 | 1114
12 | 154 | 279 | 491 | 732 | 1003 | 1305
14 | 181 | 326 | 575 | 856 | 1173 | 1527
16 | 203 | 366 | 644 | 960 | 1314 | 1711
18 | 214 | 385 | 678 | 1011 | 1385 | 1802
20 | 236 | 426 | 748 | 1115 | 1529 | 1990
Pressur Drop