## Sheet1
FLOW |  |  |  | QUANTITY | Cv |  | resistance | Ft of head
10gpm
BOILER |  |  |  | 2' |  |  |  | 2'
AIR SCOOP | 1 1/4" |  | 53.5 |  | 53.5 |  |  | .08'
573 ZONE VALVE |  |  | 7.2 |  | 7.2 |  |  | 4.46'
1 1/4 PIPE |  |  |  | 130' |  |  | 1.76/100 | 2.29'
FITTINGS |  |  |  | 50%of pipe |  |  |  | 1.145'
MONOFLOW TEE |  | single tees @3000 millinches each | each | 5 |  |  | 1500mi | 1.25 feet
|  | double tees @7000millinches each |  | 4 |  |  | 2800mi | 2.33 feet
[6 empty] | Toyal ffe of head |  | 13.56 feet
Boiler is 120,000 input/ output 96000/10,000=9.6 gpm | [6 empty] | Circulator needed would be 10gpm @14' of head