## Summary
Assumptions:
Design Temperature, F | 9
Design Heating Load, BTU/hr | 20000
"Break-Even" Temperature, F | 60
|  |  | Annual heating load, BTU |  | HP COP, weighted average | Annual HP Heat Contribution, BTU | Short Cycle Loss % | Short Cycle Loss, kWh | Annual HP electricity usage, kWh | Annual Supplemental Heat Contribution, BTU | Annual Total electricity usage, kWh | Percent HP | Percent Supplemental | Annual Degree-Days
Totals | 5739.6688 |  | 46527500.2875 |  | 2.8179 | 43426936.1871 | 2.649% | 128.1958 | 3802.2854 | 3100564.1004 | 4839.2045 | 81.22% | 18.78% | 6139.3112
Outdoor Temperature, F | Annual hours at this temperature | Heating load at this temperature, BTU/hr | Annual heating load, BTU | HP Capacity at this temperature, BTU/hr | HP COP at this temperature | Annual HP Heat Contribution, BTU | Short Cycle Loss % | Short Cycle Loss, kWh | Annual HP electricity usage, kWh | Annual Supplemental Heat Contribution, BTU | Annual Total electricity usage, kWh | Percent HP | Percent Supplemental | Annual Degree-Days
-1 | 12.0003 | 23921.5686 | 287064.8237 | 10830 | 2.167 | 129962.7164 | 0% | 0 | 17.5772 | 157102.1072 | 63.6212 | 27.63% | 72.37% | 33.0007 | -1
0 | 12.0002 | 23529.4118 | 282356.9412 | 10975 | 2.1875 | 131701.8658 | 0% | 0 | 17.6455 | 150655.0755 | 61.8 | 28.55% | 71.45% | 32.5005 | 0
1 | 16.0002 | 23137.2549 | 370200.0785 | 11120 | 2.208 | 177921.9225 | 0% | 0 | 23.6168 | 192278.156 | 79.9703 | 29.53% | 70.47% | 42.6671 | 1
2 | 16 | 22745.098 | 363922.5686 | 11265 | 2.2285 | 180240.4953 | 0% | 0 | 23.7045 | 183682.0734 | 77.5386 | 30.57% | 69.43% | 42.0001 | 2
3 | 17.0007 | 22352.9412 | 380016.0007 | 11410 | 2.249 | 193978.1675 | 0% | 0 | 25.2787 | 186037.8332 | 79.8032 | 31.68% | 68.32% | 43.9185 | 3
4 | 11.0004 | 21960.7843 | 241576.6277 | 11555 | 2.2695 | 127109.2095 | 0% | 0 | 16.4149 | 114467.4183 | 49.9634 | 32.85% | 67.15% | 27.9593 | 4
5 | 16.0005 | 21568.6275 | 345108.0395 | 11700 | 2.29 | 187205.4247 | 0% | 0 | 23.9593 | 157902.6148 | 70.2379 | 34.11% | 65.89% | 40.0012 | 5
6 | 11.0002 | 21176.4706 | 232946.1766 | 11983.3333 | 2.3217 | 131819.4961 | 0% | 0 | 16.6407 | 101126.6805 | 46.2792 | 35.96% | 64.04% | 27.0422 | 6
7 | 19.0002 | 20784.3137 | 394906.9609 | 12266.6667 | 2.3533 | 233069.6177 | 0% | 0 | 29.0264 | 161837.3432 | 76.4582 | 37.96% | 62.04% | 45.9172 | 7
8 | 24.0001 | 20392.1569 | 489414.7647 | 12550 | 2.385 | 301201.8463 | 0% | 0 | 37.0135 | 188212.9184 | 92.1756 | 40.16% | 59.84% | 57.0003 | 8
9 | 27 | 20000 | 540000 | 12833.3333 | 2.4167 | 346500 | 0% | 0 | 42.0221 | 193500 | 98.7337 | 42.56% | 57.44% | 63 | 9
10 | 35.0015 | 19607.8431 | 686303.5111 | 13116.6667 | 2.4483 | 459102.7337 | 0% | 0 | 54.9579 | 227200.7773 | 121.5467 | 45.22% | 54.78% | 80.2117 | 10
11 | 39.0014 | 19215.6863 | 749437.7656 | 13400 | 2.48 | 522618.1317 | 0% | 0 | 61.7623 | 226819.634 | 128.2394 | 48.16% | 51.84% | 87.753 | 11
12 | 37.001 | 18823.5294 | 696489.5888 | 13683.3333 | 2.5117 | 506297.1453 | 0% | 0 | 59.0792 | 190192.4434 | 114.8214 | 51.45% | 48.55% | 81.7106 | 12
13 | 32.0006 | 18431.3725 | 589814.9218 | 13966.6667 | 2.5433 | 446941.6689 | 0% | 0 | 51.5037 | 142873.2529 | 93.3775 | 55.16% | 44.84% | 69.3346 | 13
14 | 39.0004 | 18039.2157 | 703537.4119 | 14250 | 2.575 | 555756.3196 | 0% | 0 | 63.2555 | 147781.0922 | 106.5676 | 59.36% | 40.64% | 82.8759 | 14
15 | 28.0001 | 17647.0588 | 494118.6471 | 14533.3333 | 2.6067 | 406934.1569 | 0% | 0 | 45.7541 | 87184.4902 | 71.3064 | 64.17% | 35.83% | 58.3335 | 15
16 | 40.0021 | 17254.902 | 690232.0803 | 14816.6667 | 2.6383 | 592697.5812 | 0% | 0 | 65.8407 | 97534.4991 | 94.4264 | 69.73% | 30.27% | 81.6709 | 16
17 | 57.0025 | 16862.7451 | 961218.4724 | 15100 | 2.67 | 860737.6112 | 0% | 0 | 94.4823 | 100480.8612 | 123.9316 | 76.24% | 23.76% | 114.005 | 17
18 | 60.0021 | 16470.5882 | 988270.2954 | 15376.6667 | 2.7007 | 922632.6766 | 0% | 0 | 100.1265 | 65637.6188 | 119.3637 | 83.88% | 16.12% | 117.5042 | 18
19 | 66.0017 | 16078.4314 | 1061204.4713 | 15653.3333 | 2.7313 | 1033147.2604 | 0% | 0 | 110.8609 | 28057.2109 | 119.084 | 93.09% | 6.905% | 126.5033 | 19
20 | 67.0011 | 15686.2745 | 1050998.3925 | 15930 | 2.7732 | 1050998.3925 | 0% | 0 | 111.0729 | 0 | 111.0729 | 100% | 0% | 125.6272 | 20
21 | 62.0005 | 15294.1176 | 948242.2942 | 16206.6667 | 2.8347 | 948242.2942 | 0% | 0 | 98.0403 | 0 | 98.0403 | 100% | 0% | 113.6675 | 21
22 | 45.0029 | 14901.9608 | 670631.2381 | 16483.3333 | 2.8962 | 670631.2381 | 0% | 0 | 67.866 | 0 | 67.866 | 100% | 0% | 80.6302 | 22
23 | 60.0033 | 14509.8039 | 870636.238 | 16760 | 2.9576 | 870636.238 | 0% | 0 | 86.2749 | 0 | 86.2749 | 100% | 0% | 105.0058 | 23
24 | 51.0023 | 14117.6471 | 720033.0015 | 17036.6667 | 3.0191 | 720033.0015 | 0% | 0 | 69.8983 | 0 | 69.8983 | 100% | 0% | 87.129 | 24
25 | 69.0024 | 13725.4902 | 947091.8247 | 17313.3333 | 3.0806 | 947091.8247 | 0% | 0 | 90.1058 | 0 | 90.1058 | 100% | 0% | 115.004 | 25
26 | 90.0023 | 13333.3333 | 1200030.0008 | 17590 | 3.142 | 1200030.0008 | 0% | 0 | 111.9367 | 0 | 111.9367 | 100% | 0% | 146.2537 | 26
27 | 90.0012 | 12941.1765 | 1164720.8826 | 17866.6667 | 3.2035 | 1164720.8826 | 0% | 0 | 106.5586 | 0 | 106.5586 | 100% | 0% | 142.5018 | 27
28 | 103.0002 | 12549.0196 | 1292551.0196 | 18143.3333 | 3.264 | 1292551.0196 | 0.03344% | 0.038808 | 116.0616 | 0 | 116.1004 | 99.97% | 0.03343% | 158.7919 | 28
29 | 101.0072 | 12156.8627 | 1227930.1434 | 18420 | 3.318 | 1227930.1434 | 0.3013% | 0.32679 | 108.4647 | 0 | 108.7915 | 99.7% | 0.3004% | 151.5107 | 29
30 | 101.006 | 11764.7059 | 1188306.2984 | 18696.6667 | 3.372 | 1188306.2984 | 0.587% | 0.60628 | 103.2837 | 0 | 103.89 | 99.42% | 0.5836% | 147.3005 | 30
31 | 74.0035 | 11372.549 | 841608.6294 | 18973.3333 | 3.426 | 841608.6294 | 0.8924% | 0.64251 | 71.9969 | 0 | 72.6394 | 99.12% | 0.8845% | 104.8383 | 31
32 | 105.0037 | 10980.3922 | 1152982.1779 | 19250 | 3.48 | 1152982.1779 | 1.22% | 1.1843 | 97.1034 | 0 | 98.2877 | 98.8% | 1.205% | 144.3801 | 32
33 | 76.0016 | 10588.2353 | 804722.8827 | 19526.6667 | 3.534 | 804722.8827 | 1.571% | 1.0485 | 66.7376 | 0 | 67.7862 | 98.45% | 1.547% | 101.3355 | 33
34 | 114.0008 | 10196.0784 | 1162360.9412 | 19803.3333 | 3.588 | 1162360.9412 | 1.95% | 1.8511 | 94.9466 | 0 | 96.7977 | 98.09% | 1.912% | 147.251 | 34
35 | 139.0131 | 9803.9216 | 1362873.1101 | 20080 | 3.642 | 1362873.1101 | 2.358% | 2.5866 | 109.6747 | 0 | 112.2613 | 97.7% | 2.304% | 173.7663 | 35
36 | 140.0114 | 9411.7647 | 1317754.0675 | 20356.6667 | 3.696 | 1317754.0675 | 2.801% | 2.9272 | 104.4945 | 0 | 107.4216 | 97.28% | 2.725% | 169.1804 | 36
37 | 155.0104 | 9019.6078 | 1398133.222 | 20633.3333 | 3.75 | 1398133.222 | 3.283% | 3.587 | 109.2718 | 0 | 112.8588 | 96.82% | 3.178% | 180.8455 | 37
38 | 159.0082 | 8627.451 | 1371835.7096 | 20910 | 3.804 | 1371835.7096 | 3.808% | 4.0246 | 105.6945 | 0 | 109.7191 | 96.33% | 3.668% | 178.8843 | 38
39 | 144.0051 | 8235.2941 | 1185924.3544 | 21186.6667 | 3.858 | 1185924.3544 | 4.383% | 3.9486 | 90.0919 | 0 | 94.0405 | 95.8% | 4.199% | 156.0055 | 39
40 | 106.0018 | 7843.1373 | 831386.5493 | 21463.3333 | 3.912 | 831386.5493 | 5.015% | 3.124 | 62.2867 | 0 | 65.4107 | 95.22% | 4.776% | 110.4185 | 40
41 | 155.0203 | 7450.9804 | 1155052.9807 | 21740 | 3.966 | 1155052.9807 | 5.715% | 4.8779 | 85.3572 | 0 | 90.2351 | 94.59% | 5.406% | 155.0203 | 41
42 | 109.0126 | 7058.8235 | 769500.7751 | 22016.6667 | 4.02 | 769500.7751 | 6.492% | 3.6419 | 56.1014 | 0 | 59.7434 | 93.9% | 6.096% | 104.4704 | 42
43 | 153.0153 | 6666.6667 | 1020102.0102 | 22293.3333 | 4.074 | 1020102.0102 | 7.36% | 5.4012 | 73.3861 | 0 | 78.7873 | 93.14% | 6.855% | 140.264 | 43
44 | 193.0156 | 6274.5098 | 1211078.4001 | 22570 | 4.128 | 1211078.4001 | 8.337% | 7.1685 | 85.9852 | 0 | 93.1536 | 92.3% | 7.695% | 168.8887 | 44
45 | 197.0117 | 5882.3529 | 1158892.5336 | 22846.6667 | 4.182 | 1158892.5336 | 9.444% | 7.6702 | 81.2176 | 0 | 88.8878 | 91.37% | 8.629% | 164.1764 | 45
46 | 195.0069 | 5490.1961 | 1070626.2367 | 23123.3333 | 4.236 | 1070626.2367 | 10.71% | 7.9329 | 74.0752 | 0 | 82.0081 | 90.33% | 9.673% | 154.3805 | 46
47 | 198.0014 | 5098.0392 | 1009418.7648 | 23400 | 4.29 | 1009418.7648 | 12.17% | 8.3921 | 68.9612 | 0 | 77.3533 | 89.15% | 10.85% | 148.501 | 47
48 | 182.034 | 4705.8824 | 856630.6182 | 23676.6667 | 4.344 | 856630.6182 | 13.87% | 8.0177 | 57.7956 | 0 | 65.8133 | 87.82% | 12.18% | 128.9408 | 48
49 | 125.0209 | 4313.7255 | 539305.7014 | 23953.3333 | 4.398 | 539305.7014 | 15.89% | 5.7091 | 35.9394 | 0 | 41.6485 | 86.29% | 13.71% | 83.3472 | 49
50 | 166.024 | 3921.5686 | 651074.4058 | 24230 | 4.452 | 651074.4058 | 18.3% | 7.8441 | 42.8614 | 0 | 50.7055 | 84.53% | 15.47% | 103.765 | 50
51 | 123.0142 | 3529.4118 | 434167.6529 | 24506.6667 | 4.506 | 434167.6529 | 20% | 5.6479 | 28.2395 | 0 | 33.8874 | 83.33% | 16.67% | 71.7583 | 51
52 | 169.0137 | 3137.2549 | 530239.0819 | 24783.3333 | 4.56 | 530239.0819 | 20% | 6.816 | 34.0799 | 0 | 40.8958 | 83.33% | 16.67% | 91.5491 | 52
53 | 185.0066 | 2745.098 | 507861.1379 | 25060 | 4.614 | 507861.1379 | 20% | 6.4519 | 32.2596 | 0 | 38.7115 | 83.33% | 16.67% | 92.5033 | 53
54 | 183.0731 | 2352.9412 | 430760.3041 | 25336.6667 | 4.668 | 430760.3041 | 20% | 5.4091 | 27.0455 | 0 | 32.4547 | 83.33% | 16.67% | 83.9085 | 54
55 | 174.0694 | 1960.7843 | 341312.525 | 25613.3333 | 4.722 | 341312.525 | 20% | 4.2369 | 21.1845 | 0 | 25.4213 | 83.33% | 16.67% | 72.5289 | 55
56 | 176.0702 | 1568.6275 | 276188.4754 | 25890 | 4.776 | 276188.4754 | 20% | 3.3897 | 16.9485 | 0 | 20.3382 | 83.33% | 16.67% | 66.0263 | 56
57 | 144.057 | 1176.4706 | 169478.7915 | 26166.6667 | 4.83 | 169478.7915 | 20% | 2.0568 | 10.2839 | 0 | 12.3407 | 83.33% | 16.67% | 48.019 | 57
58 | 102.0408 | 784.3137 | 80032.0128 | 26443.3333 | 4.884 | 80032.0128 | 20% | 0.96053 | 4.8026 | 0 | 5.7632 | 83.33% | 16.67% | 29.7619 | 58
59 | 145.0561 | 392.1569 | 56884.7539 | 26720 | 4.938 | 56884.7539 | 20% | 0.67525 | 3.3763 | 0 | 4.0515 | 83.33% | 16.67% | 36.264 | 59
60 | 0 | 0 | 0 | 26996.6667 | 4.992 | 0 | 20% | 0 | 0 | 0 | 0 | 0% | 100% | 0 | 60
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Data from Neep.org
Outdoor Temperature (°F) | Supplemental Heat (low) | Supplemental Heat (high) | Modulating Heat Pump (low) | Modulating Heat Pump (high) | Potential Low-Load Cycling | Design Temperature | Heating Max. Cap. | Heating Min. Cap. | Heating Load Line (Btu/h) | Annual Load x Hours (Btu/yr) | Heating Rated Cap.
-1 | 10830 | 23921 | 10830 | 10830 |  |  |  |  | 23921 | 287058
0 | 10975 | 23529 | 10975 | 10975 |  |  |  |  | 23529 | 282352
1 | 11120 | 23137 | 11120 | 11120 |  |  |  |  | 23137 | 370196
2 | 11265 | 22745 | 11265 | 11265 |  |  |  |  | 22745 | 363921
3 | 11410 | 22352 | 11410 | 11410 |  |  |  |  | 22352 | 380000
4 | 11555 | 21960 | 11555 | 11555 |  |  |  |  | 21960 | 241568
5 | 11700 | 21568 | 11700 | 11700 |  |  | 11700 | 11700 | 21568 | 345098 | 11700
6 | 11983 | 21176 | 11983 | 11983 |  |  |  |  | 21176 | 232941
7 | 12266 | 20784 | 12266 | 12266 |  |  |  |  | 20784 | 394901
8 | 12550 | 20392 | 12550 | 12550 |  |  |  |  | 20392 | 489411
9 | 12833 | 20000 | 12833 | 12833 |  | 0 |  |  | 20000 | 540000
10 | 13116 | 19607 | 13116 | 13116 |  |  |  |  | 19607 | 686274
11 | 13400 | 19215 | 13400 | 13400 |  |  |  |  | 19215 | 749411
12 | 13683 | 18823 | 13683 | 13683 |  |  |  |  | 18823 | 696470
13 | 13966 | 18431 | 13966 | 13966 |  |  |  |  | 18431 | 589803
14 | 14250 | 18039 | 14250 | 14250 |  |  |  |  | 18039 | 703529
15 | 14533 | 17647 | 14533 | 14533 |  |  |  |  | 17647 | 494117
16 | 14816 | 17254 | 14816 | 14816 |  |  |  |  | 17254 | 690196
17 | 15100 | 16862 | 15100 | 15100 |  |  | 15100 | 15100 | 16862 | 961176 | 15100
18 | 15376 | 16470 | 14870 | 15376 |  |  |  |  | 16470 | 988235
19 | 15653 | 16078 | 14640 | 15653 |  |  |  |  | 16078 | 1061176
20 |  |  | 14410 | 15930 |  |  |  |  | 15686 | 1050980
21 |  |  | 14180 | 16206 |  |  |  |  | 15294 | 948235
22 |  |  | 13950 | 16483 |  |  |  |  | 14901 | 670588
23 |  |  | 13720 | 16760 |  |  |  |  | 14509 | 870588
24 |  |  | 13490 | 17036 |  |  |  |  | 14117 | 720000
25 |  |  | 13260 | 17313 |  |  |  |  | 13725 | 947058
26 |  |  | 13030 | 17590 |  |  |  |  | 13333 | 1200000
27 |  |  | 12800 | 17866 | 12941 |  |  |  | 12941 | 1164705
28 |  |  | 12570 | 18143 | 12549 |  |  |  | 12549 | 1292549
29 |  |  | 12340 | 18420 | 12156 |  |  |  | 12156 | 1227843
30 |  |  | 12110 | 18696 | 11764 |  |  |  | 11764 | 1188235
31 |  |  | 11880 | 18973 | 11372 |  |  |  | 11372 | 841568
32 |  |  | 11650 | 19250 | 10980 |  |  |  | 10980 | 1152941
33 |  |  | 11420 | 19526 | 10588 |  |  |  | 10588 | 804705
34 |  |  | 11190 | 19803 | 10196 |  |  |  | 10196 | 1162352
35 |  |  | 10960 | 20080 | 9803 |  |  |  | 9803 | 1362745
36 |  |  | 10730 | 20356 | 9411 |  |  |  | 9411 | 1317647
37 |  |  | 10500 | 20633 | 9019 |  |  |  | 9019 | 1398039
38 |  |  | 10270 | 20910 | 8627 |  |  |  | 8627 | 1371764
39 |  |  | 10040 | 21186 | 8235 |  |  |  | 8235 | 1185882
40 |  |  | 9810 | 21463 | 7843 |  |  |  | 7843 | 831372
41 |  |  | 9580 | 21740 | 7450 |  |  |  | 7450 | 1154901
42 |  |  | 9350 | 22016 | 7058 |  |  |  | 7058 | 769411
43 |  |  | 9120 | 22293 | 6666 |  |  |  | 6666 | 1020000
44 |  |  | 8890 | 22570 | 6274 |  |  |  | 6274 | 1210980
45 |  |  | 8660 | 22846 | 5882 |  |  |  | 5882 | 1158823
46 |  |  | 8430 | 23123 | 5490 |  |  |  | 5490 | 1070588
47 |  |  | 8200 | 23400 | 5098 |  | 23400 | 8200 | 5098 | 1009411 | 23400
48 |  |  | 7970 | 23676 | 4705 |  |  |  | 4705 | 856470
49 |  |  | 7740 | 23953 | 4313 |  |  |  | 4313 | 539215
50 |  |  | 7510 | 24230 | 3921 |  |  |  | 3921 | 650980
51 |  |  | 7280 | 24506 | 3529 |  |  |  | 3529 | 434117
52 |  |  | 7050 | 24783 | 3137 |  |  |  | 3137 | 530196
53 |  |  | 6820 | 25060 | 2745 |  |  |  | 2745 | 507843
54 |  |  | 6590 | 25336 | 2352 |  |  |  | 2352 | 430588
55 |  |  | 6360 | 25613 | 1960 |  |  |  | 1960 | 341176
56 |  |  | 6130 | 25890 | 1568 |  |  |  | 1568 | 276078
57 |  |  | 5900 | 26166 | 1176 |  |  |  | 1176 | 169411
58 |  |  | 5670 | 26443 | 784 |  |  |  | 784 | 80000
59 |  |  | 5440 | 26720 | 392 |  |  |  | 392 | 56862
60 |  |  | 5210 | 26996 | 0 |  |  |  | 0 | 0
54000

## Heat Pump Performance Curve
https://ashp.neep.org/#!/product/34583/7/25000/95/7500/0///0 | [7 empty] | (paste from NEEP.org website) |  |  |  | Min | Rated | Max
| Temp |  |  | Min Output | COP @ min output | Max Output | Cop @ max output | Heating | 47℉ | 70℉ | Btu/h⁺ | 8200 | 23400 | 23400
Heating | 47 |  |  | 8200 | 4.29 | 23400 | 3.59 | kW | 0.56 | 1.91 | 1.91
Heating | 17 |  |  | 15100 | 2.67 | 15100 | 2.67 | COP | 4.29 | 3.59 | 3.59
Heating | 5 |  |  | 11700 | 2.29 | 11700 | 2.29 | Heating | 17℉ | 70℉ | Btu/h⁺ | 15100 | 15100 | 15100
Heating | -15 |  |  | 8800 | 1.88 | 8800 | 1.88 | kW | 1.66 | 1.66 | 1.66
[8 empty] | COP | 2.67 | 2.67 | 2.67
[8 empty] | Heating | 5℉ | 70℉ | Btu/h⁺ | 11700 | 11700 | 11700
Temperature | Min Output | COP @ min output | Max Output | Cop @ max output | Load | COP @ Load |  | kW | 1.5 | 1.5 | 1.5
-1 | 10830 | 2.167 | 10830 | 2.167 | 23921.5686 | 2.167 |  | COP | 2.29 | 2.29 | 2.29
0 | 10975 | 2.1875 | 10975 | 2.1875 | 23529.4118 | 2.1875 |  | Heating | -15℉ | 70℉ | Btu/h⁺ | 8800 | - | 8800
1 | 11120 | 2.208 | 11120 | 2.208 | 23137.2549 | 2.208 |  | kW | 1.37 | - | 1.37
2 | 11265 | 2.2285 | 11265 | 2.2285 | 22745.098 | 2.2285 |  | COP | 1.88 | - | 1.88
3 | 11410 | 2.249 | 11410 | 2.249 | 22352.9412 | 2.249
4 | 11555 | 2.2695 | 11555 | 2.2695 | 21960.7843 | 2.2695
5 | 11700 | 2.29 | 11700 | 2.29 | 21568.6275 | 2.29
6 | 11983.3333 | 2.3217 | 11983.3333 | 2.3217 | 21176.4706 | 2.3217
7 | 12266.6667 | 2.3533 | 12266.6667 | 2.3533 | 20784.3137 | 2.3533
8 | 12550 | 2.385 | 12550 | 2.385 | 20392.1569 | 2.385
9 | 12833.3333 | 2.4167 | 12833.3333 | 2.4167 | 20000 | 2.4167
10 | 13116.6667 | 2.4483 | 13116.6667 | 2.4483 | 19607.8431 | 2.4483
11 | 13400 | 2.48 | 13400 | 2.48 | 19215.6863 | 2.48
12 | 13683.3333 | 2.5117 | 13683.3333 | 2.5117 | 18823.5294 | 2.5117
13 | 13966.6667 | 2.5433 | 13966.6667 | 2.5433 | 18431.3725 | 2.5433
14 | 14250 | 2.575 | 14250 | 2.575 | 18039.2157 | 2.575
15 | 14533.3333 | 2.6067 | 14533.3333 | 2.6067 | 17647.0588 | 2.6067
16 | 14816.6667 | 2.6383 | 14816.6667 | 2.6383 | 17254.902 | 2.6383
17 | 15100 | 2.67 | 15100 | 2.67 | 16862.7451 | 2.67
18 | 14870 | 2.724 | 15376.6667 | 2.7007 | 16470.5882 | 2.7007
19 | 14640 | 2.778 | 15653.3333 | 2.7313 | 16078.4314 | 2.7313
20 | 14410 | 2.832 | 15930 | 2.762 | 15686.2745 | 2.7732
21 | 14180 | 2.886 | 16206.6667 | 2.7927 | 15294.1176 | 2.8347
22 | 13950 | 2.94 | 16483.3333 | 2.8233 | 14901.9608 | 2.8962
23 | 13720 | 2.994 | 16760 | 2.854 | 14509.8039 | 2.9576
24 | 13490 | 3.048 | 17036.6667 | 2.8847 | 14117.6471 | 3.0191
25 | 13260 | 3.102 | 17313.3333 | 2.9153 | 13725.4902 | 3.0806
26 | 13030 | 3.156 | 17590 | 2.946 | 13333.3333 | 3.142
27 | 12800 | 3.21 | 17866.6667 | 2.9767 | 12941.1765 | 3.2035
28 | 12570 | 3.264 | 18143.3333 | 3.0073 | 12549.0196 | 3.264
29 | 12340 | 3.318 | 18420 | 3.038 | 12156.8627 | 3.318
30 | 12110 | 3.372 | 18696.6667 | 3.0687 | 11764.7059 | 3.372
31 | 11880 | 3.426 | 18973.3333 | 3.0993 | 11372.549 | 3.426
32 | 11650 | 3.48 | 19250 | 3.13 | 10980.3922 | 3.48
33 | 11420 | 3.534 | 19526.6667 | 3.1607 | 10588.2353 | 3.534
34 | 11190 | 3.588 | 19803.3333 | 3.1913 | 10196.0784 | 3.588
35 | 10960 | 3.642 | 20080 | 3.222 | 9803.9216 | 3.642
36 | 10730 | 3.696 | 20356.6667 | 3.2527 | 9411.7647 | 3.696
37 | 10500 | 3.75 | 20633.3333 | 3.2833 | 9019.6078 | 3.75
38 | 10270 | 3.804 | 20910 | 3.314 | 8627.451 | 3.804
39 | 10040 | 3.858 | 21186.6667 | 3.3447 | 8235.2941 | 3.858
40 | 9810 | 3.912 | 21463.3333 | 3.3753 | 7843.1373 | 3.912
41 | 9580 | 3.966 | 21740 | 3.406 | 7450.9804 | 3.966
42 | 9350 | 4.02 | 22016.6667 | 3.4367 | 7058.8235 | 4.02
43 | 9120 | 4.074 | 22293.3333 | 3.4673 | 6666.6667 | 4.074
44 | 8890 | 4.128 | 22570 | 3.498 | 6274.5098 | 4.128
45 | 8660 | 4.182 | 22846.6667 | 3.5287 | 5882.3529 | 4.182
46 | 8430 | 4.236 | 23123.3333 | 3.5593 | 5490.1961 | 4.236
47 | 8200 | 4.29 | 23400 | 3.59 | 5098.0392 | 4.29
48 | 7970 | 4.344 | 23676.6667 | 3.6207 | 4705.8824 | 4.344
49 | 7740 | 4.398 | 23953.3333 | 3.6513 | 4313.7255 | 4.398
50 | 7510 | 4.452 | 24230 | 3.682 | 3921.5686 | 4.452
51 | 7280 | 4.506 | 24506.6667 | 3.7127 | 3529.4118 | 4.506
52 | 7050 | 4.56 | 24783.3333 | 3.7433 | 3137.2549 | 4.56
53 | 6820 | 4.614 | 25060 | 3.774 | 2745.098 | 4.614
54 | 6590 | 4.668 | 25336.6667 | 3.8047 | 2352.9412 | 4.668
55 | 6360 | 4.722 | 25613.3333 | 3.8353 | 1960.7843 | 4.722
56 | 6130 | 4.776 | 25890 | 3.866 | 1568.6275 | 4.776
57 | 5900 | 4.83 | 26166.6667 | 3.8967 | 1176.4706 | 4.83
58 | 5670 | 4.884 | 26443.3333 | 3.9273 | 784.3137 | 4.884
59 | 5440 | 4.938 | 26720 | 3.958 | 392.1569 | 4.938
60 | 5210 | 4.992 | 26996.6667 | 3.9887 | 0 | 4.992
0

## Analysis
Electricity
$ per kWh | 0.27738
BTU/kWh | 3412
$/kBTU | 0.081295
Gas
$ per therm | 1.48
BTU/therm | 100000
Efficiency | 90%
$/kBTU | 0.016444
Break-even COP | 4.9436
Break-even Temp |  | F
Annual Cost
| Gas | Electric | Total | Savings compared to all-gas | Savings compared to heat pump
All-Electric | 0 | 3782.473 | 3782.473
All-gas | 765.1189 | 0 | 765.1189 |  | 577.1797 |  | 516.9722 | therms per year
All heat pump | 0 | 1342.2986 | 1342.2986 | -577.1797
Heat pump, Gas for supplemental | 50.9871 | 1090.2369 | 1141.2239 | -376.105 | 201.0746
Heat pump, Gas below break-even | 765.1189 | 0 | 765.1189 | 0 | 577.1797 | 0% | 43%