## Main
Input | BOILER CALCULATIONS |  | STEAM MAINS CALCULATIONS |  | VENT CALCULATIONS
Output | Manufacturer Selection | Weil-Mclain | Riser Size(Schd40) | 6 | Main Vol(ft3) | 19.6354
| Boiler Selection | LGB-12 | Riser Count | 1 | Radiator Vol(ft3) | 74.25
| Gross BTU/HR | 1144000 | Main Diameter(Schd40) | 6 | Upfeed Vol(ft3) | 10.8052
| Water@Waterline(gal) | 69.1 | Main Length(ft) | 100 | Total Vol(ft3) | 104.6906
| Operating Pressure(PSIG) | 0.1 | Riser Velocity(fps) | 43.5938 | Total Rad Vent(cfm) | 85.14
| Section Weight(lbs) | 3365 | Main Velocity | 43.5938 | Main Vent | Gorton #2
| Enthalpy(BTU/LB) | 968.7975 | Main end pressure(psig) | 0.073808 | Main Vent Count | 5
| Steam Density(lb/ft3) | 0.037504 |  |  | Main Vent Cap(cfm) | 11
| Steam Rate(Lb/HR) | 1180.8454 |  |  | Time to Vent(min) | 9.5173
| Time to Steam(min) | 8.1352 |  |  | Return Size | 3
| Boiler Duty Cycle | 109.1% |  |  | Return Length | 30
| RADIATION CALCULATIONS |  | FAILED TRAP CALCULATIONS
| Radiators(BTU/HR) | 950400 | Steam Pass thru(Lb/Hr) | 9.2782
| Radiator Condensate(lbs/hr) | 953.2598 | BTU/Hr to Condense | 8999.8336
| Upfeed(BTU/HR) | 243540 | Lost Steam(Lb/Hr) | 0
| Upfeed Condensate(lb/hr) | 979.7938 | Lost Heat(BTU/HR) | 0
| Main Radiation(BTU/HR) | 54600
| Main Condensate(lb/hr) | 56.3585
| Total Radiation(BTU/HR) | 1248540
| Total condensate(lb/hr) | 1989.4121
| Min Radiator Pressure(psig) | 0.06755
| Init BTU to Heat Pipes(BTU) | 59121.4853
| Init BTU to Heat Radiators(BTU) | 556174.08
| Init Time to heat Metal(min) | 32.2707
| Time to Steady State(min) | 49.9233
| Return Max Radiation(BTU/HR) | 9090

## TimeAnalysis (hidden)
| Main | Supplies | Radiators | Timestep(min) | Time(min) | BTU Output | ft3/hr gen | Main Venting(%) | Supply Venting(%) | Radiator Venting(%) | Total Venting | Main Heating | Supply Heating | Radiator Heating | Total Radiation(BTU/hr) | Condensate Gen(lb/hr) | Energy(BTUs) | Time | % Load
Volf(ft3) | 19.6354 | 10.8052 | 99 | 0.01 | 0 | 1144000 | 660 | 0 |  |  | 0 | 0 |  |  |  | 0 |  | 0 | 0%
BTU Heat | 31523.4036 | 55231.9139 | 519583.68 |  | 0.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0%
Radiation(btu/hr) | 54600 | 243540 | 950400 |  | 0.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0%
TTH(min) | 1.6533 | 2.8968 | 27.2509 |  | 0.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0%
TTV(min) | 1.785 | 0.98229 | 9 |  | 0.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0%
[5 empty] | 0.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0%
[5 empty] | 0.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0%
[5 empty] | 0.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0%
Start Temp(f) |  |  |  |  | 0.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0%
70 |  |  |  |  | 0.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0%
[5 empty] | 0.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0%
Time to Hourly Output |  |  |  |  | 0.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0%
17.72 |  |  |  |  | 0.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0%
[5 empty] | 0.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0%
[5 empty] | 0.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0%
[5 empty] | 0.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0%
[5 empty] | 0.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0%
[5 empty] | 0.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0%
[5 empty] | 0.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0%
[5 empty] | 0.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0%
[5 empty] | 0.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0%
[5 empty] | 0.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0%
[5 empty] | 0.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0%
[5 empty] | 0.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0%
[5 empty] | 0.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0%
[5 empty] | 0.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0%
[5 empty] | 0.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0%
[5 empty] | 0.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0%
[5 empty] | 0.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0%
[5 empty] | 0.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 0%
[5 empty] | 0.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0%
[5 empty] | 0.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0%
[5 empty] | 0.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0%
[5 empty] | 0.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0%
[5 empty] | 0.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0%
[5 empty] | 0.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0%
[5 empty] | 0.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 0%
[5 empty] | 0.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 0%
[5 empty] | 0.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0%
[5 empty] | 0.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0%
[5 empty] | 0.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0%
[5 empty] | 0.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0%
[5 empty] | 0.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 0%
[5 empty] | 0.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0%
[5 empty] | 0.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0%
[5 empty] | 0.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0%
[5 empty] | 0.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 0%
[5 empty] | 0.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47 | 0%
[5 empty] | 0.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0%
[5 empty] | 0.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0%
[5 empty] | 0.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0%
[5 empty] | 0.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0%
[5 empty] | 0.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0%
[5 empty] | 0.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0%
[5 empty] | 0.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0%
[5 empty] | 0.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55 | 0%
[5 empty] | 0.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 0%
[5 empty] | 0.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0%
[5 empty] | 0.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0%
[5 empty] | 0.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59 | 0%
[5 empty] | 0.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0%
[5 empty] | 0.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0%
[5 empty] | 0.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0%
[5 empty] | 0.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0%
[5 empty] | 0.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0%
[5 empty] | 0.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0%
[5 empty] | 0.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 0%
[5 empty] | 0.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0%
[5 empty] | 0.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0%
[5 empty] | 0.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 0%
[5 empty] | 0.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0%
[5 empty] | 0.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0%
[5 empty] | 0.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0%
[5 empty] | 0.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 0%
[5 empty] | 0.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 0%
[5 empty] | 0.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0%
[5 empty] | 0.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 0%
[5 empty] | 0.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0%
[5 empty] | 0.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0%
[5 empty] | 0.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0%
[5 empty] | 0.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0%
[5 empty] | 0.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0%
[5 empty] | 0.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 0%
[5 empty] | 0.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0%
[5 empty] | 0.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0%
[5 empty] | 0.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0%
[5 empty] | 0.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0%
[5 empty] | 0.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87 | 0%
[5 empty] | 0.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0%
[5 empty] | 0.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0%
[5 empty] | 0.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0%
[5 empty] | 0.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0%
[5 empty] | 0.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 0%
[5 empty] | 0.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93 | 0%
[5 empty] | 0.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 0%
[5 empty] | 0.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0%
[5 empty] | 0.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0%
[5 empty] | 0.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | 0%
[5 empty] | 0.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0%
[5 empty] | 0.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0%
[5 empty] | 1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0%
[5 empty] | 1.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 0%
[5 empty] | 1.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0%
[5 empty] | 1.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03 | 0%
[5 empty] | 1.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0%
[5 empty] | 1.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0%
[5 empty] | 1.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 0%
[5 empty] | 1.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 0%
[5 empty] | 1.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0%
[5 empty] | 1.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 0%
[5 empty] | 1.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0%
[5 empty] | 1.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.11 | 0%
[5 empty] | 1.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0%
[5 empty] | 1.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.13 | 0%
[5 empty] | 1.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0%
[5 empty] | 1.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0%
[5 empty] | 1.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16 | 0%
[5 empty] | 1.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 0%
[5 empty] | 1.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 0%
[5 empty] | 1.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.19 | 0%
[5 empty] | 1.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0%
[5 empty] | 1.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 0%
[5 empty] | 1.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0%
[5 empty] | 1.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0%
[5 empty] | 1.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.24 | 0%
[5 empty] | 1.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 0%
[5 empty] | 1.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0%
[5 empty] | 1.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 0%
[5 empty] | 1.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 0%
[5 empty] | 1.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29 | 0%
[5 empty] | 1.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0%
[5 empty] | 1.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.31 | 0%
[5 empty] | 1.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.32 | 0%
[5 empty] | 1.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0%
[5 empty] | 1.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 0%
[5 empty] | 1.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.35 | 0%
[5 empty] | 1.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36 | 0%
[5 empty] | 1.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 0%
[5 empty] | 1.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 0%
[5 empty] | 1.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.39 | 0%
[5 empty] | 1.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0%
[5 empty] | 1.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.41 | 0%
[5 empty] | 1.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0%
[5 empty] | 1.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 0%
[5 empty] | 1.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 0%
[5 empty] | 1.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 0%
[5 empty] | 1.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.46 | 0%
[5 empty] | 1.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 0%
[5 empty] | 1.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 0%
[5 empty] | 1.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.49 | 0%
[5 empty] | 1.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0%
[5 empty] | 1.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 0%
[5 empty] | 1.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.52 | 0%
[5 empty] | 1.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.53 | 0%
[5 empty] | 1.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.54 | 0%
[5 empty] | 1.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 0%
[5 empty] | 1.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0%
[5 empty] | 1.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.57 | 0%
[5 empty] | 1.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0%
[5 empty] | 1.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.59 | 0%
[5 empty] | 1.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0%
[5 empty] | 1.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 0%
[5 empty] | 1.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 0%
[5 empty] | 1.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0%
[5 empty] | 1.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.64 | 0%
[5 empty] | 1.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 0%
[5 empty] | 1.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0%
[5 empty] | 1.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 0%
[5 empty] | 1.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 0%
[5 empty] | 1.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.69 | 0%
[5 empty] | 1.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0%
[5 empty] | 1.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 0%
[5 empty] | 1.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 0%
[5 empty] | 1.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 0%
[5 empty] | 1.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 0%
[5 empty] | 1.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0%
[5 empty] | 1.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.76 | 0%
[5 empty] | 1.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.77 | 0%
[5 empty] | 1.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0%
[5 empty] | 1.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.79 | 0%
[5 empty] | 1.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0%
[5 empty] | 1.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.81 | 0%
[5 empty] | 1.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 0%
[5 empty] | 1.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.83 | 0%
[5 empty] | 1.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 0%
[5 empty] | 1.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.85 | 0%
[5 empty] | 1.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.86 | 0%
[5 empty] | 1.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 0%
[5 empty] | 1.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 0%
[5 empty] | 1.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.89 | 0%
[5 empty] | 1.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0%
[5 empty] | 1.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.91 | 0%
[5 empty] | 1.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 0%
[5 empty] | 1.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.93 | 0%
[5 empty] | 1.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 0%
[5 empty] | 1.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.95 | 0%
[5 empty] | 1.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 0%
[5 empty] | 1.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97 | 0%
[5 empty] | 1.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 0%
[5 empty] | 1.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.99 | 0%
[5 empty] | 2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0%
[5 empty] | 2.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | 0%
[5 empty] | 2.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 0%
[5 empty] | 2.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.03 | 0%
[5 empty] | 2.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 0%
[5 empty] | 2.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.05 | 0%
[5 empty] | 2.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 0%
[5 empty] | 2.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 0%
[5 empty] | 2.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0%
[5 empty] | 2.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 0%
[5 empty] | 2.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0%
[5 empty] | 2.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.11 | 0%
[5 empty] | 2.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0%
[5 empty] | 2.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0%
[5 empty] | 2.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.14 | 0%
[5 empty] | 2.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | 0%
[5 empty] | 2.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0%
[5 empty] | 2.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0%
[5 empty] | 2.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.18 | 0%
[5 empty] | 2.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.19 | 0%
[5 empty] | 2.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0%
[5 empty] | 2.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.21 | 0%
[5 empty] | 2.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 0%
[5 empty] | 2.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.23 | 0%
[5 empty] | 2.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 0%
[5 empty] | 2.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 0%
[5 empty] | 2.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | 0%
[5 empty] | 2.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.27 | 0%
[5 empty] | 2.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.28 | 0%
[5 empty] | 2.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.29 | 0%
[5 empty] | 2.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0%
[5 empty] | 2.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 0%
[5 empty] | 2.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 0%
[5 empty] | 2.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.33 | 0%
[5 empty] | 2.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.34 | 0%
[5 empty] | 2.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.35 | 0%
[5 empty] | 2.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.36 | 0%
[5 empty] | 2.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.37 | 0%
[5 empty] | 2.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0%
[5 empty] | 2.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.39 | 0%
[5 empty] | 2.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0%
[5 empty] | 2.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.41 | 0%
[5 empty] | 2.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 0%
[5 empty] | 2.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.43 | 0%
[5 empty] | 2.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.44 | 0%
[5 empty] | 2.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.45 | 0%
[5 empty] | 2.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.46 | 0%
[5 empty] | 2.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0%
[5 empty] | 2.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.48 | 0%
[5 empty] | 2.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.49 | 0%
[5 empty] | 2.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0%
[5 empty] | 2.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 0%
[5 empty] | 2.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.52 | 0%
[5 empty] | 2.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 0%
[5 empty] | 2.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 0%
[5 empty] | 2.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.55 | 0%
[5 empty] | 2.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 0%
[5 empty] | 2.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57 | 0%
[5 empty] | 2.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58 | 0%
[5 empty] | 2.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.59 | 0%
[5 empty] | 2.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0%
[5 empty] | 2.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.61 | 0%
[5 empty] | 2.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 0%
[5 empty] | 2.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 0%
[5 empty] | 2.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.64 | 0%
[5 empty] | 2.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.65 | 0%
[5 empty] | 2.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.66 | 0%
[5 empty] | 2.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.67 | 0%
[5 empty] | 2.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.68 | 0%
[5 empty] | 2.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 0%
[5 empty] | 2.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0%
[5 empty] | 2.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 0%
[5 empty] | 2.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 0%
[5 empty] | 2.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.73 | 0%
[5 empty] | 2.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 0%
[5 empty] | 2.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.75 | 0%
[5 empty] | 2.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.76 | 0%
[5 empty] | 2.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.77 | 0%
[5 empty] | 2.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.78 | 0%
[5 empty] | 2.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.79 | 0%
[5 empty] | 2.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0%
[5 empty] | 2.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.81 | 0%
[5 empty] | 2.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.82 | 0%
[5 empty] | 2.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.83 | 0%
[5 empty] | 2.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.84 | 0%
[5 empty] | 2.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 0%
[5 empty] | 2.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 0%
[5 empty] | 2.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.87 | 0%
[5 empty] | 2.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 0%
[5 empty] | 2.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 0%
[5 empty] | 2.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0%
[5 empty] | 2.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.91 | 0%
[5 empty] | 2.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.92 | 0%
[5 empty] | 2.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.93 | 0%
[5 empty] | 2.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 0%
[5 empty] | 2.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 0%
[5 empty] | 2.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.96 | 0%
[5 empty] | 2.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.97 | 0%
[5 empty] | 2.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.98 | 0%
[5 empty] | 2.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.99 | 0%
[5 empty] | 3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0%
[5 empty] | 3.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 0%
[5 empty] | 3.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 0%
[5 empty] | 3.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.03 | 0%
[5 empty] | 3.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.04 | 0%
[5 empty] | 3.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.05 | 0%
[5 empty] | 3.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.06 | 0%
[5 empty] | 3.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 0%
[5 empty] | 3.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 0%
[5 empty] | 3.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.09 | 0%
[5 empty] | 3.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0%
[5 empty] | 3.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.11 | 0%
[5 empty] | 3.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0%
[5 empty] | 3.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 0%
[5 empty] | 3.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 0%
[5 empty] | 3.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 0%
[5 empty] | 3.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 0%
[5 empty] | 3.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 0%
[5 empty] | 3.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.18 | 0%
[5 empty] | 3.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.19 | 0%
[5 empty] | 3.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0%
[5 empty] | 3.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.21 | 0%
[5 empty] | 3.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 0%
[5 empty] | 3.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.23 | 0%
[5 empty] | 3.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.24 | 0%
[5 empty] | 3.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 0%
[5 empty] | 3.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.26 | 0%
[5 empty] | 3.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 0%
[5 empty] | 3.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 0%
[5 empty] | 3.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.29 | 0%
[5 empty] | 3.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0%
[5 empty] | 3.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 0%
[5 empty] | 3.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.32 | 0%
[5 empty] | 3.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.33 | 0%
[5 empty] | 3.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.34 | 0%
[5 empty] | 3.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.35 | 0%
[5 empty] | 3.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.36 | 0%
[5 empty] | 3.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 0%
[5 empty] | 3.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.38 | 0%
[5 empty] | 3.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.39 | 0%
[5 empty] | 3.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0%
[5 empty] | 3.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.41 | 0%
[5 empty] | 3.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.42 | 0%
[5 empty] | 3.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.43 | 0%
[5 empty] | 3.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.44 | 0%
[5 empty] | 3.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.45 | 0%
[5 empty] | 3.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.46 | 0%
[5 empty] | 3.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.47 | 0%
[5 empty] | 3.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.48 | 0%
[5 empty] | 3.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.49 | 0%
[5 empty] | 3.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0%
[5 empty] | 3.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 0%
[5 empty] | 3.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.52 | 0%
[5 empty] | 3.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.53 | 0%
[5 empty] | 3.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.54 | 0%
[5 empty] | 3.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.55 | 0%
[5 empty] | 3.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56 | 0%
[5 empty] | 3.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.57 | 0%
[5 empty] | 3.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 0%
[5 empty] | 3.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.59 | 0%
[5 empty] | 3.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0%
[5 empty] | 3.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.61 | 0%
[5 empty] | 3.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.62 | 0%
[5 empty] | 3.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.63 | 0%
[5 empty] | 3.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.64 | 0%
[5 empty] | 3.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.65 | 0%
[5 empty] | 3.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.66 | 0%
[5 empty] | 3.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.67 | 0%
[5 empty] | 3.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.68 | 0%
[5 empty] | 3.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 0%
[5 empty] | 3.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0%
[5 empty] | 3.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.71 | 0%
[5 empty] | 3.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0%
[5 empty] | 3.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.73 | 0%
[5 empty] | 3.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.74 | 0%
[5 empty] | 3.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.75 | 0%
[5 empty] | 3.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.76 | 0%
[5 empty] | 3.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.77 | 0%
[5 empty] | 3.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.78 | 0%
[5 empty] | 3.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.79 | 0%
[5 empty] | 3.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0%
[5 empty] | 3.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.81 | 0%
[5 empty] | 3.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.82 | 0%
[5 empty] | 3.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 0%
[5 empty] | 3.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.84 | 0%
[5 empty] | 3.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.85 | 0%
[5 empty] | 3.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 0%
[5 empty] | 3.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.87 | 0%
[5 empty] | 3.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.88 | 0%
[5 empty] | 3.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.89 | 0%
[5 empty] | 3.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0%
[5 empty] | 3.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.91 | 0%
[5 empty] | 3.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 0%
[5 empty] | 3.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.93 | 0%
[5 empty] | 3.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.94 | 0%
[5 empty] | 3.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.95 | 0%
[5 empty] | 3.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.96 | 0%
[5 empty] | 3.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.97 | 0%
[5 empty] | 3.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.98 | 0%
[5 empty] | 3.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 0%
[5 empty] | 4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0%
[5 empty] | 4.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.01 | 0%
[5 empty] | 4.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.02 | 0%
[5 empty] | 4.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.03 | 0%
[5 empty] | 4.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 0%
[5 empty] | 4.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.05 | 0%
[5 empty] | 4.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0%
[5 empty] | 4.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.07 | 0%
[5 empty] | 4.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.08 | 0%
[5 empty] | 4.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.09 | 0%
[5 empty] | 4.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0%
[5 empty] | 4.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.11 | 0%
[5 empty] | 4.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.12 | 0%
[5 empty] | 4.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.13 | 0%
[5 empty] | 4.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.14 | 0%
[5 empty] | 4.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.15 | 0%
[5 empty] | 4.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.16 | 0%
[5 empty] | 4.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.17 | 0%
[5 empty] | 4.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.18 | 0%
[5 empty] | 4.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.19 | 0%
[5 empty] | 4.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0%
[5 empty] | 4.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.21 | 0%
[5 empty] | 4.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.22 | 0%
[5 empty] | 4.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.23 | 0%
[5 empty] | 4.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.24 | 0%
[5 empty] | 4.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.25 | 0%
[5 empty] | 4.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.26 | 0%
[5 empty] | 4.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.27 | 0%
[5 empty] | 4.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.28 | 0%
[5 empty] | 4.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.29 | 0%
[5 empty] | 4.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0%
[5 empty] | 4.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.31 | 0%
[5 empty] | 4.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.32 | 0%
[5 empty] | 4.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.33 | 0%
[5 empty] | 4.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.34 | 0%
[5 empty] | 4.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.35 | 0%
[5 empty] | 4.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.36 | 0%
[5 empty] | 4.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.37 | 0%
[5 empty] | 4.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.38 | 0%
[5 empty] | 4.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.39 | 0%
[5 empty] | 4.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0%
[5 empty] | 4.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.41 | 0%
[5 empty] | 4.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.42 | 0%
[5 empty] | 4.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.43 | 0%
[5 empty] | 4.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.44 | 0%
[5 empty] | 4.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.45 | 0%
[5 empty] | 4.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.46 | 0%
[5 empty] | 4.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.47 | 0%
[5 empty] | 4.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.48 | 0%
[5 empty] | 4.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 0%
[5 empty] | 4.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0%
[5 empty] | 4.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.51 | 0%
[5 empty] | 4.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.52 | 0%
[5 empty] | 4.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.53 | 0%
[5 empty] | 4.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.54 | 0%
[5 empty] | 4.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.55 | 0%
[5 empty] | 4.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0%
[5 empty] | 4.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.57 | 0%
[5 empty] | 4.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.58 | 0%
[5 empty] | 4.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0%
[5 empty] | 4.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0%
[5 empty] | 4.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.61 | 0%
[5 empty] | 4.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.62 | 0%
[5 empty] | 4.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.63 | 0%
[5 empty] | 4.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 0%
[5 empty] | 4.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.65 | 0%
[5 empty] | 4.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.66 | 0%
[5 empty] | 4.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.67 | 0%
[5 empty] | 4.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.68 | 0%
[5 empty] | 4.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 0%
[5 empty] | 4.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0%
[5 empty] | 4.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.71 | 0%
[5 empty] | 4.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.72 | 0%
[5 empty] | 4.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 0%
[5 empty] | 4.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.74 | 0%
[5 empty] | 4.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.75 | 0%
[5 empty] | 4.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.76 | 0%
[5 empty] | 4.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.77 | 0%
[5 empty] | 4.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.78 | 0%
[5 empty] | 4.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.79 | 0%
[5 empty] | 4.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0%
[5 empty] | 4.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.81 | 0%
[5 empty] | 4.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.82 | 0%
[5 empty] | 4.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.83 | 0%
[5 empty] | 4.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.84 | 0%
[5 empty] | 4.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.85 | 0%
[5 empty] | 4.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.86 | 0%
[5 empty] | 4.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.87 | 0%
[5 empty] | 4.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.88 | 0%
[5 empty] | 4.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.89 | 0%
[5 empty] | 4.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0%
[5 empty] | 4.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.91 | 0%
[5 empty] | 4.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.92 | 0%
[5 empty] | 4.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.93 | 0%
[5 empty] | 4.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.94 | 0%
[5 empty] | 4.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 0%
[5 empty] | 4.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | 0%
[5 empty] | 4.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.97 | 0%
[5 empty] | 4.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.98 | 0%
[5 empty] | 4.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.99 | 0%
[5 empty] | 5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0%
[5 empty] | 5.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0%
[5 empty] | 5.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.02 | 0%
[5 empty] | 5.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.03 | 0%
[5 empty] | 5.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.04 | 0%
[5 empty] | 5.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.05 | 0%
[5 empty] | 5.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.06 | 0%
[5 empty] | 5.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.07 | 0%
[5 empty] | 5.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.08 | 0%
[5 empty] | 5.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.09 | 0%
[5 empty] | 5.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0%
[5 empty] | 5.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 0%
[5 empty] | 5.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.12 | 0%
[5 empty] | 5.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.13 | 0%
[5 empty] | 5.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.14 | 0%
[5 empty] | 5.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.15 | 0%
[5 empty] | 5.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.16 | 0%
[5 empty] | 5.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.17 | 0%
[5 empty] | 5.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.18 | 0%
[5 empty] | 5.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.19 | 0%
[5 empty] | 5.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0%
[5 empty] | 5.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.21 | 0%
[5 empty] | 5.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.22 | 0%
[5 empty] | 5.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.23 | 0%
[5 empty] | 5.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.24 | 0%
[5 empty] | 5.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.25 | 0%
[5 empty] | 5.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.26 | 0%
[5 empty] | 5.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.27 | 0%
[5 empty] | 5.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.28 | 0%
[5 empty] | 5.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.29 | 0%
[5 empty] | 5.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0%
[5 empty] | 5.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.31 | 0%
[5 empty] | 5.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.32 | 0%
[5 empty] | 5.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.33 | 0%
[5 empty] | 5.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.34 | 0%
[5 empty] | 5.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.35 | 0%
[5 empty] | 5.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.36 | 0%
[5 empty] | 5.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.37 | 0%
[5 empty] | 5.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.38 | 0%
[5 empty] | 5.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.39 | 0%
[5 empty] | 5.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0%
[5 empty] | 5.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.41 | 0%
[5 empty] | 5.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.42 | 0%
[5 empty] | 5.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.43 | 0%
[5 empty] | 5.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.44 | 0%
[5 empty] | 5.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.45 | 0%
[5 empty] | 5.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.46 | 0%
[5 empty] | 5.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.47 | 0%
[5 empty] | 5.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.48 | 0%
[5 empty] | 5.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.49 | 0%
[5 empty] | 5.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0%
[5 empty] | 5.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.51 | 0%
[5 empty] | 5.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.52 | 0%
[5 empty] | 5.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.53 | 0%
[5 empty] | 5.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.54 | 0%
[5 empty] | 5.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.55 | 0%
[5 empty] | 5.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.56 | 0%
[5 empty] | 5.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.57 | 0%
[5 empty] | 5.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.58 | 0%
[5 empty] | 5.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.59 | 0%
[5 empty] | 5.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0%
[5 empty] | 5.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.61 | 0%
[5 empty] | 5.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.62 | 0%
[5 empty] | 5.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.63 | 0%
[5 empty] | 5.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.64 | 0%
[5 empty] | 5.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.65 | 0%
[5 empty] | 5.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.66 | 0%
[5 empty] | 5.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.67 | 0%
[5 empty] | 5.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.68 | 0%
[5 empty] | 5.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.69 | 0%
[5 empty] | 5.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 0%
[5 empty] | 5.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.71 | 0%
[5 empty] | 5.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.72 | 0%
[5 empty] | 5.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.73 | 0%
[5 empty] | 5.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.74 | 0%
[5 empty] | 5.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.75 | 0%
[5 empty] | 5.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.76 | 0%
[5 empty] | 5.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.77 | 0%
[5 empty] | 5.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.78 | 0%
[5 empty] | 5.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.79 | 0%
[5 empty] | 5.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0%
[5 empty] | 5.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.81 | 0%
[5 empty] | 5.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.82 | 0%
[5 empty] | 5.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.83 | 0%
[5 empty] | 5.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.84 | 0%
[5 empty] | 5.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.85 | 0%
[5 empty] | 5.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 0%
[5 empty] | 5.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.87 | 0%
[5 empty] | 5.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.88 | 0%
[5 empty] | 5.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.89 | 0%
[5 empty] | 5.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0%
[5 empty] | 5.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.91 | 0%
[5 empty] | 5.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.92 | 0%
[5 empty] | 5.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.93 | 0%
[5 empty] | 5.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 0%
[5 empty] | 5.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.95 | 0%
[5 empty] | 5.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.96 | 0%
[5 empty] | 5.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.97 | 0%
[5 empty] | 5.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.98 | 0%
[5 empty] | 5.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.99 | 0%
[5 empty] | 6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0%
[5 empty] | 6.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.01 | 0%
[5 empty] | 6.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.02 | 0%
[5 empty] | 6.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.03 | 0%
[5 empty] | 6.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.04 | 0%
[5 empty] | 6.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.05 | 0%
[5 empty] | 6.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.06 | 0%
[5 empty] | 6.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.07 | 0%
[5 empty] | 6.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.08 | 0%
[5 empty] | 6.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.09 | 0%
[5 empty] | 6.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 0%
[5 empty] | 6.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.11 | 0%
[5 empty] | 6.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.12 | 0%
[5 empty] | 6.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.13 | 0%
[5 empty] | 6.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.14 | 0%
[5 empty] | 6.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.15 | 0%
[5 empty] | 6.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.16 | 0%
[5 empty] | 6.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.17 | 0%
[5 empty] | 6.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18 | 0%
[5 empty] | 6.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.19 | 0%
[5 empty] | 6.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 0%
[5 empty] | 6.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.21 | 0%
[5 empty] | 6.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.22 | 0%
[5 empty] | 6.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.23 | 0%
[5 empty] | 6.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 0%
[5 empty] | 6.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 0%
[5 empty] | 6.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.26 | 0%
[5 empty] | 6.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.27 | 0%
[5 empty] | 6.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.28 | 0%
[5 empty] | 6.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.29 | 0%
[5 empty] | 6.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 0%
[5 empty] | 6.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.31 | 0%
[5 empty] | 6.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0%
[5 empty] | 6.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.33 | 0%
[5 empty] | 6.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0%
[5 empty] | 6.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.35 | 0%
[5 empty] | 6.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.36 | 0%
[5 empty] | 6.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.37 | 0%
[5 empty] | 6.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.38 | 0%
[5 empty] | 6.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.39 | 0%
[5 empty] | 6.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0%
[5 empty] | 6.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.41 | 0%
[5 empty] | 6.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.42 | 0%
[5 empty] | 6.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.43 | 0%
[5 empty] | 6.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.44 | 0%
[5 empty] | 6.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.45 | 0%
[5 empty] | 6.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.46 | 0%
[5 empty] | 6.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.47 | 0%
[5 empty] | 6.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.48 | 0%
[5 empty] | 6.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.49 | 0%
[5 empty] | 6.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 0%
[5 empty] | 6.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.51 | 0%
[5 empty] | 6.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.52 | 0%
[5 empty] | 6.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.53 | 0%
[5 empty] | 6.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.54 | 0%
[5 empty] | 6.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.55 | 0%
[5 empty] | 6.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.56 | 0%
[5 empty] | 6.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.57 | 0%
[5 empty] | 6.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.58 | 0%
[5 empty] | 6.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.59 | 0%
[5 empty] | 6.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0%
[5 empty] | 6.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.61 | 0%
[5 empty] | 6.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.62 | 0%
[5 empty] | 6.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.63 | 0%
[5 empty] | 6.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.64 | 0%
[5 empty] | 6.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.65 | 0%
[5 empty] | 6.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.66 | 0%
[5 empty] | 6.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.67 | 0%
[5 empty] | 6.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.68 | 0%
[5 empty] | 6.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.69 | 0%
[5 empty] | 6.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0%
[5 empty] | 6.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.71 | 0%
[5 empty] | 6.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 0%
[5 empty] | 6.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.73 | 0%
[5 empty] | 6.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.74 | 0%
[5 empty] | 6.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.75 | 0%
[5 empty] | 6.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.76 | 0%
[5 empty] | 6.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.77 | 0%
[5 empty] | 6.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.78 | 0%
[5 empty] | 6.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.79 | 0%
[5 empty] | 6.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0%
[5 empty] | 6.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.81 | 0%
[5 empty] | 6.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.82 | 0%
[5 empty] | 6.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.83 | 0%
[5 empty] | 6.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 0%
[5 empty] | 6.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.85 | 0%
[5 empty] | 6.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.86 | 0%
[5 empty] | 6.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.87 | 0%
[5 empty] | 6.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.88 | 0%
[5 empty] | 6.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.89 | 0%
[5 empty] | 6.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0%
[5 empty] | 6.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.91 | 0%
[5 empty] | 6.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.92 | 0%
[5 empty] | 6.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.93 | 0%
[5 empty] | 6.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.94 | 0%
[5 empty] | 6.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.95 | 0%
[5 empty] | 6.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.96 | 0%
[5 empty] | 6.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.97 | 0%
[5 empty] | 6.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.98 | 0%
[5 empty] | 6.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.99 | 0%
[5 empty] | 7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0%
[5 empty] | 7.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.01 | 0%
[5 empty] | 7.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.02 | 0%
[5 empty] | 7.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.03 | 0%
[5 empty] | 7.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.04 | 0%
[5 empty] | 7.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.05 | 0%
[5 empty] | 7.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.06 | 0%
[5 empty] | 7.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.07 | 0%
[5 empty] | 7.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.08 | 0%
[5 empty] | 7.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.09 | 0%
[5 empty] | 7.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0%
[5 empty] | 7.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.11 | 0%
[5 empty] | 7.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.12 | 0%
[5 empty] | 7.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.13 | 0%
[5 empty] | 7.14 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.14 | 0%
[5 empty] | 7.15 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.15 | 0%
[5 empty] | 7.16 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.16 | 0%
[5 empty] | 7.17 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.17 | 0%
[5 empty] | 7.18 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.18 | 0%
[5 empty] | 7.19 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.19 | 0%
[5 empty] | 7.2 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 0%
[5 empty] | 7.21 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.21 | 0%
[5 empty] | 7.22 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.22 | 0%
[5 empty] | 7.23 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.23 | 0%
[5 empty] | 7.24 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0%
[5 empty] | 7.25 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.25 | 0%
[5 empty] | 7.26 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.26 | 0%
[5 empty] | 7.27 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.27 | 0%
[5 empty] | 7.28 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.28 | 0%
[5 empty] | 7.29 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.29 | 0%
[5 empty] | 7.3 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 0%
[5 empty] | 7.31 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.31 | 0%
[5 empty] | 7.32 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.32 | 0%
[5 empty] | 7.33 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.33 | 0%
[5 empty] | 7.34 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.34 | 0%
[5 empty] | 7.35 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.35 | 0%
[5 empty] | 7.36 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.36 | 0%
[5 empty] | 7.37 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.37 | 0%
[5 empty] | 7.38 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.38 | 0%
[5 empty] | 7.39 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.39 | 0%
[5 empty] | 7.4 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0%
[5 empty] | 7.41 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.41 | 0%
[5 empty] | 7.42 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.42 | 0%
[5 empty] | 7.43 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.43 | 0%
[5 empty] | 7.44 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.44 | 0%
[5 empty] | 7.45 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.45 | 0%
[5 empty] | 7.46 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.46 | 0%
[5 empty] | 7.47 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.47 | 0%
[5 empty] | 7.48 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.48 | 0%
[5 empty] | 7.49 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.49 | 0%
[5 empty] | 7.5 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0%
[5 empty] | 7.51 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.51 | 0%
[5 empty] | 7.52 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 0%
[5 empty] | 7.53 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.53 | 0%
[5 empty] | 7.54 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.54 | 0%
[5 empty] | 7.55 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.55 | 0%
[5 empty] | 7.56 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.56 | 0%
[5 empty] | 7.57 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.57 | 0%
[5 empty] | 7.58 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.58 | 0%
[5 empty] | 7.59 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.59 | 0%
[5 empty] | 7.6 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6 | 0%
[5 empty] | 7.61 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.61 | 0%
[5 empty] | 7.62 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.62 | 0%
[5 empty] | 7.63 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.63 | 0%
[5 empty] | 7.64 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.64 | 0%
[5 empty] | 7.65 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.65 | 0%
[5 empty] | 7.66 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.66 | 0%
[5 empty] | 7.67 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.67 | 0%
[5 empty] | 7.68 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.68 | 0%
[5 empty] | 7.69 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.69 | 0%
[5 empty] | 7.7 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7 | 0%
[5 empty] | 7.71 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.71 | 0%
[5 empty] | 7.72 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.72 | 0%
[5 empty] | 7.73 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.73 | 0%
[5 empty] | 7.74 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.74 | 0%
[5 empty] | 7.75 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 0%
[5 empty] | 7.76 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.76 | 0%
[5 empty] | 7.77 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.77 | 0%
[5 empty] | 7.78 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.78 | 0%
[5 empty] | 7.79 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.79 | 0%
[5 empty] | 7.8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 0%
[5 empty] | 7.81 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.81 | 0%
[5 empty] | 7.82 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.82 | 0%
[5 empty] | 7.83 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.83 | 0%
[5 empty] | 7.84 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.84 | 0%
[5 empty] | 7.85 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.85 | 0%
[5 empty] | 7.86 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.86 | 0%
[5 empty] | 7.87 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.87 | 0%
[5 empty] | 7.88 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.88 | 0%
[5 empty] | 7.89 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89 | 0%
[5 empty] | 7.9 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 0%
[5 empty] | 7.91 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.91 | 0%
[5 empty] | 7.92 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.92 | 0%
[5 empty] | 7.93 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.93 | 0%
[5 empty] | 7.94 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.94 | 0%
[5 empty] | 7.95 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.95 | 0%
[5 empty] | 7.96 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.96 | 0%
[5 empty] | 7.97 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.97 | 0%
[5 empty] | 7.98 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.98 | 0%
[5 empty] | 7.99 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.99 | 0%
[5 empty] | 8 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0%
[5 empty] | 8.01 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.01 | 0%
[5 empty] | 8.02 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.02 | 0%
[5 empty] | 8.03 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.03 | 0%
[5 empty] | 8.04 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0%
[5 empty] | 8.05 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.05 | 0%
[5 empty] | 8.06 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.06 | 0%
[5 empty] | 8.07 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.07 | 0%
[5 empty] | 8.08 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0%
[5 empty] | 8.09 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.09 | 0%
[5 empty] | 8.1 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 0%
[5 empty] | 8.11 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.11 | 0%
[5 empty] | 8.12 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12 | 0%
[5 empty] | 8.13 | 1144000 | 660 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.13 | 0%
[5 empty] | 8.14 | 1144000 | 660 | 0.2663% | 0% | 0% | 0.00040389 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 0%
[5 empty] | 8.15 | 1144000 | 660 | 0.8265% | 0% | 0% | 0.0012537 | 0 | 0 | 0 | 0 | 0 | 0 | 8.15 | 0%
[5 empty] | 8.16 | 1144000 | 660 | 1.387% | 0% | 0% | 0.0021035 | 31843.4017 | 0 | 0 | 31843.4017 | 0.32869 | 5.3072 | 8.16 | 2.55%
[5 empty] | 8.17 | 1144000 | 660 | 1.947% | 0% | 0% | 0.0029533 | 31972.6796 | 0 | 0 | 31972.6796 | 0.65871 | 10.636 | 8.17 | 2.561%
[5 empty] | 8.18 | 1144000 | 660 | 2.507% | 0% | 0% | 0.0038031 | 32101.9575 | 0 | 0 | 32101.9575 | 0.99007 | 15.9863 | 8.18 | 2.571%
[5 empty] | 8.19 | 1144000 | 660 | 3.067% | 0% | 0% | 0.0046529 | 32231.2354 | 0 | 0 | 32231.2354 | 1.3228 | 21.3582 | 8.19 | 2.582%
[5 empty] | 8.2 | 1144000 | 660 | 3.628% | 0% | 0% | 0.0055028 | 32360.5133 | 0 | 0 | 32360.5133 | 1.6568 | 26.7516 | 8.2 | 2.592%
[5 empty] | 8.21 | 1144000 | 660 | 4.188% | 0% | 0% | 0.0063526 | 32489.7912 | 0 | 0 | 32489.7912 | 1.9922 | 32.1666 | 8.21 | 2.602%
[5 empty] | 8.22 | 1144000 | 660 | 4.748% | 0% | 0% | 0.0072024 | 32619.0691 | 0 | 0 | 32619.0691 | 2.3289 | 37.6031 | 8.22 | 2.613%
[5 empty] | 8.23 | 1144000 | 660 | 5.308% | 0% | 0% | 0.0080522 | 32748.347 | 0 | 0 | 32748.347 | 2.6669 | 43.0612 | 8.23 | 2.623%
[5 empty] | 8.24 | 1144000 | 660 | 5.868% | 0% | 0% | 0.008902 | 32877.625 | 0 | 0 | 32877.625 | 3.0062 | 48.5408 | 8.24 | 2.633%
[5 empty] | 8.25 | 1144000 | 660 | 6.429% | 0% | 0% | 0.0097518 | 33006.9029 | 0 | 0 | 33006.9029 | 3.3469 | 54.0419 | 8.25 | 2.644%
[5 empty] | 8.26 | 1144000 | 660 | 6.989% | 0% | 0% | 0.010602 | 33136.1808 | 0 | 0 | 33136.1808 | 3.689 | 59.5646 | 8.26 | 2.654%
[5 empty] | 8.27 | 1144000 | 660 | 7.549% | 0% | 0% | 0.011451 | 33265.4587 | 0 | 0 | 33265.4587 | 4.0324 | 65.1089 | 8.27 | 2.664%
[5 empty] | 8.28 | 1144000 | 660 | 8.109% | 0% | 0% | 0.012301 | 33394.7366 | 0 | 0 | 33394.7366 | 4.3771 | 70.6746 | 8.28 | 2.675%
[5 empty] | 8.29 | 1144000 | 660 | 8.669% | 0% | 0% | 0.013151 | 33524.0145 | 0 | 0 | 33524.0145 | 4.7231 | 76.262 | 8.29 | 2.685%
[5 empty] | 8.3 | 1144000 | 660 | 9.23% | 0% | 0% | 0.014001 | 33653.2924 | 0 | 0 | 33653.2924 | 5.0705 | 81.8709 | 8.3 | 2.695%
[5 empty] | 8.31 | 1144000 | 660 | 9.79% | 0% | 0% | 0.014851 | 33782.5703 | 0 | 0 | 33782.5703 | 5.4192 | 87.5013 | 8.31 | 2.706%
[5 empty] | 8.32 | 1144000 | 660 | 10.35% | 0% | 0% | 0.0157 | 33911.8482 | 0 | 0 | 33911.8482 | 5.7692 | 93.1533 | 8.32 | 2.716%
[5 empty] | 8.33 | 1144000 | 660 | 10.91% | 0% | 0% | 0.01655 | 34041.1261 | 0 | 0 | 34041.1261 | 6.1206 | 98.8268 | 8.33 | 2.726%
[5 empty] | 8.34 | 1144000 | 660 | 11.47% | 0% | 0% | 0.0174 | 34170.404 | 0 | 0 | 34170.404 | 6.4733 | 104.5219 | 8.34 | 2.737%
[5 empty] | 8.35 | 1144000 | 660 | 12.03% | 0% | 0% | 0.01825 | 34299.6819 | 0 | 0 | 34299.6819 | 6.8273 | 110.2385 | 8.35 | 2.747%
[5 empty] | 8.36 | 1144000 | 660 | 12.59% | 0% | 0% | 0.0191 | 34428.9599 | 0 | 0 | 34428.9599 | 7.1827 | 115.9766 | 8.36 | 2.758%
[5 empty] | 8.37 | 1144000 | 660 | 13.15% | 0% | 0% | 0.01995 | 34558.2378 | 0 | 0 | 34558.2378 | 7.5394 | 121.7363 | 8.37 | 2.768%
[5 empty] | 8.38 | 1144000 | 660 | 13.71% | 0% | 0% | 0.020799 | 34687.5157 | 0 | 0 | 34687.5157 | 7.8975 | 127.5176 | 8.38 | 2.778%
[5 empty] | 8.39 | 1144000 | 660 | 14.27% | 0% | 0% | 0.021649 | 34816.7936 | 0 | 0 | 34816.7936 | 8.2569 | 133.3204 | 8.39 | 2.789%
[5 empty] | 8.4 | 1144000 | 660 | 14.83% | 0% | 0% | 0.022499 | 34946.0715 | 0 | 0 | 34946.0715 | 8.6176 | 139.1447 | 8.4 | 2.799%
[5 empty] | 8.41 | 1144000 | 660 | 15.39% | 0% | 0% | 0.023349 | 35075.3494 | 0 | 0 | 35075.3494 | 8.9796 | 144.9906 | 8.41 | 2.809%
[5 empty] | 8.42 | 1144000 | 660 | 15.95% | 0% | 0% | 0.024199 | 35204.6273 | 0 | 0 | 35204.6273 | 9.343 | 150.8581 | 8.42 | 2.82%
[5 empty] | 8.43 | 1144000 | 660 | 16.51% | 0% | 0% | 0.025048 | 35333.9052 | 0 | 0 | 35333.9052 | 9.7077 | 156.747 | 8.43 | 2.83%
[5 empty] | 8.44 | 1144000 | 660 | 17.07% | 0% | 0% | 0.025898 | 35463.1831 | 0 | 0 | 35463.1831 | 10.0738 | 162.6576 | 8.44 | 2.84%
[5 empty] | 8.45 | 1144000 | 660 | 17.63% | 0% | 0% | 0.026748 | 35592.461 | 0 | 0 | 35592.461 | 10.4412 | 168.5897 | 8.45 | 2.851%
[5 empty] | 8.46 | 1144000 | 660 | 18.19% | 0% | 0% | 0.027598 | 35721.7389 | 0 | 0 | 35721.7389 | 10.8099 | 174.5433 | 8.46 | 2.861%
[5 empty] | 8.47 | 1144000 | 660 | 18.75% | 0% | 0% | 0.028448 | 35851.0169 | 0 | 0 | 35851.0169 | 11.1799 | 180.5184 | 8.47 | 2.871%
[5 empty] | 8.48 | 1144000 | 660 | 19.31% | 0% | 0% | 0.029297 | 35980.2948 | 0 | 0 | 35980.2948 | 11.5513 | 186.5152 | 8.48 | 2.882%
[5 empty] | 8.49 | 1144000 | 660 | 19.87% | 0% | 0% | 0.030147 | 36109.5727 | 0 | 0 | 36109.5727 | 11.9241 | 192.5334 | 8.49 | 2.892%
[5 empty] | 8.5 | 1144000 | 660 | 20.43% | 0% | 0% | 0.030997 | 36238.8506 | 0 | 0 | 36238.8506 | 12.2981 | 198.5732 | 8.5 | 2.902%
[5 empty] | 8.51 | 1144000 | 660 | 20.99% | 0% | 0% | 0.031847 | 36368.1285 | 0 | 0 | 36368.1285 | 12.6735 | 204.6346 | 8.51 | 2.913%
[5 empty] | 8.52 | 1144000 | 660 | 21.55% | 0% | 0% | 0.032697 | 36497.4064 | 0 | 0 | 36497.4064 | 13.0503 | 210.7175 | 8.52 | 2.923%
[5 empty] | 8.53 | 1144000 | 660 | 22.11% | 0% | 0% | 0.033547 | 36626.6843 | 0 | 0 | 36626.6843 | 13.4283 | 216.8219 | 8.53 | 2.934%
[5 empty] | 8.54 | 1144000 | 660 | 22.67% | 0% | 0% | 0.034396 | 36755.9622 | 0 | 0 | 36755.9622 | 13.8077 | 222.9479 | 8.54 | 2.944%
[5 empty] | 8.55 | 1144000 | 660 | 23.23% | 0% | 0% | 0.035246 | 36885.2401 | 0 | 0 | 36885.2401 | 14.1884 | 229.0955 | 8.55 | 2.954%
[5 empty] | 8.56 | 1144000 | 660 | 23.8% | 0% | 0% | 0.036096 | 37014.518 | 0 | 0 | 37014.518 | 14.5705 | 235.2646 | 8.56 | 2.965%
[5 empty] | 8.57 | 1144000 | 660 | 24.36% | 0% | 0% | 0.036946 | 37143.7959 | 0 | 0 | 37143.7959 | 14.9539 | 241.4552 | 8.57 | 2.975%
[5 empty] | 8.58 | 1144000 | 660 | 24.92% | 0% | 0% | 0.037796 | 37273.0738 | 0 | 0 | 37273.0738 | 15.3386 | 247.6674 | 8.58 | 2.985%
[5 empty] | 8.59 | 1144000 | 660 | 25.48% | 0% | 0% | 0.038645 | 37402.3518 | 0 | 0 | 37402.3518 | 15.7247 | 253.9011 | 8.59 | 2.996%
[5 empty] | 8.6 | 1144000 | 660 | 26.04% | 0% | 0% | 0.039495 | 37531.6297 | 0 | 0 | 37531.6297 | 16.1121 | 260.1564 | 8.6 | 3.006%
[5 empty] | 8.61 | 1144000 | 660 | 26.6% | 0% | 0% | 0.040345 | 37660.9076 | 0 | 0 | 37660.9076 | 16.5009 | 266.4332 | 8.61 | 3.016%
[5 empty] | 8.62 | 1144000 | 660 | 27.16% | 0% | 0% | 0.041195 | 37790.1855 | 0 | 0 | 37790.1855 | 16.8909 | 272.7315 | 8.62 | 3.027%
[5 empty] | 8.63 | 1144000 | 660 | 27.72% | 0% | 0% | 0.042045 | 37919.4634 | 0 | 0 | 37919.4634 | 17.2823 | 279.0515 | 8.63 | 3.037%
[5 empty] | 8.64 | 1144000 | 660 | 28.28% | 0% | 0% | 0.042894 | 38048.7413 | 0 | 0 | 38048.7413 | 17.6751 | 285.3929 | 8.64 | 3.047%
[5 empty] | 8.65 | 1144000 | 660 | 28.84% | 0% | 0% | 0.043744 | 38178.0192 | 0 | 0 | 38178.0192 | 18.0692 | 291.7559 | 8.65 | 3.058%
[5 empty] | 8.66 | 1144000 | 660 | 29.4% | 0% | 0% | 0.044594 | 38307.2971 | 0 | 0 | 38307.2971 | 18.4646 | 298.1405 | 8.66 | 3.068%
[5 empty] | 8.67 | 1144000 | 660 | 29.96% | 0% | 0% | 0.045444 | 38436.575 | 0 | 0 | 38436.575 | 18.8613 | 304.5466 | 8.67 | 3.079%
[5 empty] | 8.68 | 1144000 | 660 | 30.52% | 0% | 0% | 0.046294 | 38565.8529 | 0 | 0 | 38565.8529 | 19.2594 | 310.9742 | 8.68 | 3.089%
[5 empty] | 8.69 | 1144000 | 660 | 31.08% | 0% | 0% | 0.047143 | 38695.1308 | 0 | 0 | 38695.1308 | 19.6588 | 317.4234 | 8.69 | 3.099%
[5 empty] | 8.7 | 1144000 | 660 | 31.64% | 0% | 0% | 0.047993 | 38824.4088 | 0 | 0 | 38824.4088 | 20.0596 | 323.8941 | 8.7 | 3.11%
[5 empty] | 8.71 | 1144000 | 660 | 32.2% | 0% | 0% | 0.048843 | 38953.6867 | 0 | 0 | 38953.6867 | 20.4616 | 330.3864 | 8.71 | 3.12%
[5 empty] | 8.72 | 1144000 | 660 | 32.76% | 0% | 0% | 0.049693 | 39082.9646 | 0 | 0 | 39082.9646 | 20.8651 | 336.9002 | 8.72 | 3.13%
[5 empty] | 8.73 | 1144000 | 660 | 33.32% | 0% | 0% | 0.050543 | 39212.2425 | 0 | 0 | 39212.2425 | 21.2698 | 343.4356 | 8.73 | 3.141%
[5 empty] | 8.74 | 1144000 | 660 | 33.88% | 0% | 0% | 0.051393 | 39341.5204 | 0 | 0 | 39341.5204 | 21.6759 | 349.9925 | 8.74 | 3.151%
[5 empty] | 8.75 | 1144000 | 660 | 34.44% | 0% | 0% | 0.052242 | 39470.7983 | 0 | 0 | 39470.7983 | 22.0833 | 356.571 | 8.75 | 3.161%
[5 empty] | 8.76 | 1144000 | 660 | 35% | 0% | 0% | 0.053092 | 39600.0762 | 0 | 0 | 39600.0762 | 22.4921 | 363.171 | 8.76 | 3.172%
[5 empty] | 8.77 | 1144000 | 660 | 35.56% | 0% | 0% | 0.053942 | 39729.3541 | 0 | 0 | 39729.3541 | 22.9022 | 369.7926 | 8.77 | 3.182%
[5 empty] | 8.78 | 1144000 | 660 | 36.12% | 0% | 0% | 0.054792 | 39858.632 | 0 | 0 | 39858.632 | 23.3136 | 376.4357 | 8.78 | 3.192%
[5 empty] | 8.79 | 1144000 | 660 | 36.68% | 0% | 0% | 0.055642 | 39987.9099 | 0 | 0 | 39987.9099 | 23.7263 | 383.1003 | 8.79 | 3.203%
[5 empty] | 8.8 | 1144000 | 660 | 37.24% | 0% | 0% | 0.056491 | 40117.1878 | 0 | 0 | 40117.1878 | 24.1404 | 389.7865 | 8.8 | 3.213%
[5 empty] | 8.81 | 1144000 | 660 | 37.8% | 0% | 0% | 0.057341 | 40246.4658 | 0 | 0 | 40246.4658 | 24.5559 | 396.4943 | 8.81 | 3.223%
[5 empty] | 8.82 | 1144000 | 660 | 38.36% | 0% | 0% | 0.058191 | 40375.7437 | 0 | 0 | 40375.7437 | 24.9726 | 403.2236 | 8.82 | 3.234%
[5 empty] | 8.83 | 1144000 | 660 | 38.92% | 0% | 0% | 0.059041 | 40505.0216 | 0 | 0 | 40505.0216 | 25.3907 | 409.9744 | 8.83 | 3.244%
[5 empty] | 8.84 | 1144000 | 660 | 39.48% | 0% | 0% | 0.059891 | 40634.2995 | 0 | 0 | 40634.2995 | 25.8101 | 416.7468 | 8.84 | 3.255%
[5 empty] | 8.85 | 1144000 | 660 | 40.04% | 0% | 0% | 0.06074 | 40763.5774 | 0 | 0 | 40763.5774 | 26.2309 | 423.5407 | 8.85 | 3.265%
[5 empty] | 8.86 | 1144000 | 660 | 40.6% | 0% | 0% | 0.06159 | 40892.8553 | 0 | 0 | 40892.8553 | 26.653 | 430.3562 | 8.86 | 3.275%
[5 empty] | 8.87 | 1144000 | 660 | 41.16% | 0% | 0% | 0.06244 | 41022.1332 | 0 | 0 | 41022.1332 | 27.0764 | 437.1932 | 8.87 | 3.286%
[5 empty] | 8.88 | 1144000 | 660 | 41.72% | 0% | 0% | 0.06329 | 41151.4111 | 0 | 0 | 41151.4111 | 27.5012 | 444.0518 | 8.88 | 3.296%
[5 empty] | 8.89 | 1144000 | 660 | 42.28% | 0% | 0% | 0.06414 | 41280.689 | 0 | 0 | 41280.689 | 27.9273 | 450.9319 | 8.89 | 3.306%
[5 empty] | 8.9 | 1144000 | 660 | 42.84% | 0% | 0% | 0.064989 | 41409.9669 | 0 | 0 | 41409.9669 | 28.3548 | 457.8336 | 8.9 | 3.317%
[5 empty] | 8.91 | 1144000 | 660 | 43.4% | 0% | 0% | 0.065839 | 41539.2448 | 0 | 0 | 41539.2448 | 28.7835 | 464.7568 | 8.91 | 3.327%
[5 empty] | 8.92 | 1144000 | 660 | 43.96% | 0% | 0% | 0.066689 | 41668.5227 | 0 | 0 | 41668.5227 | 29.2136 | 471.7015 | 8.92 | 3.337%
[5 empty] | 8.93 | 1144000 | 660 | 44.52% | 0% | 0% | 0.067539 | 41797.8007 | 0 | 0 | 41797.8007 | 29.6451 | 478.6678 | 8.93 | 3.348%
[5 empty] | 8.94 | 1144000 | 660 | 45.08% | 0% | 0% | 0.068389 | 41927.0786 | 0 | 0 | 41927.0786 | 30.0778 | 485.6557 | 8.94 | 3.358%
[5 empty] | 8.95 | 1144000 | 660 | 45.64% | 0% | 0% | 0.069239 | 42056.3565 | 0 | 0 | 42056.3565 | 30.512 | 492.6651 | 8.95 | 3.368%
[5 empty] | 8.96 | 1144000 | 660 | 46.2% | 0% | 0% | 0.070088 | 42185.6344 | 0 | 0 | 42185.6344 | 30.9474 | 499.696 | 8.96 | 3.379%
[5 empty] | 8.97 | 1144000 | 660 | 46.76% | 0% | 0% | 0.070938 | 42314.9123 | 0 | 0 | 42314.9123 | 31.3842 | 506.7485 | 8.97 | 3.389%
[5 empty] | 8.98 | 1144000 | 660 | 47.32% | 0% | 0% | 0.071788 | 42444.1902 | 0 | 0 | 42444.1902 | 31.8223 | 513.8225 | 8.98 | 3.4%
[5 empty] | 8.99 | 1144000 | 660 | 47.88% | 0% | 0% | 0.072638 | 42573.4681 | 0 | 0 | 42573.4681 | 32.2617 | 520.9181 | 8.99 | 3.41%
[5 empty] | 9 | 1144000 | 660 | 48.44% | 0% | 0% | 0.073488 | 42702.746 | 0 | 0 | 42702.746 | 32.7025 | 528.0352 | 9 | 3.42%
[5 empty] | 9.01 | 1144000 | 660 | 49% | 0% | 0% | 0.074337 | 42832.0239 | 0 | 0 | 42832.0239 | 33.1446 | 535.1739 | 9.01 | 3.431%
[5 empty] | 9.02 | 1144000 | 660 | 49.56% | 0% | 0% | 0.075187 | 42961.3018 | 0 | 0 | 42961.3018 | 33.5881 | 542.3341 | 9.02 | 3.441%
[5 empty] | 9.03 | 1144000 | 660 | 50.13% | 0% | 0% | 0.076037 | 43090.5797 | 0 | 0 | 43090.5797 | 34.0329 | 549.5159 | 9.03 | 3.451%
[5 empty] | 9.04 | 1144000 | 660 | 50.69% | 0% | 0% | 0.076887 | 43219.8577 | 0 | 0 | 43219.8577 | 34.479 | 556.7192 | 9.04 | 3.462%
[5 empty] | 9.05 | 1144000 | 660 | 51.25% | 0% | 0% | 0.077737 | 43349.1356 | 0 | 0 | 43349.1356 | 34.9264 | 563.944 | 9.05 | 3.472%
[5 empty] | 9.06 | 1144000 | 660 | 51.81% | 0% | 0% | 0.078586 | 43478.4135 | 0 | 0 | 43478.4135 | 35.3752 | 571.1904 | 9.06 | 3.482%
[5 empty] | 9.07 | 1144000 | 660 | 52.37% | 0% | 0% | 0.079436 | 43607.6914 | 0 | 0 | 43607.6914 | 35.8253 | 578.4584 | 9.07 | 3.493%
[5 empty] | 9.08 | 1144000 | 660 | 52.93% | 0% | 0% | 0.080286 | 43736.9693 | 0 | 0 | 43736.9693 | 36.2768 | 585.7479 | 9.08 | 3.503%
[5 empty] | 9.09 | 1144000 | 660 | 53.49% | 0% | 0% | 0.081136 | 43866.2472 | 0 | 0 | 43866.2472 | 36.7296 | 593.0589 | 9.09 | 3.513%
[5 empty] | 9.1 | 1144000 | 660 | 54.05% | 0% | 0% | 0.081986 | 43995.5251 | 0 | 0 | 43995.5251 | 37.1837 | 600.3915 | 9.1 | 3.524%
[5 empty] | 9.11 | 1144000 | 660 | 54.61% | 0% | 0% | 0.082836 | 44124.803 | 0 | 0 | 44124.803 | 37.6392 | 607.7456 | 9.11 | 3.534%
[5 empty] | 9.12 | 1144000 | 660 | 55.17% | 0% | 0% | 0.083685 | 44254.0809 | 0 | 0 | 44254.0809 | 38.096 | 615.1213 | 9.12 | 3.544%
[5 empty] | 9.13 | 1144000 | 660 | 55.73% | 0% | 0% | 0.084535 | 44383.3588 | 0 | 0 | 44383.3588 | 38.5541 | 622.5185 | 9.13 | 3.555%
[5 empty] | 9.14 | 1144000 | 660 | 56.29% | 0% | 0% | 0.085385 | 44512.6367 | 0 | 0 | 44512.6367 | 39.0136 | 629.9373 | 9.14 | 3.565%
[5 empty] | 9.15 | 1144000 | 660 | 56.85% | 0% | 0% | 0.086235 | 44641.9146 | 0 | 0 | 44641.9146 | 39.4744 | 637.3776 | 9.15 | 3.576%
[5 empty] | 9.16 | 1144000 | 660 | 57.41% | 0% | 0% | 0.087085 | 44771.1926 | 0 | 0 | 44771.1926 | 39.9365 | 644.8395 | 9.16 | 3.586%
[5 empty] | 9.17 | 1144000 | 660 | 57.97% | 0% | 0% | 0.087934 | 44900.4705 | 0 | 0 | 44900.4705 | 40.4 | 652.3229 | 9.17 | 3.596%
[5 empty] | 9.18 | 1144000 | 660 | 58.53% | 0% | 0% | 0.088784 | 45029.7484 | 0 | 0 | 45029.7484 | 40.8648 | 659.8279 | 9.18 | 3.607%
[5 empty] | 9.19 | 1144000 | 660 | 59.09% | 0% | 0% | 0.089634 | 45159.0263 | 0 | 0 | 45159.0263 | 41.3309 | 667.3544 | 9.19 | 3.617%
[5 empty] | 9.2 | 1144000 | 660 | 59.65% | 0% | 0% | 0.090484 | 45288.3042 | 0 | 0 | 45288.3042 | 41.7984 | 674.9024 | 9.2 | 3.627%
[5 empty] | 9.21 | 1144000 | 660 | 60.21% | 0% | 0% | 0.091334 | 45417.5821 | 0 | 0 | 45417.5821 | 42.2672 | 682.472 | 9.21 | 3.638%
[5 empty] | 9.22 | 1144000 | 660 | 60.77% | 0% | 0% | 0.092183 | 45546.86 | 0 | 0 | 45546.86 | 42.7373 | 690.0632 | 9.22 | 3.648%
[5 empty] | 9.23 | 1144000 | 660 | 61.33% | 0% | 0% | 0.093033 | 45676.1379 | 0 | 0 | 45676.1379 | 43.2088 | 697.6759 | 9.23 | 3.658%
[5 empty] | 9.24 | 1144000 | 660 | 61.89% | 0% | 0% | 0.093883 | 45805.4158 | 0 | 0 | 45805.4158 | 43.6816 | 705.3101 | 9.24 | 3.669%
[5 empty] | 9.25 | 1144000 | 660 | 62.45% | 0% | 0% | 0.094733 | 45934.6937 | 0 | 0 | 45934.6937 | 44.1557 | 712.9659 | 9.25 | 3.679%
[5 empty] | 9.26 | 1144000 | 660 | 63.01% | 0% | 0% | 0.095583 | 46063.9716 | 0 | 0 | 46063.9716 | 44.6312 | 720.6432 | 9.26 | 3.689%
[5 empty] | 9.27 | 1144000 | 660 | 63.57% | 0% | 0% | 0.096432 | 46193.2496 | 0 | 0 | 46193.2496 | 45.108 | 728.3421 | 9.27 | 3.7%
[5 empty] | 9.28 | 1144000 | 660 | 64.13% | 0% | 0% | 0.097282 | 46322.5275 | 0 | 0 | 46322.5275 | 45.5862 | 736.0625 | 9.28 | 3.71%
[5 empty] | 9.29 | 1144000 | 660 | 64.69% | 0% | 0% | 0.098132 | 46451.8054 | 0 | 0 | 46451.8054 | 46.0656 | 743.8045 | 9.29 | 3.72%
[5 empty] | 9.3 | 1144000 | 660 | 65.25% | 0% | 0% | 0.098982 | 46581.0833 | 0 | 0 | 46581.0833 | 46.5464 | 751.568 | 9.3 | 3.731%
[5 empty] | 9.31 | 1144000 | 660 | 65.81% | 0% | 0% | 0.099832 | 46710.3612 | 0 | 0 | 46710.3612 | 47.0286 | 759.353 | 9.31 | 3.741%
[5 empty] | 9.32 | 1144000 | 660 | 66.37% | 0% | 0% | 0.10068 | 46839.6391 | 0 | 0 | 46839.6391 | 47.5121 | 767.1596 | 9.32 | 3.752%
[5 empty] | 9.33 | 1144000 | 660 | 66.93% | 0% | 0% | 0.10153 | 46968.917 | 0 | 0 | 46968.917 | 47.9969 | 774.9878 | 9.33 | 3.762%
[5 empty] | 9.34 | 1144000 | 660 | 67.49% | 0% | 0% | 0.10238 | 47098.1949 | 0 | 0 | 47098.1949 | 48.483 | 782.8375 | 9.34 | 3.772%
[5 empty] | 9.35 | 1144000 | 660 | 68.05% | 0% | 0% | 0.10323 | 47227.4728 | 0 | 0 | 47227.4728 | 48.9705 | 790.7087 | 9.35 | 3.783%
[5 empty] | 9.36 | 1144000 | 660 | 68.61% | 0% | 0% | 0.10408 | 47356.7507 | 0 | 0 | 47356.7507 | 49.4593 | 798.6015 | 9.36 | 3.793%
[5 empty] | 9.37 | 1144000 | 660 | 69.17% | 0% | 0% | 0.10493 | 47486.0286 | 0 | 0 | 47486.0286 | 49.9495 | 806.5159 | 9.37 | 3.803%
[5 empty] | 9.38 | 1144000 | 660 | 69.73% | 0% | 0% | 0.10578 | 47615.3065 | 0 | 0 | 47615.3065 | 50.441 | 814.4518 | 9.38 | 3.814%
[5 empty] | 9.39 | 1144000 | 660 | 70.29% | 0% | 0% | 0.10663 | 47744.5845 | 0 | 0 | 47744.5845 | 50.9338 | 822.4092 | 9.39 | 3.824%
[5 empty] | 9.4 | 1144000 | 660 | 70.85% | 0% | 0% | 0.10748 | 47873.8624 | 0 | 0 | 47873.8624 | 51.428 | 830.3882 | 9.4 | 3.834%
[5 empty] | 9.41 | 1144000 | 660 | 71.41% | 0% | 0% | 0.10833 | 48003.1403 | 0 | 0 | 48003.1403 | 51.9235 | 838.3887 | 9.41 | 3.845%
[5 empty] | 9.42 | 1144000 | 660 | 71.97% | 0% | 0% | 0.10918 | 48132.4182 | 0 | 0 | 48132.4182 | 52.4203 | 846.4108 | 9.42 | 3.855%
[5 empty] | 9.43 | 1144000 | 660 | 72.53% | 0% | 0% | 0.11003 | 48261.6961 | 0 | 0 | 48261.6961 | 52.9185 | 854.4544 | 9.43 | 3.865%
[5 empty] | 9.44 | 1144000 | 660 | 73.09% | 0% | 0% | 0.11088 | 48390.974 | 0 | 0 | 48390.974 | 53.4179 | 862.5195 | 9.44 | 3.876%
[5 empty] | 9.45 | 1144000 | 660 | 73.65% | 0% | 0% | 0.11173 | 48520.2519 | 0 | 0 | 48520.2519 | 53.9188 | 870.6062 | 9.45 | 3.886%
[5 empty] | 9.46 | 1144000 | 660 | 74.21% | 0% | 0% | 0.11258 | 48649.5298 | 0 | 0 | 48649.5298 | 54.4209 | 878.7145 | 9.46 | 3.897%
[5 empty] | 9.47 | 1144000 | 660 | 74.77% | 0% | 0% | 0.11343 | 48778.8077 | 0 | 0 | 48778.8077 | 54.9244 | 886.8443 | 9.47 | 3.907%
[5 empty] | 9.48 | 1144000 | 660 | 75.33% | 0% | 0% | 0.11428 | 48908.0856 | 0 | 0 | 48908.0856 | 55.4293 | 894.9957 | 9.48 | 3.917%
[5 empty] | 9.49 | 1144000 | 660 | 75.89% | 0% | 0% | 0.11513 | 49037.3635 | 0 | 0 | 49037.3635 | 55.9354 | 903.1685 | 9.49 | 3.928%
[5 empty] | 9.5 | 1144000 | 660 | 76.46% | 0% | 0% | 0.11598 | 49166.6415 | 0 | 0 | 49166.6415 | 56.4429 | 911.363 | 9.5 | 3.938%
[5 empty] | 9.51 | 1144000 | 660 | 77.02% | 0% | 0% | 0.11683 | 49295.9194 | 0 | 0 | 49295.9194 | 56.9518 | 919.579 | 9.51 | 3.948%
[5 empty] | 9.52 | 1144000 | 660 | 77.58% | 0% | 0% | 0.11768 | 49425.1973 | 0 | 0 | 49425.1973 | 57.4619 | 927.8165 | 9.52 | 3.959%
[5 empty] | 9.53 | 1144000 | 660 | 78.14% | 0% | 0% | 0.11853 | 49554.4752 | 0 | 0 | 49554.4752 | 57.9735 | 936.0756 | 9.53 | 3.969%
[5 empty] | 9.54 | 1144000 | 660 | 78.7% | 0% | 0% | 0.11938 | 49683.7531 | 0 | 0 | 49683.7531 | 58.4863 | 944.3562 | 9.54 | 3.979%
[5 empty] | 9.55 | 1144000 | 660 | 79.26% | 0% | 0% | 0.12023 | 49813.031 | 0 | 0 | 49813.031 | 59.0005 | 952.6584 | 9.55 | 3.99%
[5 empty] | 9.56 | 1144000 | 660 | 79.82% | 0% | 0% | 0.12108 | 49942.3089 | 0 | 0 | 49942.3089 | 59.516 | 960.9821 | 9.56 | 4%
[5 empty] | 9.57 | 1144000 | 660 | 80.38% | 0% | 0% | 0.12193 | 50071.5868 | 0 | 0 | 50071.5868 | 60.0328 | 969.3274 | 9.57 | 4.01%
[5 empty] | 9.58 | 1144000 | 660 | 80.94% | 0% | 0% | 0.12278 | 50200.8647 | 0 | 0 | 50200.8647 | 60.551 | 977.6942 | 9.58 | 4.021%
[5 empty] | 9.59 | 1144000 | 660 | 81.5% | 0% | 0% | 0.12363 | 50330.1426 | 0 | 0 | 50330.1426 | 61.0705 | 986.0825 | 9.59 | 4.031%
[5 empty] | 9.6 | 1144000 | 660 | 82.06% | 0% | 0% | 0.12448 | 50459.4205 | 0 | 0 | 50459.4205 | 61.5914 | 994.4924 | 9.6 | 4.041%
[5 empty] | 9.61 | 1144000 | 660 | 82.62% | 0% | 0% | 0.12533 | 50588.6984 | 0 | 0 | 50588.6984 | 62.1135 | 1002.9239 | 9.61 | 4.052%
[5 empty] | 9.62 | 1144000 | 660 | 83.18% | 0% | 0% | 0.12618 | 50717.9764 | 0 | 0 | 50717.9764 | 62.637 | 1011.3769 | 9.62 | 4.062%
[5 empty] | 9.63 | 1144000 | 660 | 83.74% | 0% | 0% | 0.12703 | 50847.2543 | 0 | 0 | 50847.2543 | 63.1619 | 1019.8514 | 9.63 | 4.073%
[5 empty] | 9.64 | 1144000 | 660 | 84.3% | 0% | 0% | 0.12788 | 50976.5322 | 0 | 0 | 50976.5322 | 63.6881 | 1028.3475 | 9.64 | 4.083%
[5 empty] | 9.65 | 1144000 | 660 | 84.86% | 0% | 0% | 0.12873 | 51105.8101 | 0 | 0 | 51105.8101 | 64.2156 | 1036.8651 | 9.65 | 4.093%
[5 empty] | 9.66 | 1144000 | 660 | 85.42% | 0% | 0% | 0.12958 | 51235.088 | 0 | 0 | 51235.088 | 64.7445 | 1045.4043 | 9.66 | 4.104%
[5 empty] | 9.67 | 1144000 | 660 | 85.98% | 0% | 0% | 0.13042 | 51364.3659 | 0 | 0 | 51364.3659 | 65.2746 | 1053.9651 | 9.67 | 4.114%
[5 empty] | 9.68 | 1144000 | 660 | 86.54% | 0% | 0% | 0.13127 | 51493.6438 | 0 | 0 | 51493.6438 | 65.8062 | 1062.5473 | 9.68 | 4.124%
[5 empty] | 9.69 | 1144000 | 660 | 87.1% | 0% | 0% | 0.13212 | 51622.9217 | 0 | 0 | 51622.9217 | 66.339 | 1071.1512 | 9.69 | 4.135%
[5 empty] | 9.7 | 1144000 | 660 | 87.66% | 0% | 0% | 0.13297 | 51752.1996 | 0 | 0 | 51752.1996 | 66.8732 | 1079.7765 | 9.7 | 4.145%
[5 empty] | 9.71 | 1144000 | 660 | 88.22% | 0% | 0% | 0.13382 | 51881.4775 | 0 | 0 | 51881.4775 | 67.4087 | 1088.4234 | 9.71 | 4.155%
[5 empty] | 9.72 | 1144000 | 660 | 88.78% | 0% | 0% | 0.13467 | 52010.7554 | 0 | 0 | 52010.7554 | 67.9456 | 1097.0919 | 9.72 | 4.166%
[5 empty] | 9.73 | 1144000 | 660 | 89.34% | 0% | 0% | 0.13552 | 52140.0334 | 0 | 0 | 52140.0334 | 68.4838 | 1105.7819 | 9.73 | 4.176%
[5 empty] | 9.74 | 1144000 | 660 | 89.9% | 0% | 0% | 0.13637 | 52269.3113 | 0 | 0 | 52269.3113 | 69.0233 | 1114.4934 | 9.74 | 4.186%
[5 empty] | 9.75 | 1144000 | 660 | 90.46% | 0% | 0% | 0.13722 | 52398.5892 | 0 | 0 | 52398.5892 | 69.5642 | 1123.2265 | 9.75 | 4.197%
[5 empty] | 9.76 | 1144000 | 660 | 91.02% | 0% | 0% | 0.13807 | 52527.8671 | 0 | 0 | 52527.8671 | 70.1064 | 1131.9812 | 9.76 | 4.207%
[5 empty] | 9.77 | 1144000 | 660 | 91.58% | 0% | 0% | 0.13892 | 52657.145 | 0 | 0 | 52657.145 | 70.6499 | 1140.7574 | 9.77 | 4.217%
[5 empty] | 9.78 | 1144000 | 660 | 92.14% | 0% | 0% | 0.13977 | 52786.4229 | 0 | 0 | 52786.4229 | 71.1948 | 1149.5551 | 9.78 | 4.228%
[5 empty] | 9.79 | 1144000 | 660 | 92.7% | 0% | 0% | 0.14062 | 52915.7008 | 0 | 0 | 52915.7008 | 71.741 | 1158.3744 | 9.79 | 4.238%
[5 empty] | 9.8 | 1144000 | 660 | 93.26% | 0% | 0% | 0.14147 | 53044.9787 | 0 | 0 | 53044.9787 | 72.2885 | 1167.2152 | 9.8 | 4.249%
[5 empty] | 9.81 | 1144000 | 660 | 93.82% | 0% | 0% | 0.14232 | 53174.2566 | 0 | 0 | 53174.2566 | 72.8374 | 1176.0776 | 9.81 | 4.259%
[5 empty] | 9.82 | 1144000 | 660 | 94.38% | 0% | 0% | 0.14317 | 53303.5345 | 0 | 0 | 53303.5345 | 73.3876 | 1184.9615 | 9.82 | 4.269%
[5 empty] | 9.83 | 1144000 | 660 | 94.94% | 0% | 0% | 0.14402 | 53432.8124 | 0 | 0 | 53432.8124 | 73.9391 | 1193.867 | 9.83 | 4.28%
[5 empty] | 9.84 | 1144000 | 660 | 95.5% | 0% | 0% | 0.14487 | 53562.0904 | 0 | 0 | 53562.0904 | 74.492 | 1202.794 | 9.84 | 4.29%
[5 empty] | 9.85 | 1144000 | 660 | 96.06% | 0% | 0% | 0.14572 | 53691.3683 | 0 | 0 | 53691.3683 | 75.0462 | 1211.7426 | 9.85 | 4.3%
[5 empty] | 9.86 | 1144000 | 660 | 96.62% | 0% | 0% | 0.14657 | 53820.6462 | 0 | 0 | 53820.6462 | 75.6017 | 1220.7127 | 9.86 | 4.311%
[5 empty] | 9.87 | 1144000 | 660 | 97.18% | 0% | 0% | 0.14742 | 53949.9241 | 0 | 0 | 53949.9241 | 76.1586 | 1229.7043 | 9.87 | 4.321%
[5 empty] | 9.88 | 1144000 | 660 | 97.74% | 0% | 0% | 0.14827 | 54079.202 | 0 | 0 | 54079.202 | 76.7168 | 1238.7175 | 9.88 | 4.331%
[5 empty] | 9.89 | 1144000 | 660 | 98.3% | 0% | 0% | 0.14912 | 54208.4799 | 0 | 0 | 54208.4799 | 77.2764 | 1247.7523 | 9.89 | 4.342%
[5 empty] | 9.9 | 1144000 | 660 | 98.86% | 0% | 0% | 0.14997 | 54337.7578 | 0 | 0 | 54337.7578 | 77.8372 | 1256.8086 | 9.9 | 4.352%
[5 empty] | 9.91 | 1144000 | 660 | 99.42% | 0% | 0% | 0.15082 | 54467.0357 | 0 | 0 | 54467.0357 | 78.3994 | 1265.8864 | 9.91 | 4.362%
[5 empty] | 9.92 | 1144000 | 660 | 99.98% | 0% | 0% | 0.15167 | 54596.3136 | 0 | 0 | 54596.3136 | 78.963 | 1274.9858 | 9.92 | 4.373%
[5 empty] | 9.93 | 1144000 | 660 | 100% | 0.989% | 0% | 0.15252 | 54600 | 0 | 0 | 54600 | 79.5266 | 1284.0858 | 9.93 | 4.373%
[5 empty] | 9.94 | 1144000 | 660 | 100% | 2.007% | 0% | 0.15337 | 54600 | 59011.306 | 0 | 113611.306 | 80.6993 | 1303.021 | 9.94 | 9.1%
[5 empty] | 9.95 | 1144000 | 660 | 100% | 3.025% | 0% | 0.15422 | 54600 | 60928.3342 | 0 | 115528.3342 | 81.8918 | 1322.2757 | 9.95 | 9.253%
[5 empty] | 9.96 | 1144000 | 660 | 100% | 4.043% | 0% | 0.15507 | 54600 | 62845.3625 | 0 | 117445.3625 | 83.1041 | 1341.85 | 9.96 | 9.407%
[5 empty] | 9.97 | 1144000 | 660 | 100% | 5.061% | 0% | 0.15592 | 54600 | 64762.3907 | 0 | 119362.3907 | 84.3361 | 1361.7437 | 9.97 | 9.56%
[5 empty] | 9.98 | 1144000 | 660 | 100% | 6.079% | 0% | 0.15677 | 54600 | 66679.4189 | 0 | 121279.4189 | 85.588 | 1381.9569 | 9.98 | 9.714%
[5 empty] | 9.99 | 1144000 | 660 | 100% | 7.097% | 0% | 0.15762 | 54600 | 68596.4472 | 0 | 123196.4472 | 86.8596 | 1402.4897 | 9.99 | 9.867%
[5 empty] | 10 | 1144000 | 660 | 100% | 8.115% | 0% | 0.15847 | 54600 | 70513.4754 | 0 | 125113.4754 | 88.1511 | 1423.3419 | 10 | 10.02%
[5 empty] | 10.01 | 1144000 | 660 | 100% | 9.133% | 0% | 0.15932 | 54600 | 72430.5037 | 0 | 127030.5037 | 89.4623 | 1444.5137 | 10.01 | 10.17%
[5 empty] | 10.02 | 1144000 | 660 | 100% | 10.15% | 0% | 0.16017 | 54600 | 74347.5319 | 0 | 128947.5319 | 90.7933 | 1466.0049 | 10.02 | 10.33%
[5 empty] | 10.03 | 1144000 | 660 | 100% | 11.17% | 0% | 0.16102 | 54600 | 76264.5601 | 0 | 130864.5601 | 92.1441 | 1487.8157 | 10.03 | 10.48%
[5 empty] | 10.04 | 1144000 | 660 | 100% | 12.19% | 0% | 0.16187 | 54600 | 78181.5884 | 0 | 132781.5884 | 93.5147 | 1509.946 | 10.04 | 10.63%
[5 empty] | 10.05 | 1144000 | 660 | 100% | 13.21% | 0% | 0.16272 | 54600 | 80098.6166 | 0 | 134698.6166 | 94.905 | 1532.3957 | 10.05 | 10.79%
[5 empty] | 10.06 | 1144000 | 660 | 100% | 14.22% | 0% | 0.16357 | 54600 | 82015.6448 | 0 | 136615.6448 | 96.3152 | 1555.165 | 10.06 | 10.94%
[5 empty] | 10.07 | 1144000 | 660 | 100% | 15.24% | 0% | 0.16442 | 54600 | 83932.6731 | 0 | 138532.6731 | 97.7451 | 1578.2538 | 10.07 | 11.1%
[5 empty] | 10.08 | 1144000 | 660 | 100% | 16.26% | 0% | 0.16527 | 54600 | 85849.7013 | 0 | 140449.7013 | 99.1949 | 1601.6621 | 10.08 | 11.25%
[5 empty] | 10.09 | 1144000 | 660 | 100% | 17.28% | 0% | 0.16612 | 54600 | 87766.7295 | 0 | 142366.7295 | 100.6644 | 1625.3898 | 10.09 | 11.4%
[5 empty] | 10.1 | 1144000 | 660 | 100% | 18.3% | 0% | 0.16697 | 54600 | 89683.7578 | 0 | 144283.7578 | 102.1537 | 1649.4371 | 10.1 | 11.56%
[5 empty] | 10.11 | 1144000 | 660 | 100% | 19.31% | 0% | 0.16782 | 54600 | 91600.786 | 0 | 146200.786 | 103.6628 | 1673.8039 | 10.11 | 11.71%
[5 empty] | 10.12 | 1144000 | 660 | 100% | 20.33% | 0% | 0.16867 | 54600 | 93517.8143 | 0 | 148117.8143 | 105.1917 | 1698.4902 | 10.12 | 11.86%
[5 empty] | 10.13 | 1144000 | 660 | 100% | 21.35% | 0% | 0.16952 | 54600 | 95434.8425 | 0 | 150034.8425 | 106.7403 | 1723.496 | 10.13 | 12.02%
[5 empty] | 10.14 | 1144000 | 660 | 100% | 22.37% | 0% | 0.17037 | 54600 | 97351.8707 | 0 | 151951.8707 | 108.3088 | 1748.8214 | 10.14 | 12.17%
[5 empty] | 10.15 | 1144000 | 660 | 100% | 23.39% | 0% | 0.17122 | 54600 | 99268.899 | 0 | 153868.899 | 109.897 | 1774.4662 | 10.15 | 12.32%
[5 empty] | 10.16 | 1144000 | 660 | 100% | 24.4% | 0% | 0.17207 | 54600 | 101185.9272 | 0 | 155785.9272 | 111.5051 | 1800.4305 | 10.16 | 12.48%
[5 empty] | 10.17 | 1144000 | 660 | 100% | 25.42% | 0% | 0.17292 | 54600 | 103102.9554 | 0 | 157702.9554 | 113.1329 | 1826.7143 | 10.17 | 12.63%
[5 empty] | 10.18 | 1144000 | 660 | 100% | 26.44% | 0% | 0.17377 | 54600 | 105019.9837 | 0 | 159619.9837 | 114.7805 | 1853.3177 | 10.18 | 12.78%
[5 empty] | 10.19 | 1144000 | 660 | 100% | 27.46% | 0% | 0.17462 | 54600 | 106937.0119 | 0 | 161537.0119 | 116.4479 | 1880.2405 | 10.19 | 12.94%
[5 empty] | 10.2 | 1144000 | 660 | 100% | 28.48% | 0% | 0.17546 | 54600 | 108854.0401 | 0 | 163454.0401 | 118.1351 | 1907.4828 | 10.2 | 13.09%
[5 empty] | 10.21 | 1144000 | 660 | 100% | 29.49% | 0% | 0.17631 | 54600 | 110771.0684 | 0 | 165371.0684 | 119.8421 | 1935.0447 | 10.21 | 13.25%
[5 empty] | 10.22 | 1144000 | 660 | 100% | 30.51% | 0% | 0.17716 | 54600 | 112688.0966 | 0 | 167288.0966 | 121.5688 | 1962.926 | 10.22 | 13.4%
[5 empty] | 10.23 | 1144000 | 660 | 100% | 31.53% | 0% | 0.17801 | 54600 | 114605.1249 | 0 | 169205.1249 | 123.3154 | 1991.1269 | 10.23 | 13.55%
[5 empty] | 10.24 | 1144000 | 660 | 100% | 32.55% | 0% | 0.17886 | 54600 | 116522.1531 | 0 | 171122.1531 | 125.0817 | 2019.6472 | 10.24 | 13.71%
[5 empty] | 10.25 | 1144000 | 660 | 100% | 33.57% | 0% | 0.17971 | 54600 | 118439.1813 | 0 | 173039.1813 | 126.8678 | 2048.4871 | 10.25 | 13.86%
[5 empty] | 10.26 | 1144000 | 660 | 100% | 34.58% | 0% | 0.18056 | 54600 | 120356.2096 | 0 | 174956.2096 | 128.6737 | 2077.6465 | 10.26 | 14.01%
[5 empty] | 10.27 | 1144000 | 660 | 100% | 35.6% | 0% | 0.18141 | 54600 | 122273.2378 | 0 | 176873.2378 | 130.4994 | 2107.1253 | 10.27 | 14.17%
[5 empty] | 10.28 | 1144000 | 660 | 100% | 36.62% | 0% | 0.18226 | 54600 | 124190.266 | 0 | 178790.266 | 132.3449 | 2136.9237 | 10.28 | 14.32%
[5 empty] | 10.29 | 1144000 | 660 | 100% | 37.64% | 0% | 0.18311 | 54600 | 126107.2943 | 0 | 180707.2943 | 134.2102 | 2167.0416 | 10.29 | 14.47%
[5 empty] | 10.3 | 1144000 | 660 | 100% | 38.66% | 0% | 0.18396 | 54600 | 128024.3225 | 0 | 182624.3225 | 136.0953 | 2197.479 | 10.3 | 14.63%
[5 empty] | 10.31 | 1144000 | 660 | 100% | 39.67% | 0% | 0.18481 | 54600 | 129941.3507 | 0 | 184541.3507 | 138.0001 | 2228.2359 | 10.31 | 14.78%
[5 empty] | 10.32 | 1144000 | 660 | 100% | 40.69% | 0% | 0.18566 | 54600 | 131858.379 | 0 | 186458.379 | 139.9247 | 2259.3123 | 10.32 | 14.93%
[5 empty] | 10.33 | 1144000 | 660 | 100% | 41.71% | 0% | 0.18651 | 54600 | 133775.4072 | 0 | 188375.4072 | 141.8692 | 2290.7082 | 10.33 | 15.09%
[5 empty] | 10.34 | 1144000 | 660 | 100% | 42.73% | 0% | 0.18736 | 54600 | 135692.4355 | 0 | 190292.4355 | 143.8334 | 2322.4236 | 10.34 | 15.24%
[5 empty] | 10.35 | 1144000 | 660 | 100% | 43.75% | 0% | 0.18821 | 54600 | 137609.4637 | 0 | 192209.4637 | 145.8174 | 2354.4585 | 10.35 | 15.39%
[5 empty] | 10.36 | 1144000 | 660 | 100% | 44.76% | 0% | 0.18906 | 54600 | 139526.4919 | 0 | 194126.4919 | 147.8212 | 2386.8129 | 10.36 | 15.55%
[5 empty] | 10.37 | 1144000 | 660 | 100% | 45.78% | 0% | 0.18991 | 54600 | 141443.5202 | 0 | 196043.5202 | 149.8447 | 2419.4868 | 10.37 | 15.7%
[5 empty] | 10.38 | 1144000 | 660 | 100% | 46.8% | 0% | 0.19076 | 54600 | 143360.5484 | 0 | 197960.5484 | 151.8881 | 2452.4803 | 10.38 | 15.86%
[5 empty] | 10.39 | 1144000 | 660 | 100% | 47.82% | 0% | 0.19161 | 54600 | 145277.5766 | 0 | 199877.5766 | 153.9513 | 2485.7932 | 10.39 | 16.01%
[5 empty] | 10.4 | 1144000 | 660 | 100% | 48.84% | 0% | 0.19246 | 54600 | 147194.6049 | 0 | 201794.6049 | 156.0342 | 2519.4256 | 10.4 | 16.16%
[5 empty] | 10.41 | 1144000 | 660 | 100% | 49.85% | 0% | 0.19331 | 54600 | 149111.6331 | 0 | 203711.6331 | 158.1369 | 2553.3776 | 10.41 | 16.32%
[5 empty] | 10.42 | 1144000 | 660 | 100% | 50.87% | 0% | 0.19416 | 54600 | 151028.6613 | 0 | 205628.6613 | 160.2594 | 2587.649 | 10.42 | 16.47%
[5 empty] | 10.43 | 1144000 | 660 | 100% | 51.89% | 0% | 0.19501 | 54600 | 152945.6896 | 0 | 207545.6896 | 162.4017 | 2622.2399 | 10.43 | 16.62%
[5 empty] | 10.44 | 1144000 | 660 | 100% | 52.91% | 0% | 0.19586 | 54600 | 154862.7178 | 0 | 209462.7178 | 164.5638 | 2657.1504 | 10.44 | 16.78%
[5 empty] | 10.45 | 1144000 | 660 | 100% | 53.93% | 0% | 0.19671 | 54600 | 156779.746 | 0 | 211379.746 | 166.7457 | 2692.3804 | 10.45 | 16.93%
[5 empty] | 10.46 | 1144000 | 660 | 100% | 54.94% | 0% | 0.19756 | 54600 | 158696.7743 | 0 | 213296.7743 | 168.9474 | 2727.9298 | 10.46 | 17.08%
[5 empty] | 10.47 | 1144000 | 660 | 100% | 55.96% | 0% | 0.19841 | 54600 | 160613.8025 | 0 | 215213.8025 | 171.1688 | 2763.7988 | 10.47 | 17.24%
[5 empty] | 10.48 | 1144000 | 660 | 100% | 56.98% | 0% | 0.19926 | 54600 | 162530.8308 | 0 | 217130.8308 | 173.4101 | 2799.9873 | 10.48 | 17.39%
[5 empty] | 10.49 | 1144000 | 660 | 100% | 58% | 0% | 0.20011 | 54600 | 164447.859 | 0 | 219047.859 | 175.6711 | 2836.4952 | 10.49 | 17.54%
[5 empty] | 10.5 | 1144000 | 660 | 100% | 59.02% | 0% | 0.20096 | 54600 | 166364.8872 | 0 | 220964.8872 | 177.9519 | 2873.3227 | 10.5 | 17.7%
[5 empty] | 10.51 | 1144000 | 660 | 100% | 60.03% | 0% | 0.20181 | 54600 | 168281.9155 | 0 | 222881.9155 | 180.2525 | 2910.4697 | 10.51 | 17.85%
[5 empty] | 10.52 | 1144000 | 660 | 100% | 61.05% | 0% | 0.20266 | 54600 | 170198.9437 | 0 | 224798.9437 | 182.5729 | 2947.9362 | 10.52 | 18%
[5 empty] | 10.53 | 1144000 | 660 | 100% | 62.07% | 0% | 0.20351 | 54600 | 172115.9719 | 0 | 226715.9719 | 184.9131 | 2985.7222 | 10.53 | 18.16%
[5 empty] | 10.54 | 1144000 | 660 | 100% | 63.09% | 0% | 0.20436 | 54600 | 174033.0002 | 0 | 228633.0002 | 187.2731 | 3023.8277 | 10.54 | 18.31%
[5 empty] | 10.55 | 1144000 | 660 | 100% | 64.11% | 0% | 0.20521 | 54600 | 175950.0284 | 0 | 230550.0284 | 189.6528 | 3062.2527 | 10.55 | 18.47%
[5 empty] | 10.56 | 1144000 | 660 | 100% | 65.12% | 0% | 0.20606 | 54600 | 177867.0566 | 0 | 232467.0566 | 192.0524 | 3100.9972 | 10.56 | 18.62%
[5 empty] | 10.57 | 1144000 | 660 | 100% | 66.14% | 0% | 0.20691 | 54600 | 179784.0849 | 0 | 234384.0849 | 194.4717 | 3140.0612 | 10.57 | 18.77%
[5 empty] | 10.58 | 1144000 | 660 | 100% | 67.16% | 0% | 0.20776 | 54600 | 181701.1131 | 0 | 236301.1131 | 196.9108 | 3179.4447 | 10.58 | 18.93%
[5 empty] | 10.59 | 1144000 | 660 | 100% | 68.18% | 0% | 0.20861 | 54600 | 183618.1414 | 0 | 238218.1414 | 199.3697 | 3219.1478 | 10.59 | 19.08%
[5 empty] | 10.6 | 1144000 | 660 | 100% | 69.2% | 0% | 0.20946 | 54600 | 185535.1696 | 0 | 240135.1696 | 201.8484 | 3259.1703 | 10.6 | 19.23%
[5 empty] | 10.61 | 1144000 | 660 | 100% | 70.21% | 0% | 0.21031 | 54600 | 187452.1978 | 0 | 242052.1978 | 204.3469 | 3299.5123 | 10.61 | 19.39%
[5 empty] | 10.62 | 1144000 | 660 | 100% | 71.23% | 0% | 0.21116 | 54600 | 189369.2261 | 0 | 243969.2261 | 206.8652 | 3340.1739 | 10.62 | 19.54%
[5 empty] | 10.63 | 1144000 | 660 | 100% | 72.25% | 0% | 0.21201 | 54600 | 191286.2543 | 0 | 245886.2543 | 209.4032 | 3381.1549 | 10.63 | 19.69%
[5 empty] | 10.64 | 1144000 | 660 | 100% | 73.27% | 0% | 0.21286 | 54600 | 193203.2825 | 0 | 247803.2825 | 211.9611 | 3422.4554 | 10.64 | 19.85%
[5 empty] | 10.65 | 1144000 | 660 | 100% | 74.29% | 0% | 0.21371 | 54600 | 195120.3108 | 0 | 249720.3108 | 214.5387 | 3464.0755 | 10.65 | 20%
[5 empty] | 10.66 | 1144000 | 660 | 100% | 75.31% | 0% | 0.21456 | 54600 | 197037.339 | 0 | 251637.339 | 217.1361 | 3506.0151 | 10.66 | 20.15%
[5 empty] | 10.67 | 1144000 | 660 | 100% | 76.32% | 0% | 0.21541 | 54600 | 198954.3672 | 0 | 253554.3672 | 219.7533 | 3548.2741 | 10.67 | 20.31%
[5 empty] | 10.68 | 1144000 | 660 | 100% | 77.34% | 0% | 0.21626 | 54600 | 200871.3955 | 0 | 255471.3955 | 222.3903 | 3590.8527 | 10.68 | 20.46%
[5 empty] | 10.69 | 1144000 | 660 | 100% | 78.36% | 0% | 0.21711 | 54600 | 202788.4237 | 0 | 257388.4237 | 225.0471 | 3633.7508 | 10.69 | 20.62%
[5 empty] | 10.7 | 1144000 | 660 | 100% | 79.38% | 0% | 0.21796 | 54600 | 204705.452 | 0 | 259305.452 | 227.7237 | 3676.9683 | 10.7 | 20.77%
[5 empty] | 10.71 | 1144000 | 660 | 100% | 80.4% | 0% | 0.21881 | 54600 | 206622.4802 | 0 | 261222.4802 | 230.42 | 3720.5054 | 10.71 | 20.92%
[5 empty] | 10.72 | 1144000 | 660 | 100% | 81.41% | 0% | 0.21965 | 54600 | 208539.5084 | 0 | 263139.5084 | 233.1362 | 3764.362 | 10.72 | 21.08%
[5 empty] | 10.73 | 1144000 | 660 | 100% | 82.43% | 0% | 0.2205 | 54600 | 210456.5367 | 0 | 265056.5367 | 235.8721 | 3808.5381 | 10.73 | 21.23%
[5 empty] | 10.74 | 1144000 | 660 | 100% | 83.45% | 0% | 0.22135 | 54600 | 212373.5649 | 0 | 266973.5649 | 238.6278 | 3853.0337 | 10.74 | 21.38%
[5 empty] | 10.75 | 1144000 | 660 | 100% | 84.47% | 0% | 0.2222 | 54600 | 214290.5931 | 0 | 268890.5931 | 241.4033 | 3897.8488 | 10.75 | 21.54%
[5 empty] | 10.76 | 1144000 | 660 | 100% | 85.49% | 0% | 0.22305 | 54600 | 216207.6214 | 0 | 270807.6214 | 244.1986 | 3942.9834 | 10.76 | 21.69%
[5 empty] | 10.77 | 1144000 | 660 | 100% | 86.5% | 0% | 0.2239 | 54600 | 218124.6496 | 0 | 272724.6496 | 247.0137 | 3988.4375 | 10.77 | 21.84%
[5 empty] | 10.78 | 1144000 | 660 | 100% | 87.52% | 0% | 0.22475 | 54600 | 220041.6778 | 0 | 274641.6778 | 249.8486 | 4034.2111 | 10.78 | 22%
[5 empty] | 10.79 | 1144000 | 660 | 100% | 88.54% | 0% | 0.2256 | 54600 | 221958.7061 | 0 | 276558.7061 | 252.7032 | 4080.3042 | 10.79 | 22.15%
[5 empty] | 10.8 | 1144000 | 660 | 100% | 89.56% | 0% | 0.22645 | 54600 | 223875.7343 | 0 | 278475.7343 | 255.5777 | 4126.7168 | 10.8 | 22.3%
[5 empty] | 10.81 | 1144000 | 660 | 100% | 90.58% | 0% | 0.2273 | 54600 | 225792.7626 | 0 | 280392.7626 | 258.4719 | 4173.449 | 10.81 | 22.46%
[5 empty] | 10.82 | 1144000 | 660 | 100% | 91.59% | 0% | 0.22815 | 54600 | 227709.7908 | 0 | 282309.7908 | 261.3859 | 4220.5006 | 10.82 | 22.61%
[5 empty] | 10.83 | 1144000 | 660 | 100% | 92.61% | 0% | 0.229 | 54600 | 229626.819 | 0 | 284226.819 | 264.3198 | 4267.8717 | 10.83 | 22.76%
[5 empty] | 10.84 | 1144000 | 660 | 100% | 93.63% | 0% | 0.22985 | 54600 | 231543.8473 | 0 | 286143.8473 | 267.2734 | 4315.5624 | 10.84 | 22.92%
[5 empty] | 10.85 | 1144000 | 660 | 100% | 94.65% | 0% | 0.2307 | 54600 | 233460.8755 | 0 | 288060.8755 | 270.2467 | 4363.5725 | 10.85 | 23.07%
[5 empty] | 10.86 | 1144000 | 660 | 100% | 95.67% | 0% | 0.23155 | 54600 | 235377.9037 | 0 | 289977.9037 | 273.2399 | 4411.9022 | 10.86 | 23.23%
[5 empty] | 10.87 | 1144000 | 660 | 100% | 96.68% | 0% | 0.2324 | 54600 | 237294.932 | 0 | 291894.932 | 276.2529 | 4460.5513 | 10.87 | 23.38%
[5 empty] | 10.88 | 1144000 | 660 | 100% | 97.7% | 0% | 0.23325 | 54600 | 239211.9602 | 0 | 293811.9602 | 279.2856 | 4509.52 | 10.88 | 23.53%
[5 empty] | 10.89 | 1144000 | 660 | 100% | 98.72% | 0% | 0.2341 | 54600 | 241128.9884 | 0 | 295728.9884 | 282.3382 | 4558.8082 | 10.89 | 23.69%
[5 empty] | 10.9 | 1144000 | 660 | 100% | 99.74% | 0% | 0.23495 | 54600 | 243046.0167 | 0 | 297646.0167 | 285.4105 | 4608.4158 | 10.9 | 23.84%
[5 empty] | 10.91 | 1144000 | 660 | 100% | 100.8% | 0.08248% | 0.23643 | 54600 | 244963.0449 | 519939.0164 | 819502.0613 | 293.8694 | 4744.9995 | 10.91 | 65.64%
[5 empty] | 10.92 | 1144000 | 660 | 100% | 100% | 0.1936% | 0.23665 | 54600 | 243540 | 520417.7012 | 818557.7012 | 302.3187 | 4881.4258 | 10.92 | 65.56%
[5 empty] | 10.93 | 1144000 | 660 | 100% | 100% | 0.3047% | 0.2375 | 54600 | 243540 | 520896.386 | 819036.386 | 310.7728 | 5017.9319 | 10.93 | 65.6%
[5 empty] | 10.94 | 1144000 | 660 | 100% | 100% | 0.4158% | 0.23835 | 54600 | 243540 | 521375.0708 | 819515.0708 | 319.2319 | 5154.5177 | 10.94 | 65.64%
[5 empty] | 10.95 | 1144000 | 660 | 100% | 100% | 0.5269% | 0.2392 | 54600 | 243540 | 521853.7556 | 819993.7556 | 327.6959 | 5291.1833 | 10.95 | 65.68%
[5 empty] | 10.96 | 1144000 | 660 | 100% | 100% | 0.638% | 0.24005 | 54600 | 243540 | 522332.4404 | 820472.4404 | 336.1649 | 5427.9287 | 10.96 | 65.71%
[5 empty] | 10.97 | 1144000 | 660 | 100% | 100% | 0.7491% | 0.2409 | 54600 | 243540 | 522811.1252 | 820951.1252 | 344.6388 | 5564.7539 | 10.97 | 65.75%
[5 empty] | 10.98 | 1144000 | 660 | 100% | 100% | 0.8603% | 0.24175 | 54600 | 243540 | 523289.81 | 821429.81 | 353.1177 | 5701.6589 | 10.98 | 65.79%
[5 empty] | 10.99 | 1144000 | 660 | 100% | 100% | 0.9714% | 0.2426 | 54600 | 243540 | 523768.4948 | 821908.4948 | 361.6015 | 5838.6436 | 10.99 | 65.83%
[5 empty] | 11 | 1144000 | 660 | 100% | 100% | 1.082% | 0.24345 | 54600 | 243540 | 524247.1796 | 822387.1796 | 370.0902 | 5975.7082 | 11 | 65.87%
[5 empty] | 11.01 | 1144000 | 660 | 100% | 100% | 1.194% | 0.2443 | 54600 | 243540 | 524725.8644 | 822865.8644 | 378.5839 | 6112.8525 | 11.01 | 65.91%
[5 empty] | 11.02 | 1144000 | 660 | 100% | 100% | 1.305% | 0.24515 | 54600 | 243540 | 525204.5492 | 823344.5492 | 387.0826 | 6250.0766 | 11.02 | 65.94%
[5 empty] | 11.03 | 1144000 | 660 | 100% | 100% | 1.416% | 0.246 | 54600 | 243540 | 525683.234 | 823823.234 | 395.5861 | 6387.3804 | 11.03 | 65.98%
[5 empty] | 11.04 | 1144000 | 660 | 100% | 100% | 1.527% | 0.24685 | 54600 | 243540 | 526161.9188 | 824301.9188 | 404.0946 | 6524.7641 | 11.04 | 66.02%
[5 empty] | 11.05 | 1144000 | 660 | 100% | 100% | 1.638% | 0.2477 | 54600 | 243540 | 526640.6036 | 824780.6036 | 412.6081 | 6662.2275 | 11.05 | 66.06%
[5 empty] | 11.06 | 1144000 | 660 | 100% | 100% | 1.749% | 0.24855 | 54600 | 243540 | 527119.2884 | 825259.2884 | 421.1265 | 6799.7707 | 11.06 | 66.1%
[5 empty] | 11.07 | 1144000 | 660 | 100% | 100% | 1.86% | 0.2494 | 54600 | 243540 | 527597.9732 | 825737.9732 | 429.6498 | 6937.3937 | 11.07 | 66.14%
[5 empty] | 11.08 | 1144000 | 660 | 100% | 100% | 1.971% | 0.25025 | 54600 | 243540 | 528076.658 | 826216.658 | 438.1781 | 7075.0965 | 11.08 | 66.17%
[5 empty] | 11.09 | 1144000 | 660 | 100% | 100% | 2.082% | 0.2511 | 54600 | 243540 | 528555.3428 | 826695.3428 | 446.7113 | 7212.8791 | 11.09 | 66.21%
[5 empty] | 11.1 | 1144000 | 660 | 100% | 100% | 2.194% | 0.25195 | 54600 | 243540 | 529034.0276 | 827174.0276 | 455.2494 | 7350.7414 | 11.1 | 66.25%
[5 empty] | 11.11 | 1144000 | 660 | 100% | 100% | 2.305% | 0.2528 | 54600 | 243540 | 529512.7124 | 827652.7124 | 463.7925 | 7488.6835 | 11.11 | 66.29%
[5 empty] | 11.12 | 1144000 | 660 | 100% | 100% | 2.416% | 0.25365 | 54600 | 243540 | 529991.3972 | 828131.3972 | 472.3406 | 7626.7054 | 11.12 | 66.33%
[5 empty] | 11.13 | 1144000 | 660 | 100% | 100% | 2.527% | 0.2545 | 54600 | 243540 | 530470.082 | 828610.082 | 480.8935 | 7764.8071 | 11.13 | 66.37%
[5 empty] | 11.14 | 1144000 | 660 | 100% | 100% | 2.638% | 0.25535 | 54600 | 243540 | 530948.7668 | 829088.7668 | 489.4514 | 7902.9886 | 11.14 | 66.4%
[5 empty] | 11.15 | 1144000 | 660 | 100% | 100% | 2.749% | 0.2562 | 54600 | 243540 | 531427.4516 | 829567.4516 | 498.0143 | 8041.2498 | 11.15 | 66.44%
[5 empty] | 11.16 | 1144000 | 660 | 100% | 100% | 2.86% | 0.25705 | 54600 | 243540 | 531906.1364 | 830046.1364 | 506.5821 | 8179.5908 | 11.16 | 66.48%
[5 empty] | 11.17 | 1144000 | 660 | 100% | 100% | 2.971% | 0.2579 | 54600 | 243540 | 532384.8212 | 830524.8212 | 515.1548 | 8318.0116 | 11.17 | 66.52%
[5 empty] | 11.18 | 1144000 | 660 | 100% | 100% | 3.082% | 0.25875 | 54600 | 243540 | 532863.506 | 831003.506 | 523.7325 | 8456.5122 | 11.18 | 66.56%
[5 empty] | 11.19 | 1144000 | 660 | 100% | 100% | 3.194% | 0.2596 | 54600 | 243540 | 533342.1908 | 831482.1908 | 532.3151 | 8595.0926 | 11.19 | 66.6%
[5 empty] | 11.2 | 1144000 | 660 | 100% | 100% | 3.305% | 0.26045 | 54600 | 243540 | 533820.8756 | 831960.8756 | 540.9027 | 8733.7527 | 11.2 | 66.63%
[5 empty] | 11.21 | 1144000 | 660 | 100% | 100% | 3.416% | 0.2613 | 54600 | 243540 | 534299.5604 | 832439.5604 | 549.4952 | 8872.4927 | 11.21 | 66.67%
[5 empty] | 11.22 | 1144000 | 660 | 100% | 100% | 3.527% | 0.26215 | 54600 | 243540 | 534778.2452 | 832918.2452 | 558.0927 | 9011.3124 | 11.22 | 66.71%
[5 empty] | 11.23 | 1144000 | 660 | 100% | 100% | 3.638% | 0.263 | 54600 | 243540 | 535256.93 | 833396.93 | 566.695 | 9150.2119 | 11.23 | 66.75%
[5 empty] | 11.24 | 1144000 | 660 | 100% | 100% | 3.749% | 0.26385 | 54600 | 243540 | 535735.6148 | 833875.6148 | 575.3024 | 9289.1911 | 11.24 | 66.79%
[5 empty] | 11.25 | 1144000 | 660 | 100% | 100% | 3.86% | 0.26469 | 54600 | 243540 | 536214.2996 | 834354.2996 | 583.9146 | 9428.2502 | 11.25 | 66.83%
[5 empty] | 11.26 | 1144000 | 660 | 100% | 100% | 3.971% | 0.26554 | 54600 | 243540 | 536692.9844 | 834832.9844 | 592.5318 | 9567.389 | 11.26 | 66.86%
[5 empty] | 11.27 | 1144000 | 660 | 100% | 100% | 4.082% | 0.26639 | 54600 | 243540 | 537171.6692 | 835311.6692 | 601.154 | 9706.6076 | 11.27 | 66.9%
[5 empty] | 11.28 | 1144000 | 660 | 100% | 100% | 4.194% | 0.26724 | 54600 | 243540 | 537650.354 | 835790.354 | 609.7811 | 9845.906 | 11.28 | 66.94%
[5 empty] | 11.29 | 1144000 | 660 | 100% | 100% | 4.305% | 0.26809 | 54600 | 243540 | 538129.0388 | 836269.0388 | 618.4131 | 9985.2842 | 11.29 | 66.98%
[5 empty] | 11.3 | 1144000 | 660 | 100% | 100% | 4.416% | 0.26894 | 54600 | 243540 | 538607.7236 | 836747.7236 | 627.0501 | 10124.7421 | 11.3 | 67.02%
[5 empty] | 11.31 | 1144000 | 660 | 100% | 100% | 4.527% | 0.26979 | 54600 | 243540 | 539086.4084 | 837226.4084 | 635.692 | 10264.2799 | 11.31 | 67.06%
[5 empty] | 11.32 | 1144000 | 660 | 100% | 100% | 4.638% | 0.27064 | 54600 | 243540 | 539565.0932 | 837705.0932 | 644.3389 | 10403.8974 | 11.32 | 67.09%
[5 empty] | 11.33 | 1144000 | 660 | 100% | 100% | 4.749% | 0.27149 | 54600 | 243540 | 540043.778 | 838183.778 | 652.9907 | 10543.5947 | 11.33 | 67.13%
[5 empty] | 11.34 | 1144000 | 660 | 100% | 100% | 4.86% | 0.27234 | 54600 | 243540 | 540522.4628 | 838662.4628 | 661.6474 | 10683.3718 | 11.34 | 67.17%
[5 empty] | 11.35 | 1144000 | 660 | 100% | 100% | 4.971% | 0.27319 | 54600 | 243540 | 541001.1476 | 839141.1476 | 670.3091 | 10823.2286 | 11.35 | 67.21%
[5 empty] | 11.36 | 1144000 | 660 | 100% | 100% | 5.082% | 0.27404 | 54600 | 243540 | 541479.8324 | 839619.8324 | 678.9757 | 10963.1653 | 11.36 | 67.25%
[5 empty] | 11.37 | 1144000 | 660 | 100% | 100% | 5.194% | 0.27489 | 54600 | 243540 | 541958.5172 | 840098.5172 | 687.6472 | 11103.1817 | 11.37 | 67.29%
[5 empty] | 11.38 | 1144000 | 660 | 100% | 100% | 5.305% | 0.27574 | 54600 | 243540 | 542437.202 | 840577.202 | 696.3237 | 11243.2779 | 11.38 | 67.32%
[5 empty] | 11.39 | 1144000 | 660 | 100% | 100% | 5.416% | 0.27659 | 54600 | 243540 | 542915.8868 | 841055.8868 | 705.0052 | 11383.4539 | 11.39 | 67.36%
[5 empty] | 11.4 | 1144000 | 660 | 100% | 100% | 5.527% | 0.27744 | 54600 | 243540 | 543394.5716 | 841534.5716 | 713.6916 | 11523.7096 | 11.4 | 67.4%
[5 empty] | 11.41 | 1144000 | 660 | 100% | 100% | 5.638% | 0.27829 | 54600 | 243540 | 543873.2564 | 842013.2564 | 722.3829 | 11664.0452 | 11.41 | 67.44%
[5 empty] | 11.42 | 1144000 | 660 | 100% | 100% | 5.749% | 0.27914 | 54600 | 243540 | 544351.9412 | 842491.9412 | 731.0792 | 11804.4605 | 11.42 | 67.48%
[5 empty] | 11.43 | 1144000 | 660 | 100% | 100% | 5.86% | 0.27999 | 54600 | 243540 | 544830.626 | 842970.626 | 739.7804 | 11944.9556 | 11.43 | 67.52%
[5 empty] | 11.44 | 1144000 | 660 | 100% | 100% | 5.971% | 0.28084 | 54600 | 243540 | 545309.3108 | 843449.3108 | 748.4865 | 12085.5305 | 11.44 | 67.55%
[5 empty] | 11.45 | 1144000 | 660 | 100% | 100% | 6.082% | 0.28169 | 54600 | 243540 | 545787.9956 | 843927.9956 | 757.1976 | 12226.1851 | 11.45 | 67.59%
[5 empty] | 11.46 | 1144000 | 660 | 100% | 100% | 6.194% | 0.28254 | 54600 | 243540 | 546266.6804 | 844406.6804 | 765.9136 | 12366.9196 | 11.46 | 67.63%
[5 empty] | 11.47 | 1144000 | 660 | 100% | 100% | 6.305% | 0.28339 | 54600 | 243540 | 546745.3652 | 844885.3652 | 774.6346 | 12507.7338 | 11.47 | 67.67%
[5 empty] | 11.48 | 1144000 | 660 | 100% | 100% | 6.416% | 0.28424 | 54600 | 243540 | 547224.05 | 845364.05 | 783.3605 | 12648.6278 | 11.48 | 67.71%
[5 empty] | 11.49 | 1144000 | 660 | 100% | 100% | 6.527% | 0.28509 | 54600 | 243540 | 547702.7348 | 845842.7348 | 792.0914 | 12789.6016 | 11.49 | 67.75%
[5 empty] | 11.5 | 1144000 | 660 | 100% | 100% | 6.638% | 0.28594 | 54600 | 243540 | 548181.4196 | 846321.4196 | 800.8272 | 12930.6552 | 11.5 | 67.78%
[5 empty] | 11.51 | 1144000 | 660 | 100% | 100% | 6.749% | 0.28679 | 54600 | 243540 | 548660.1044 | 846800.1044 | 809.5679 | 13071.7885 | 11.51 | 67.82%
[5 empty] | 11.52 | 1144000 | 660 | 100% | 100% | 6.86% | 0.28764 | 54600 | 243540 | 549138.7892 | 847278.7892 | 818.3136 | 13213.0017 | 11.52 | 67.86%
[5 empty] | 11.53 | 1144000 | 660 | 100% | 100% | 6.971% | 0.28849 | 54600 | 243540 | 549617.474 | 847757.474 | 827.0642 | 13354.2946 | 11.53 | 67.9%
[5 empty] | 11.54 | 1144000 | 660 | 100% | 100% | 7.082% | 0.28934 | 54600 | 243540 | 550096.1588 | 848236.1588 | 835.8197 | 13495.6673 | 11.54 | 67.94%
[5 empty] | 11.55 | 1144000 | 660 | 100% | 100% | 7.194% | 0.29019 | 54600 | 243540 | 550574.8436 | 848714.8436 | 844.5802 | 13637.1197 | 11.55 | 67.98%
[5 empty] | 11.56 | 1144000 | 660 | 100% | 100% | 7.305% | 0.29104 | 54600 | 243540 | 551053.5284 | 849193.5284 | 853.3457 | 13778.652 | 11.56 | 68.01%
[5 empty] | 11.57 | 1144000 | 660 | 100% | 100% | 7.416% | 0.29189 | 54600 | 243540 | 551532.2132 | 849672.2132 | 862.1161 | 13920.264 | 11.57 | 68.05%
[5 empty] | 11.58 | 1144000 | 660 | 100% | 100% | 7.527% | 0.29274 | 54600 | 243540 | 552010.898 | 850150.898 | 870.8914 | 14061.9558 | 11.58 | 68.09%
[5 empty] | 11.59 | 1144000 | 660 | 100% | 100% | 7.638% | 0.29359 | 54600 | 243540 | 552489.5828 | 850629.5828 | 879.6716 | 14203.7274 | 11.59 | 68.13%
[5 empty] | 11.6 | 1144000 | 660 | 100% | 100% | 7.749% | 0.29444 | 54600 | 243540 | 552968.2676 | 851108.2676 | 888.4568 | 14345.5788 | 11.6 | 68.17%
[5 empty] | 11.61 | 1144000 | 660 | 100% | 100% | 7.86% | 0.29529 | 54600 | 243540 | 553446.9524 | 851586.9524 | 897.247 | 14487.51 | 11.61 | 68.21%
[5 empty] | 11.62 | 1144000 | 660 | 100% | 100% | 7.971% | 0.29614 | 54600 | 243540 | 553925.6372 | 852065.6372 | 906.0421 | 14629.5209 | 11.62 | 68.24%
[5 empty] | 11.63 | 1144000 | 660 | 100% | 100% | 8.082% | 0.29699 | 54600 | 243540 | 554404.322 | 852544.322 | 914.8421 | 14771.6116 | 11.63 | 68.28%
[5 empty] | 11.64 | 1144000 | 660 | 100% | 100% | 8.194% | 0.29784 | 54600 | 243540 | 554883.0068 | 853023.0068 | 923.6471 | 14913.7821 | 11.64 | 68.32%
[5 empty] | 11.65 | 1144000 | 660 | 100% | 100% | 8.305% | 0.29869 | 54600 | 243540 | 555361.6916 | 853501.6916 | 932.457 | 15056.0324 | 11.65 | 68.36%
[5 empty] | 11.66 | 1144000 | 660 | 100% | 100% | 8.416% | 0.29954 | 54600 | 243540 | 555840.3764 | 853980.3764 | 941.2718 | 15198.3625 | 11.66 | 68.4%
[5 empty] | 11.67 | 1144000 | 660 | 100% | 100% | 8.527% | 0.30039 | 54600 | 243540 | 556319.0612 | 854459.0612 | 950.0916 | 15340.7723 | 11.67 | 68.44%
[5 empty] | 11.68 | 1144000 | 660 | 100% | 100% | 8.638% | 0.30124 | 54600 | 243540 | 556797.746 | 854937.746 | 958.9163 | 15483.262 | 11.68 | 68.47%
[5 empty] | 11.69 | 1144000 | 660 | 100% | 100% | 8.749% | 0.30209 | 54600 | 243540 | 557276.4308 | 855416.4308 | 967.746 | 15625.8314 | 11.69 | 68.51%
[5 empty] | 11.7 | 1144000 | 660 | 100% | 100% | 8.86% | 0.30294 | 54600 | 243540 | 557755.1156 | 855895.1156 | 976.5806 | 15768.4805 | 11.7 | 68.55%
[5 empty] | 11.71 | 1144000 | 660 | 100% | 100% | 8.971% | 0.30379 | 54600 | 243540 | 558233.8004 | 856373.8004 | 985.4202 | 15911.2095 | 11.71 | 68.59%
[5 empty] | 11.72 | 1144000 | 660 | 100% | 100% | 9.082% | 0.30464 | 54600 | 243540 | 558712.4852 | 856852.4852 | 994.2647 | 16054.0183 | 11.72 | 68.63%
[5 empty] | 11.73 | 1144000 | 660 | 100% | 100% | 9.194% | 0.30549 | 54600 | 243540 | 559191.17 | 857331.17 | 1003.1141 | 16196.9068 | 11.73 | 68.67%
[5 empty] | 11.74 | 1144000 | 660 | 100% | 100% | 9.305% | 0.30634 | 54600 | 243540 | 559669.8548 | 857809.8548 | 1011.9685 | 16339.8751 | 11.74 | 68.71%
[5 empty] | 11.75 | 1144000 | 660 | 100% | 100% | 9.416% | 0.30719 | 54600 | 243540 | 560148.5396 | 858288.5396 | 1020.8278 | 16482.9232 | 11.75 | 68.74%
[5 empty] | 11.76 | 1144000 | 660 | 100% | 100% | 9.527% | 0.30804 | 54600 | 243540 | 560627.2244 | 858767.2244 | 1029.6921 | 16626.0511 | 11.76 | 68.78%
[5 empty] | 11.77 | 1144000 | 660 | 100% | 100% | 9.638% | 0.30889 | 54600 | 243540 | 561105.9092 | 859245.9092 | 1038.5613 | 16769.2587 | 11.77 | 68.82%
[5 empty] | 11.78 | 1144000 | 660 | 100% | 100% | 9.749% | 0.30973 | 54600 | 243540 | 561584.594 | 859724.594 | 1047.4354 | 16912.5461 | 11.78 | 68.86%
[5 empty] | 11.79 | 1144000 | 660 | 100% | 100% | 9.86% | 0.31058 | 54600 | 243540 | 562063.2788 | 860203.2788 | 1056.3145 | 17055.9134 | 11.79 | 68.9%
[5 empty] | 11.8 | 1144000 | 660 | 100% | 100% | 9.971% | 0.31143 | 54600 | 243540 | 562541.9636 | 860681.9636 | 1065.1985 | 17199.3604 | 11.8 | 68.94%
[5 empty] | 11.81 | 1144000 | 660 | 100% | 100% | 10.08% | 0.31228 | 54600 | 243540 | 563020.6484 | 861160.6484 | 1074.0875 | 17342.8871 | 11.81 | 68.97%
[5 empty] | 11.82 | 1144000 | 660 | 100% | 100% | 10.19% | 0.31313 | 54600 | 243540 | 563499.3332 | 861639.3332 | 1082.9814 | 17486.4937 | 11.82 | 69.01%
[5 empty] | 11.83 | 1144000 | 660 | 100% | 100% | 10.3% | 0.31398 | 54600 | 243540 | 563978.018 | 862118.018 | 1091.8802 | 17630.18 | 11.83 | 69.05%
[5 empty] | 11.84 | 1144000 | 660 | 100% | 100% | 10.42% | 0.31483 | 54600 | 243540 | 564456.7028 | 862596.7028 | 1100.784 | 17773.9461 | 11.84 | 69.09%
[5 empty] | 11.85 | 1144000 | 660 | 100% | 100% | 10.53% | 0.31568 | 54600 | 243540 | 564935.3876 | 863075.3876 | 1109.6928 | 17917.792 | 11.85 | 69.13%
[5 empty] | 11.86 | 1144000 | 660 | 100% | 100% | 10.64% | 0.31653 | 54600 | 243540 | 565414.0724 | 863554.0724 | 1118.6064 | 18061.7177 | 11.86 | 69.17%
[5 empty] | 11.87 | 1144000 | 660 | 100% | 100% | 10.75% | 0.31738 | 54600 | 243540 | 565892.7572 | 864032.7572 | 1127.525 | 18205.7232 | 11.87 | 69.2%
[5 empty] | 11.88 | 1144000 | 660 | 100% | 100% | 10.86% | 0.31823 | 54600 | 243540 | 566371.442 | 864511.442 | 1136.4486 | 18349.8084 | 11.88 | 69.24%
[5 empty] | 11.89 | 1144000 | 660 | 100% | 100% | 10.97% | 0.31908 | 54600 | 243540 | 566850.1268 | 864990.1268 | 1145.3771 | 18493.9734 | 11.89 | 69.28%
[5 empty] | 11.9 | 1144000 | 660 | 100% | 100% | 11.08% | 0.31993 | 54600 | 243540 | 567328.8116 | 865468.8116 | 1154.3105 | 18638.2182 | 11.9 | 69.32%
[5 empty] | 11.91 | 1144000 | 660 | 100% | 100% | 11.19% | 0.32078 | 54600 | 243540 | 567807.4964 | 865947.4964 | 1163.2489 | 18782.5428 | 11.91 | 69.36%
[5 empty] | 11.92 | 1144000 | 660 | 100% | 100% | 11.3% | 0.32163 | 54600 | 243540 | 568286.1812 | 866426.1812 | 1172.1922 | 18926.9472 | 11.92 | 69.4%
[5 empty] | 11.93 | 1144000 | 660 | 100% | 100% | 11.42% | 0.32248 | 54600 | 243540 | 568764.866 | 866904.866 | 1181.1405 | 19071.4313 | 11.93 | 69.43%
[5 empty] | 11.94 | 1144000 | 660 | 100% | 100% | 11.53% | 0.32333 | 54600 | 243540 | 569243.5508 | 867383.5508 | 1190.0937 | 19215.9952 | 11.94 | 69.47%
[5 empty] | 11.95 | 1144000 | 660 | 100% | 100% | 11.64% | 0.32418 | 54600 | 243540 | 569722.2356 | 867862.2356 | 1199.0518 | 19360.639 | 11.95 | 69.51%
[5 empty] | 11.96 | 1144000 | 660 | 100% | 100% | 11.75% | 0.32503 | 54600 | 243540 | 570200.9204 | 868340.9204 | 1208.0149 | 19505.3624 | 11.96 | 69.55%
[5 empty] | 11.97 | 1144000 | 660 | 100% | 100% | 11.86% | 0.32588 | 54600 | 243540 | 570679.6052 | 868819.6052 | 1216.9829 | 19650.1657 | 11.97 | 69.59%
[5 empty] | 11.98 | 1144000 | 660 | 100% | 100% | 11.97% | 0.32673 | 54600 | 243540 | 571158.29 | 869298.29 | 1225.9559 | 19795.0488 | 11.98 | 69.63%
[5 empty] | 11.99 | 1144000 | 660 | 100% | 100% | 12.08% | 0.32758 | 54600 | 243540 | 571636.9748 | 869776.9748 | 1234.9338 | 19940.0116 | 11.99 | 69.66%
[5 empty] | 12 | 1144000 | 660 | 100% | 100% | 12.19% | 0.32843 | 54600 | 243540 | 572115.6596 | 870255.6596 | 1243.9166 | 20085.0542 | 12 | 69.7%
[5 empty] | 12.01 | 1144000 | 660 | 100% | 100% | 12.3% | 0.32928 | 54600 | 243540 | 572594.3444 | 870734.3444 | 1252.9044 | 20230.1766 | 12.01 | 69.74%
[5 empty] | 12.02 | 1144000 | 660 | 100% | 100% | 12.42% | 0.33013 | 54600 | 243540 | 573073.0292 | 871213.0292 | 1261.8971 | 20375.3788 | 12.02 | 69.78%
[5 empty] | 12.03 | 1144000 | 660 | 100% | 100% | 12.53% | 0.33098 | 54600 | 243540 | 573551.714 | 871691.714 | 1270.8948 | 20520.6607 | 12.03 | 69.82%
[5 empty] | 12.04 | 1144000 | 660 | 100% | 100% | 12.64% | 0.33183 | 54600 | 243540 | 574030.3988 | 872170.3988 | 1279.8974 | 20666.0224 | 12.04 | 69.86%
[5 empty] | 12.05 | 1144000 | 660 | 100% | 100% | 12.75% | 0.33268 | 54600 | 243540 | 574509.0836 | 872649.0836 | 1288.905 | 20811.464 | 12.05 | 69.89%
[5 empty] | 12.06 | 1144000 | 660 | 100% | 100% | 12.86% | 0.33353 | 54600 | 243540 | 574987.7684 | 873127.7684 | 1297.9174 | 20956.9853 | 12.06 | 69.93%
[5 empty] | 12.07 | 1144000 | 660 | 100% | 100% | 12.97% | 0.33438 | 54600 | 243540 | 575466.4532 | 873606.4532 | 1306.9349 | 21102.5863 | 12.07 | 69.97%
[5 empty] | 12.08 | 1144000 | 660 | 100% | 100% | 13.08% | 0.33523 | 54600 | 243540 | 575945.138 | 874085.138 | 1315.9572 | 21248.2672 | 12.08 | 70.01%
[5 empty] | 12.09 | 1144000 | 660 | 100% | 100% | 13.19% | 0.33608 | 54600 | 243540 | 576423.8228 | 874563.8228 | 1324.9846 | 21394.0278 | 12.09 | 70.05%
[5 empty] | 12.1 | 1144000 | 660 | 100% | 100% | 13.3% | 0.33693 | 54600 | 243540 | 576902.5076 | 875042.5076 | 1334.0168 | 21539.8682 | 12.1 | 70.09%
[5 empty] | 12.11 | 1144000 | 660 | 100% | 100% | 13.42% | 0.33778 | 54600 | 243540 | 577381.1924 | 875521.1924 | 1343.054 | 21685.7884 | 12.11 | 70.12%
[5 empty] | 12.12 | 1144000 | 660 | 100% | 100% | 13.53% | 0.33863 | 54600 | 243540 | 577859.8772 | 875999.8772 | 1352.0961 | 21831.7884 | 12.12 | 70.16%
[5 empty] | 12.13 | 1144000 | 660 | 100% | 100% | 13.64% | 0.33948 | 54600 | 243540 | 578338.562 | 876478.562 | 1361.1432 | 21977.8682 | 12.13 | 70.2%
[5 empty] | 12.14 | 1144000 | 660 | 100% | 100% | 13.75% | 0.34033 | 54600 | 243540 | 578817.2468 | 876957.2468 | 1370.1952 | 22124.0277 | 12.14 | 70.24%
[5 empty] | 12.15 | 1144000 | 660 | 100% | 100% | 13.86% | 0.34118 | 54600 | 243540 | 579295.9316 | 877435.9316 | 1379.2522 | 22270.267 | 12.15 | 70.28%
[5 empty] | 12.16 | 1144000 | 660 | 100% | 100% | 13.97% | 0.34203 | 54600 | 243540 | 579774.6164 | 877914.6164 | 1388.3141 | 22416.5861 | 12.16 | 70.32%
[5 empty] | 12.17 | 1144000 | 660 | 100% | 100% | 14.08% | 0.34288 | 54600 | 243540 | 580253.3012 | 878393.3012 | 1397.3809 | 22562.985 | 12.17 | 70.35%
[5 empty] | 12.18 | 1144000 | 660 | 100% | 100% | 14.19% | 0.34373 | 54600 | 243540 | 580731.986 | 878871.986 | 1406.4527 | 22709.4637 | 12.18 | 70.39%
[5 empty] | 12.19 | 1144000 | 660 | 100% | 100% | 14.3% | 0.34458 | 54600 | 243540 | 581210.6708 | 879350.6708 | 1415.5295 | 22856.0221 | 12.19 | 70.43%
[5 empty] | 12.2 | 1144000 | 660 | 100% | 100% | 14.42% | 0.34543 | 54600 | 243540 | 581689.3556 | 879829.3556 | 1424.6111 | 23002.6604 | 12.2 | 70.47%
[5 empty] | 12.21 | 1144000 | 660 | 100% | 100% | 14.53% | 0.34628 | 54600 | 243540 | 582168.0404 | 880308.0404 | 1433.6977 | 23149.3784 | 12.21 | 70.51%
[5 empty] | 12.22 | 1144000 | 660 | 100% | 100% | 14.64% | 0.34713 | 54600 | 243540 | 582646.7252 | 880786.7252 | 1442.7893 | 23296.1762 | 12.22 | 70.55%
[5 empty] | 12.23 | 1144000 | 660 | 100% | 100% | 14.75% | 0.34798 | 54600 | 243540 | 583125.41 | 881265.41 | 1451.8858 | 23443.0537 | 12.23 | 70.58%
[5 empty] | 12.24 | 1144000 | 660 | 100% | 100% | 14.86% | 0.34883 | 54600 | 243540 | 583604.0948 | 881744.0948 | 1460.9872 | 23590.0111 | 12.24 | 70.62%
[5 empty] | 12.25 | 1144000 | 660 | 100% | 100% | 14.97% | 0.34968 | 54600 | 243540 | 584082.7796 | 882222.7796 | 1470.0936 | 23737.0482 | 12.25 | 70.66%
[5 empty] | 12.26 | 1144000 | 660 | 100% | 100% | 15.08% | 0.35053 | 54600 | 243540 | 584561.4644 | 882701.4644 | 1479.2049 | 23884.1651 | 12.26 | 70.7%
[5 empty] | 12.27 | 1144000 | 660 | 100% | 100% | 15.19% | 0.35138 | 54600 | 243540 | 585040.1492 | 883180.1492 | 1488.3211 | 24031.3618 | 12.27 | 70.74%
[5 empty] | 12.28 | 1144000 | 660 | 100% | 100% | 15.3% | 0.35223 | 54600 | 243540 | 585518.834 | 883658.834 | 1497.4423 | 24178.6383 | 12.28 | 70.78%
[5 empty] | 12.29 | 1144000 | 660 | 100% | 100% | 15.42% | 0.35308 | 54600 | 243540 | 585997.5188 | 884137.5188 | 1506.5684 | 24325.9945 | 12.29 | 70.81%
[5 empty] | 12.3 | 1144000 | 660 | 100% | 100% | 15.53% | 0.35393 | 54600 | 243540 | 586476.2036 | 884616.2036 | 1515.6995 | 24473.4306 | 12.3 | 70.85%
[5 empty] | 12.31 | 1144000 | 660 | 100% | 100% | 15.64% | 0.35477 | 54600 | 243540 | 586954.8884 | 885094.8884 | 1524.8355 | 24620.9464 | 12.31 | 70.89%
[5 empty] | 12.32 | 1144000 | 660 | 100% | 100% | 15.75% | 0.35562 | 54600 | 243540 | 587433.5732 | 885573.5732 | 1533.9765 | 24768.542 | 12.32 | 70.93%
[5 empty] | 12.33 | 1144000 | 660 | 100% | 100% | 15.86% | 0.35647 | 54600 | 243540 | 587912.258 | 886052.258 | 1543.1224 | 24916.2174 | 12.33 | 70.97%
[5 empty] | 12.34 | 1144000 | 660 | 100% | 100% | 15.97% | 0.35732 | 54600 | 243540 | 588390.9428 | 886530.9428 | 1552.2732 | 25063.9725 | 12.34 | 71.01%
[5 empty] | 12.35 | 1144000 | 660 | 100% | 100% | 16.08% | 0.35817 | 54600 | 243540 | 588869.6276 | 887009.6276 | 1561.429 | 25211.8074 | 12.35 | 71.04%
[5 empty] | 12.36 | 1144000 | 660 | 100% | 100% | 16.19% | 0.35902 | 54600 | 243540 | 589348.3124 | 887488.3124 | 1570.5897 | 25359.7222 | 12.36 | 71.08%
[5 empty] | 12.37 | 1144000 | 660 | 100% | 100% | 16.3% | 0.35987 | 54600 | 243540 | 589826.9972 | 887966.9972 | 1579.7554 | 25507.7167 | 12.37 | 71.12%
[5 empty] | 12.38 | 1144000 | 660 | 100% | 100% | 16.42% | 0.36072 | 54600 | 243540 | 590305.682 | 888445.682 | 1588.926 | 25655.7909 | 12.38 | 71.16%
[5 empty] | 12.39 | 1144000 | 660 | 100% | 100% | 16.53% | 0.36157 | 54600 | 243540 | 590784.3668 | 888924.3668 | 1598.1015 | 25803.945 | 12.39 | 71.2%
[5 empty] | 12.4 | 1144000 | 660 | 100% | 100% | 16.64% | 0.36242 | 54600 | 243540 | 591263.0516 | 889403.0516 | 1607.282 | 25952.1789 | 12.4 | 71.24%
[5 empty] | 12.41 | 1144000 | 660 | 100% | 100% | 16.75% | 0.36327 | 54600 | 243540 | 591741.7364 | 889881.7364 | 1616.4674 | 26100.4925 | 12.41 | 71.27%
[5 empty] | 12.42 | 1144000 | 660 | 100% | 100% | 16.86% | 0.36412 | 54600 | 243540 | 592220.4212 | 890360.4212 | 1625.6578 | 26248.8859 | 12.42 | 71.31%
[5 empty] | 12.43 | 1144000 | 660 | 100% | 100% | 16.97% | 0.36497 | 54600 | 243540 | 592699.106 | 890839.106 | 1634.8531 | 26397.3591 | 12.43 | 71.35%
[5 empty] | 12.44 | 1144000 | 660 | 100% | 100% | 17.08% | 0.36582 | 54600 | 243540 | 593177.7908 | 891317.7908 | 1644.0534 | 26545.912 | 12.44 | 71.39%
[5 empty] | 12.45 | 1144000 | 660 | 100% | 100% | 17.19% | 0.36667 | 54600 | 243540 | 593656.4756 | 891796.4756 | 1653.2586 | 26694.5448 | 12.45 | 71.43%
[5 empty] | 12.46 | 1144000 | 660 | 100% | 100% | 17.3% | 0.36752 | 54600 | 243540 | 594135.1604 | 892275.1604 | 1662.4687 | 26843.2573 | 12.46 | 71.47%
[5 empty] | 12.47 | 1144000 | 660 | 100% | 100% | 17.42% | 0.36837 | 54600 | 243540 | 594613.8452 | 892753.8452 | 1671.6838 | 26992.0496 | 12.47 | 71.5%
[5 empty] | 12.48 | 1144000 | 660 | 100% | 100% | 17.53% | 0.36922 | 54600 | 243540 | 595092.53 | 893232.53 | 1680.9038 | 27140.9217 | 12.48 | 71.54%
[5 empty] | 12.49 | 1144000 | 660 | 100% | 100% | 17.64% | 0.37007 | 54600 | 243540 | 595571.2148 | 893711.2148 | 1690.1287 | 27289.8736 | 12.49 | 71.58%
[5 empty] | 12.5 | 1144000 | 660 | 100% | 100% | 17.75% | 0.37092 | 54600 | 243540 | 596049.8996 | 894189.8996 | 1699.3586 | 27438.9052 | 12.5 | 71.62%
[5 empty] | 12.51 | 1144000 | 660 | 100% | 100% | 17.86% | 0.37177 | 54600 | 243540 | 596528.5844 | 894668.5844 | 1708.5935 | 27588.0166 | 12.51 | 71.66%
[5 empty] | 12.52 | 1144000 | 660 | 100% | 100% | 17.97% | 0.37262 | 54600 | 243540 | 597007.2692 | 895147.2692 | 1717.8332 | 27737.2079 | 12.52 | 71.7%
[5 empty] | 12.53 | 1144000 | 660 | 100% | 100% | 18.08% | 0.37347 | 54600 | 243540 | 597485.954 | 895625.954 | 1727.078 | 27886.4788 | 12.53 | 71.73%
[5 empty] | 12.54 | 1144000 | 660 | 100% | 100% | 18.19% | 0.37432 | 54600 | 243540 | 597964.6388 | 896104.6388 | 1736.3276 | 28035.8296 | 12.54 | 71.77%
[5 empty] | 12.55 | 1144000 | 660 | 100% | 100% | 18.3% | 0.37517 | 54600 | 243540 | 598443.3236 | 896583.3236 | 1745.5822 | 28185.2602 | 12.55 | 71.81%
[5 empty] | 12.56 | 1144000 | 660 | 100% | 100% | 18.42% | 0.37602 | 54600 | 243540 | 598922.0084 | 897062.0084 | 1754.8418 | 28334.7705 | 12.56 | 71.85%
[5 empty] | 12.57 | 1144000 | 660 | 100% | 100% | 18.53% | 0.37687 | 54600 | 243540 | 599400.6932 | 897540.6932 | 1764.1062 | 28484.3606 | 12.57 | 71.89%
[5 empty] | 12.58 | 1144000 | 660 | 100% | 100% | 18.64% | 0.37772 | 54600 | 243540 | 599879.378 | 898019.378 | 1773.3757 | 28634.0305 | 12.58 | 71.93%
[5 empty] | 12.59 | 1144000 | 660 | 100% | 100% | 18.75% | 0.37857 | 54600 | 243540 | 600358.0628 | 898498.0628 | 1782.65 | 28783.7802 | 12.59 | 71.96%
[5 empty] | 12.6 | 1144000 | 660 | 100% | 100% | 18.86% | 0.37942 | 54600 | 243540 | 600836.7476 | 898976.7476 | 1791.9293 | 28933.6097 | 12.6 | 72%
[5 empty] | 12.61 | 1144000 | 660 | 100% | 100% | 18.97% | 0.38027 | 54600 | 243540 | 601315.4324 | 899455.4324 | 1801.2136 | 29083.5189 | 12.61 | 72.04%
[5 empty] | 12.62 | 1144000 | 660 | 100% | 100% | 19.08% | 0.38112 | 54600 | 243540 | 601794.1172 | 899934.1172 | 1810.5028 | 29233.5079 | 12.62 | 72.08%
[5 empty] | 12.63 | 1144000 | 660 | 100% | 100% | 19.19% | 0.38197 | 54600 | 243540 | 602272.802 | 900412.802 | 1819.7969 | 29383.5767 | 12.63 | 72.12%
[5 empty] | 12.64 | 1144000 | 660 | 100% | 100% | 19.3% | 0.38282 | 54600 | 243540 | 602751.4868 | 900891.4868 | 1829.096 | 29533.7253 | 12.64 | 72.16%
[5 empty] | 12.65 | 1144000 | 660 | 100% | 100% | 19.42% | 0.38367 | 54600 | 243540 | 603230.1716 | 901370.1716 | 1838.4 | 29683.9537 | 12.65 | 72.19%
[5 empty] | 12.66 | 1144000 | 660 | 100% | 100% | 19.53% | 0.38452 | 54600 | 243540 | 603708.8564 | 901848.8564 | 1847.7089 | 29834.2618 | 12.66 | 72.23%
[5 empty] | 12.67 | 1144000 | 660 | 100% | 100% | 19.64% | 0.38537 | 54600 | 243540 | 604187.5412 | 902327.5412 | 1857.0228 | 29984.6497 | 12.67 | 72.27%
[5 empty] | 12.68 | 1144000 | 660 | 100% | 100% | 19.75% | 0.38622 | 54600 | 243540 | 604666.226 | 902806.226 | 1866.3417 | 30135.1174 | 12.68 | 72.31%
[5 empty] | 12.69 | 1144000 | 660 | 100% | 100% | 19.86% | 0.38707 | 54600 | 243540 | 605144.9108 | 903284.9108 | 1875.6654 | 30285.6649 | 12.69 | 72.35%
[5 empty] | 12.7 | 1144000 | 660 | 100% | 100% | 19.97% | 0.38792 | 54600 | 243540 | 605623.5956 | 903763.5956 | 1884.9941 | 30436.2922 | 12.7 | 72.39%
[5 empty] | 12.71 | 1144000 | 660 | 100% | 100% | 20.08% | 0.38877 | 54600 | 243540 | 606102.2804 | 904242.2804 | 1894.3278 | 30586.9992 | 12.71 | 72.42%
[5 empty] | 12.72 | 1144000 | 660 | 100% | 100% | 20.19% | 0.38962 | 54600 | 243540 | 606580.9652 | 904720.9652 | 1903.6664 | 30737.7861 | 12.72 | 72.46%
[5 empty] | 12.73 | 1144000 | 660 | 100% | 100% | 20.3% | 0.39047 | 54600 | 243540 | 607059.65 | 905199.65 | 1913.0099 | 30888.6527 | 12.73 | 72.5%
[5 empty] | 12.74 | 1144000 | 660 | 100% | 100% | 20.42% | 0.39132 | 54600 | 243540 | 607538.3348 | 905678.3348 | 1922.3584 | 31039.5991 | 12.74 | 72.54%
[5 empty] | 12.75 | 1144000 | 660 | 100% | 100% | 20.53% | 0.39217 | 54600 | 243540 | 608017.0196 | 906157.0196 | 1931.7118 | 31190.6252 | 12.75 | 72.58%
[5 empty] | 12.76 | 1144000 | 660 | 100% | 100% | 20.64% | 0.39302 | 54600 | 243540 | 608495.7044 | 906635.7044 | 1941.0702 | 31341.7312 | 12.76 | 72.62%
[5 empty] | 12.77 | 1144000 | 660 | 100% | 100% | 20.75% | 0.39387 | 54600 | 243540 | 608974.3892 | 907114.3892 | 1950.4335 | 31492.9169 | 12.77 | 72.65%
[5 empty] | 12.78 | 1144000 | 660 | 100% | 100% | 20.86% | 0.39472 | 54600 | 243540 | 609453.074 | 907593.074 | 1959.8017 | 31644.1824 | 12.78 | 72.69%
[5 empty] | 12.79 | 1144000 | 660 | 100% | 100% | 20.97% | 0.39557 | 54600 | 243540 | 609931.7588 | 908071.7588 | 1969.1749 | 31795.5277 | 12.79 | 72.73%
[5 empty] | 12.8 | 1144000 | 660 | 100% | 100% | 21.08% | 0.39642 | 54600 | 243540 | 610410.4436 | 908550.4436 | 1978.5531 | 31946.9528 | 12.8 | 72.77%
[5 empty] | 12.81 | 1144000 | 660 | 100% | 100% | 21.19% | 0.39727 | 54600 | 243540 | 610889.1284 | 909029.1284 | 1987.9361 | 32098.4576 | 12.81 | 72.81%
[5 empty] | 12.82 | 1144000 | 660 | 100% | 100% | 21.3% | 0.39812 | 54600 | 243540 | 611367.8132 | 909507.8132 | 1997.3241 | 32250.0423 | 12.82 | 72.85%
[5 empty] | 12.83 | 1144000 | 660 | 100% | 100% | 21.42% | 0.39897 | 54600 | 243540 | 611846.498 | 909986.498 | 2006.7171 | 32401.7067 | 12.83 | 72.88%
[5 empty] | 12.84 | 1144000 | 660 | 100% | 100% | 21.53% | 0.39981 | 54600 | 243540 | 612325.1828 | 910465.1828 | 2016.115 | 32553.4509 | 12.84 | 72.92%
[5 empty] | 12.85 | 1144000 | 660 | 100% | 100% | 21.64% | 0.40066 | 54600 | 243540 | 612803.8676 | 910943.8676 | 2025.5178 | 32705.2749 | 12.85 | 72.96%
[5 empty] | 12.86 | 1144000 | 660 | 100% | 100% | 21.75% | 0.40151 | 54600 | 243540 | 613282.5524 | 911422.5524 | 2034.9256 | 32857.1786 | 12.86 | 73%
[5 empty] | 12.87 | 1144000 | 660 | 100% | 100% | 21.86% | 0.40236 | 54600 | 243540 | 613761.2372 | 911901.2372 | 2044.3383 | 33009.1622 | 12.87 | 73.04%
[5 empty] | 12.88 | 1144000 | 660 | 100% | 100% | 21.97% | 0.40321 | 54600 | 243540 | 614239.922 | 912379.922 | 2053.7559 | 33161.2255 | 12.88 | 73.08%
[5 empty] | 12.89 | 1144000 | 660 | 100% | 100% | 22.08% | 0.40406 | 54600 | 243540 | 614718.6068 | 912858.6068 | 2063.1785 | 33313.3686 | 12.89 | 73.11%
[5 empty] | 12.9 | 1144000 | 660 | 100% | 100% | 22.19% | 0.40491 | 54600 | 243540 | 615197.2916 | 913337.2916 | 2072.6061 | 33465.5915 | 12.9 | 73.15%
[5 empty] | 12.91 | 1144000 | 660 | 100% | 100% | 22.3% | 0.40576 | 54600 | 243540 | 615675.9764 | 913815.9764 | 2082.0385 | 33617.8941 | 12.91 | 73.19%
[5 empty] | 12.92 | 1144000 | 660 | 100% | 100% | 22.42% | 0.40661 | 54600 | 243540 | 616154.6612 | 914294.6612 | 2091.476 | 33770.2766 | 12.92 | 73.23%
[5 empty] | 12.93 | 1144000 | 660 | 100% | 100% | 22.53% | 0.40746 | 54600 | 243540 | 616633.346 | 914773.346 | 2100.9183 | 33922.7388 | 12.93 | 73.27%
[5 empty] | 12.94 | 1144000 | 660 | 100% | 100% | 22.64% | 0.40831 | 54600 | 243540 | 617112.0308 | 915252.0308 | 2110.3656 | 34075.2808 | 12.94 | 73.31%
[5 empty] | 12.95 | 1144000 | 660 | 100% | 100% | 22.75% | 0.40916 | 54600 | 243540 | 617590.7156 | 915730.7156 | 2119.8179 | 34227.9026 | 12.95 | 73.34%
[5 empty] | 12.96 | 1144000 | 660 | 100% | 100% | 22.86% | 0.41001 | 54600 | 243540 | 618069.4004 | 916209.4004 | 2129.2751 | 34380.6042 | 12.96 | 73.38%
[5 empty] | 12.97 | 1144000 | 660 | 100% | 100% | 22.97% | 0.41086 | 54600 | 243540 | 618548.0852 | 916688.0852 | 2138.7372 | 34533.3855 | 12.97 | 73.42%
[5 empty] | 12.98 | 1144000 | 660 | 100% | 100% | 23.08% | 0.41171 | 54600 | 243540 | 619026.77 | 917166.77 | 2148.2042 | 34686.2466 | 12.98 | 73.46%
[5 empty] | 12.99 | 1144000 | 660 | 100% | 100% | 23.19% | 0.41256 | 54600 | 243540 | 619505.4548 | 917645.4548 | 2157.6762 | 34839.1875 | 12.99 | 73.5%
[5 empty] | 13 | 1144000 | 660 | 100% | 100% | 23.3% | 0.41341 | 54600 | 243540 | 619984.1396 | 918124.1396 | 2167.1532 | 34992.2082 | 13 | 73.54%
[5 empty] | 13.01 | 1144000 | 660 | 100% | 100% | 23.42% | 0.41426 | 54600 | 243540 | 620462.8244 | 918602.8244 | 2176.6351 | 35145.3087 | 13.01 | 73.57%
[5 empty] | 13.02 | 1144000 | 660 | 100% | 100% | 23.53% | 0.41511 | 54600 | 243540 | 620941.5092 | 919081.5092 | 2186.1219 | 35298.489 | 13.02 | 73.61%
[5 empty] | 13.03 | 1144000 | 660 | 100% | 100% | 23.64% | 0.41596 | 54600 | 243540 | 621420.194 | 919560.194 | 2195.6137 | 35451.749 | 13.03 | 73.65%
[5 empty] | 13.04 | 1144000 | 660 | 100% | 100% | 23.75% | 0.41681 | 54600 | 243540 | 621898.8788 | 920038.8788 | 2205.1104 | 35605.0888 | 13.04 | 73.69%
[5 empty] | 13.05 | 1144000 | 660 | 100% | 100% | 23.86% | 0.41766 | 54600 | 243540 | 622377.5636 | 920517.5636 | 2214.612 | 35758.5084 | 13.05 | 73.73%
[5 empty] | 13.06 | 1144000 | 660 | 100% | 100% | 23.97% | 0.41851 | 54600 | 243540 | 622856.2484 | 920996.2484 | 2224.1186 | 35912.0078 | 13.06 | 73.77%
[5 empty] | 13.07 | 1144000 | 660 | 100% | 100% | 24.08% | 0.41936 | 54600 | 243540 | 623334.9332 | 921474.9332 | 2233.6302 | 36065.5869 | 13.07 | 73.8%
[5 empty] | 13.08 | 1144000 | 660 | 100% | 100% | 24.19% | 0.42021 | 54600 | 243540 | 623813.618 | 921953.618 | 2243.1466 | 36219.2459 | 13.08 | 73.84%
[5 empty] | 13.09 | 1144000 | 660 | 100% | 100% | 24.3% | 0.42106 | 54600 | 243540 | 624292.3028 | 922432.3028 | 2252.6681 | 36372.9846 | 13.09 | 73.88%
[5 empty] | 13.1 | 1144000 | 660 | 100% | 100% | 24.42% | 0.42191 | 54600 | 243540 | 624770.9876 | 922910.9876 | 2262.1944 | 36526.8031 | 13.1 | 73.92%
[5 empty] | 13.11 | 1144000 | 660 | 100% | 100% | 24.53% | 0.42276 | 54600 | 243540 | 625249.6724 | 923389.6724 | 2271.7257 | 36680.7014 | 13.11 | 73.96%
[5 empty] | 13.12 | 1144000 | 660 | 100% | 100% | 24.64% | 0.42361 | 54600 | 243540 | 625728.3572 | 923868.3572 | 2281.2619 | 36834.6794 | 13.12 | 74%
[5 empty] | 13.13 | 1144000 | 660 | 100% | 100% | 24.75% | 0.42446 | 54600 | 243540 | 626207.042 | 924347.042 | 2290.8031 | 36988.7373 | 13.13 | 74.03%
[5 empty] | 13.14 | 1144000 | 660 | 100% | 100% | 24.86% | 0.42531 | 54600 | 243540 | 626685.7268 | 924825.7268 | 2300.3492 | 37142.8749 | 13.14 | 74.07%
[5 empty] | 13.15 | 1144000 | 660 | 100% | 100% | 24.97% | 0.42616 | 54600 | 243540 | 627164.4116 | 925304.4116 | 2309.9003 | 37297.0923 | 13.15 | 74.11%
[5 empty] | 13.16 | 1144000 | 660 | 100% | 100% | 25.08% | 0.42701 | 54600 | 243540 | 627643.0964 | 925783.0964 | 2319.4563 | 37451.3895 | 13.16 | 74.15%
[5 empty] | 13.17 | 1144000 | 660 | 100% | 100% | 25.19% | 0.42786 | 54600 | 243540 | 628121.7812 | 926261.7812 | 2329.0173 | 37605.7664 | 13.17 | 74.19%
[5 empty] | 13.18 | 1144000 | 660 | 100% | 100% | 25.3% | 0.42871 | 54600 | 243540 | 628600.466 | 926740.466 | 2338.5831 | 37760.2232 | 13.18 | 74.23%
[5 empty] | 13.19 | 1144000 | 660 | 100% | 100% | 25.42% | 0.42956 | 54600 | 243540 | 629079.1508 | 927219.1508 | 2348.154 | 37914.7597 | 13.19 | 74.26%
[5 empty] | 13.2 | 1144000 | 660 | 100% | 100% | 25.53% | 0.43041 | 54600 | 243540 | 629557.8356 | 927697.8356 | 2357.7297 | 38069.376 | 13.2 | 74.3%
[5 empty] | 13.21 | 1144000 | 660 | 100% | 100% | 25.64% | 0.43126 | 54600 | 243540 | 630036.5204 | 928176.5204 | 2367.3104 | 38224.0721 | 13.21 | 74.34%
[5 empty] | 13.22 | 1144000 | 660 | 100% | 100% | 25.75% | 0.43211 | 54600 | 243540 | 630515.2052 | 928655.2052 | 2376.8961 | 38378.848 | 13.22 | 74.38%
[5 empty] | 13.23 | 1144000 | 660 | 100% | 100% | 25.86% | 0.43296 | 54600 | 243540 | 630993.89 | 929133.89 | 2386.4867 | 38533.7036 | 13.23 | 74.42%
[5 empty] | 13.24 | 1144000 | 660 | 100% | 100% | 25.97% | 0.43381 | 54600 | 243540 | 631472.5748 | 929612.5748 | 2396.0822 | 38688.639 | 13.24 | 74.46%
[5 empty] | 13.25 | 1144000 | 660 | 100% | 100% | 26.08% | 0.43466 | 54600 | 243540 | 631951.2596 | 930091.2596 | 2405.6827 | 38843.6542 | 13.25 | 74.49%
[5 empty] | 13.26 | 1144000 | 660 | 100% | 100% | 26.19% | 0.43551 | 54600 | 243540 | 632429.9444 | 930569.9444 | 2415.2881 | 38998.7492 | 13.26 | 74.53%
[5 empty] | 13.27 | 1144000 | 660 | 100% | 100% | 26.3% | 0.43636 | 54600 | 243540 | 632908.6292 | 931048.6292 | 2424.8984 | 39153.924 | 13.27 | 74.57%
[5 empty] | 13.28 | 1144000 | 660 | 100% | 100% | 26.42% | 0.43721 | 54600 | 243540 | 633387.314 | 931527.314 | 2434.5137 | 39309.1786 | 13.28 | 74.61%
[5 empty] | 13.29 | 1144000 | 660 | 100% | 100% | 26.53% | 0.43806 | 54600 | 243540 | 633865.9988 | 932005.9988 | 2444.134 | 39464.5129 | 13.29 | 74.65%
[5 empty] | 13.3 | 1144000 | 660 | 100% | 100% | 26.64% | 0.43891 | 54600 | 243540 | 634344.6836 | 932484.6836 | 2453.7592 | 39619.927 | 13.3 | 74.69%
[5 empty] | 13.31 | 1144000 | 660 | 100% | 100% | 26.75% | 0.43976 | 54600 | 243540 | 634823.3684 | 932963.3684 | 2463.3893 | 39775.4209 | 13.31 | 74.72%
[5 empty] | 13.32 | 1144000 | 660 | 100% | 100% | 26.86% | 0.44061 | 54600 | 243540 | 635302.0532 | 933442.0532 | 2473.0243 | 39930.9946 | 13.32 | 74.76%
[5 empty] | 13.33 | 1144000 | 660 | 100% | 100% | 26.97% | 0.44146 | 54600 | 243540 | 635780.738 | 933920.738 | 2482.6643 | 40086.648 | 13.33 | 74.8%
[5 empty] | 13.34 | 1144000 | 660 | 100% | 100% | 27.08% | 0.44231 | 54600 | 243540 | 636259.4228 | 934399.4228 | 2492.3093 | 40242.3813 | 13.34 | 74.84%
[5 empty] | 13.35 | 1144000 | 660 | 100% | 100% | 27.19% | 0.44316 | 54600 | 243540 | 636738.1076 | 934878.1076 | 2501.9592 | 40398.1943 | 13.35 | 74.88%
[5 empty] | 13.36 | 1144000 | 660 | 100% | 100% | 27.3% | 0.444 | 54600 | 243540 | 637216.7924 | 935356.7924 | 2511.614 | 40554.0871 | 13.36 | 74.92%
[5 empty] | 13.37 | 1144000 | 660 | 100% | 100% | 27.42% | 0.44485 | 54600 | 243540 | 637695.4772 | 935835.4772 | 2521.2737 | 40710.0597 | 13.37 | 74.95%
[5 empty] | 13.38 | 1144000 | 660 | 100% | 100% | 27.53% | 0.4457 | 54600 | 243540 | 638174.162 | 936314.162 | 2530.9384 | 40866.112 | 13.38 | 74.99%
[5 empty] | 13.39 | 1144000 | 660 | 100% | 100% | 27.64% | 0.44655 | 54600 | 243540 | 638652.8468 | 936792.8468 | 2540.6081 | 41022.2442 | 13.39 | 75.03%
[5 empty] | 13.4 | 1144000 | 660 | 100% | 100% | 27.75% | 0.4474 | 54600 | 243540 | 639131.5316 | 937271.5316 | 2550.2827 | 41178.4561 | 13.4 | 75.07%
[5 empty] | 13.41 | 1144000 | 660 | 100% | 100% | 27.86% | 0.44825 | 54600 | 243540 | 639610.2164 | 937750.2164 | 2559.9622 | 41334.7478 | 13.41 | 75.11%
[5 empty] | 13.42 | 1144000 | 660 | 100% | 100% | 27.97% | 0.4491 | 54600 | 243540 | 640088.9012 | 938228.9012 | 2569.6467 | 41491.1193 | 13.42 | 75.15%
[5 empty] | 13.43 | 1144000 | 660 | 100% | 100% | 28.08% | 0.44995 | 54600 | 243540 | 640567.586 | 938707.586 | 2579.3361 | 41647.5705 | 13.43 | 75.18%
[5 empty] | 13.44 | 1144000 | 660 | 100% | 100% | 28.19% | 0.4508 | 54600 | 243540 | 641046.2708 | 939186.2708 | 2589.0304 | 41804.1016 | 13.44 | 75.22%
[5 empty] | 13.45 | 1144000 | 660 | 100% | 100% | 28.3% | 0.45165 | 54600 | 243540 | 641524.9556 | 939664.9556 | 2598.7297 | 41960.7124 | 13.45 | 75.26%
[5 empty] | 13.46 | 1144000 | 660 | 100% | 100% | 28.42% | 0.4525 | 54600 | 243540 | 642003.6404 | 940143.6404 | 2608.434 | 42117.403 | 13.46 | 75.3%
[5 empty] | 13.47 | 1144000 | 660 | 100% | 100% | 28.53% | 0.45335 | 54600 | 243540 | 642482.3252 | 940622.3252 | 2618.1431 | 42274.1734 | 13.47 | 75.34%
[5 empty] | 13.48 | 1144000 | 660 | 100% | 100% | 28.64% | 0.4542 | 54600 | 243540 | 642961.01 | 941101.01 | 2627.8572 | 42431.0236 | 13.48 | 75.38%
[5 empty] | 13.49 | 1144000 | 660 | 100% | 100% | 28.75% | 0.45505 | 54600 | 243540 | 643439.6948 | 941579.6948 | 2637.5763 | 42587.9535 | 13.49 | 75.41%
[5 empty] | 13.5 | 1144000 | 660 | 100% | 100% | 28.86% | 0.4559 | 54600 | 243540 | 643918.3796 | 942058.3796 | 2647.3003 | 42744.9632 | 13.5 | 75.45%
[5 empty] | 13.51 | 1144000 | 660 | 100% | 100% | 28.97% | 0.45675 | 54600 | 243540 | 644397.0644 | 942537.0644 | 2657.0292 | 42902.0528 | 13.51 | 75.49%
[5 empty] | 13.52 | 1144000 | 660 | 100% | 100% | 29.08% | 0.4576 | 54600 | 243540 | 644875.7492 | 943015.7492 | 2666.7631 | 43059.2221 | 13.52 | 75.53%
[5 empty] | 13.53 | 1144000 | 660 | 100% | 100% | 29.19% | 0.45845 | 54600 | 243540 | 645354.434 | 943494.434 | 2676.5019 | 43216.4711 | 13.53 | 75.57%
[5 empty] | 13.54 | 1144000 | 660 | 100% | 100% | 29.3% | 0.4593 | 54600 | 243540 | 645833.1188 | 943973.1188 | 2686.2457 | 43373.8 | 13.54 | 75.61%
[5 empty] | 13.55 | 1144000 | 660 | 100% | 100% | 29.42% | 0.46015 | 54600 | 243540 | 646311.8036 | 944451.8036 | 2695.9944 | 43531.2086 | 13.55 | 75.64%
[5 empty] | 13.56 | 1144000 | 660 | 100% | 100% | 29.53% | 0.461 | 54600 | 243540 | 646790.4884 | 944930.4884 | 2705.748 | 43688.697 | 13.56 | 75.68%
[5 empty] | 13.57 | 1144000 | 660 | 100% | 100% | 29.64% | 0.46185 | 54600 | 243540 | 647269.1732 | 945409.1732 | 2715.5066 | 43846.2652 | 13.57 | 75.72%
[5 empty] | 13.58 | 1144000 | 660 | 100% | 100% | 29.75% | 0.4627 | 54600 | 243540 | 647747.858 | 945887.858 | 2725.2702 | 44003.9132 | 13.58 | 75.76%
[5 empty] | 13.59 | 1144000 | 660 | 100% | 100% | 29.86% | 0.46355 | 54600 | 243540 | 648226.5428 | 946366.5428 | 2735.0386 | 44161.641 | 13.59 | 75.8%
[5 empty] | 13.6 | 1144000 | 660 | 100% | 100% | 29.97% | 0.4644 | 54600 | 243540 | 648705.2276 | 946845.2276 | 2744.812 | 44319.4485 | 13.6 | 75.84%
[5 empty] | 13.61 | 1144000 | 660 | 100% | 100% | 30.08% | 0.46525 | 54600 | 243540 | 649183.9124 | 947323.9124 | 2754.5904 | 44477.3358 | 13.61 | 75.87%
[5 empty] | 13.62 | 1144000 | 660 | 100% | 100% | 30.19% | 0.4661 | 54600 | 243540 | 649662.5972 | 947802.5972 | 2764.3737 | 44635.3029 | 13.62 | 75.91%
[5 empty] | 13.63 | 1144000 | 660 | 100% | 100% | 30.3% | 0.46695 | 54600 | 243540 | 650141.282 | 948281.282 | 2774.1619 | 44793.3498 | 13.63 | 75.95%
[5 empty] | 13.64 | 1144000 | 660 | 100% | 100% | 30.42% | 0.4678 | 54600 | 243540 | 650619.9668 | 948759.9668 | 2783.9551 | 44951.4765 | 13.64 | 75.99%
[5 empty] | 13.65 | 1144000 | 660 | 100% | 100% | 30.53% | 0.46865 | 54600 | 243540 | 651098.6516 | 949238.6516 | 2793.7532 | 45109.6829 | 13.65 | 76.03%
[5 empty] | 13.66 | 1144000 | 660 | 100% | 100% | 30.64% | 0.4695 | 54600 | 243540 | 651577.3364 | 949717.3364 | 2803.5562 | 45267.9691 | 13.66 | 76.07%
[5 empty] | 13.67 | 1144000 | 660 | 100% | 100% | 30.75% | 0.47035 | 54600 | 243540 | 652056.0212 | 950196.0212 | 2813.3642 | 45426.3351 | 13.67 | 76.1%
[5 empty] | 13.68 | 1144000 | 660 | 100% | 100% | 30.86% | 0.4712 | 54600 | 243540 | 652534.706 | 950674.706 | 2823.1772 | 45584.7809 | 13.68 | 76.14%
[5 empty] | 13.69 | 1144000 | 660 | 100% | 100% | 30.97% | 0.47205 | 54600 | 243540 | 653013.3908 | 951153.3908 | 2832.995 | 45743.3065 | 13.69 | 76.18%
[5 empty] | 13.7 | 1144000 | 660 | 100% | 100% | 31.08% | 0.4729 | 54600 | 243540 | 653492.0756 | 951632.0756 | 2842.8179 | 45901.9118 | 13.7 | 76.22%
[5 empty] | 13.71 | 1144000 | 660 | 100% | 100% | 31.19% | 0.47375 | 54600 | 243540 | 653970.7604 | 952110.7604 | 2852.6456 | 46060.5969 | 13.71 | 76.26%
[5 empty] | 13.72 | 1144000 | 660 | 100% | 100% | 31.3% | 0.4746 | 54600 | 243540 | 654449.4452 | 952589.4452 | 2862.4783 | 46219.3618 | 13.72 | 76.3%
[5 empty] | 13.73 | 1144000 | 660 | 100% | 100% | 31.42% | 0.47545 | 54600 | 243540 | 654928.13 | 953068.13 | 2872.316 | 46378.2065 | 13.73 | 76.33%
[5 empty] | 13.74 | 1144000 | 660 | 100% | 100% | 31.53% | 0.4763 | 54600 | 243540 | 655406.8148 | 953546.8148 | 2882.1585 | 46537.131 | 13.74 | 76.37%
[5 empty] | 13.75 | 1144000 | 660 | 100% | 100% | 31.64% | 0.47715 | 54600 | 243540 | 655885.4996 | 954025.4996 | 2892.0061 | 46696.1353 | 13.75 | 76.41%
[5 empty] | 13.76 | 1144000 | 660 | 100% | 100% | 31.75% | 0.478 | 54600 | 243540 | 656364.1844 | 954504.1844 | 2901.8585 | 46855.2193 | 13.76 | 76.45%
[5 empty] | 13.77 | 1144000 | 660 | 100% | 100% | 31.86% | 0.47885 | 54600 | 243540 | 656842.8692 | 954982.8692 | 2911.7159 | 47014.3831 | 13.77 | 76.49%
[5 empty] | 13.78 | 1144000 | 660 | 100% | 100% | 31.97% | 0.4797 | 54600 | 243540 | 657321.554 | 955461.554 | 2921.5783 | 47173.6267 | 13.78 | 76.53%
[5 empty] | 13.79 | 1144000 | 660 | 100% | 100% | 32.08% | 0.48055 | 54600 | 243540 | 657800.2388 | 955940.2388 | 2931.4456 | 47332.9501 | 13.79 | 76.56%
[5 empty] | 13.8 | 1144000 | 660 | 100% | 100% | 32.19% | 0.4814 | 54600 | 243540 | 658278.9236 | 956418.9236 | 2941.3178 | 47492.3532 | 13.8 | 76.6%
[5 empty] | 13.81 | 1144000 | 660 | 100% | 100% | 32.3% | 0.48225 | 54600 | 243540 | 658757.6084 | 956897.6084 | 2951.195 | 47651.8362 | 13.81 | 76.64%
[5 empty] | 13.82 | 1144000 | 660 | 100% | 100% | 32.42% | 0.4831 | 54600 | 243540 | 659236.2932 | 957376.2932 | 2961.0771 | 47811.3989 | 13.82 | 76.68%
[5 empty] | 13.83 | 1144000 | 660 | 100% | 100% | 32.53% | 0.48395 | 54600 | 243540 | 659714.978 | 957854.978 | 2970.9641 | 47971.0414 | 13.83 | 76.72%
[5 empty] | 13.84 | 1144000 | 660 | 100% | 100% | 32.64% | 0.4848 | 54600 | 243540 | 660193.6628 | 958333.6628 | 2980.8561 | 48130.7636 | 13.84 | 76.76%
[5 empty] | 13.85 | 1144000 | 660 | 100% | 100% | 32.75% | 0.48565 | 54600 | 243540 | 660672.3476 | 958812.3476 | 2990.753 | 48290.5657 | 13.85 | 76.79%
[5 empty] | 13.86 | 1144000 | 660 | 100% | 100% | 32.86% | 0.4865 | 54600 | 243540 | 661151.0324 | 959291.0324 | 3000.6549 | 48450.4475 | 13.86 | 76.83%
[5 empty] | 13.87 | 1144000 | 660 | 100% | 100% | 32.97% | 0.48735 | 54600 | 243540 | 661629.7172 | 959769.7172 | 3010.5617 | 48610.4092 | 13.87 | 76.87%
[5 empty] | 13.88 | 1144000 | 660 | 100% | 100% | 33.08% | 0.4882 | 54600 | 243540 | 662108.402 | 960248.402 | 3020.4735 | 48770.4506 | 13.88 | 76.91%
[5 empty] | 13.89 | 1144000 | 660 | 100% | 100% | 33.19% | 0.48904 | 54600 | 243540 | 662587.0868 | 960727.0868 | 3030.3902 | 48930.5717 | 13.89 | 76.95%
[5 empty] | 13.9 | 1144000 | 660 | 100% | 100% | 33.3% | 0.48989 | 54600 | 243540 | 663065.7716 | 961205.7716 | 3040.3118 | 49090.7727 | 13.9 | 76.99%
[5 empty] | 13.91 | 1144000 | 660 | 100% | 100% | 33.42% | 0.49074 | 54600 | 243540 | 663544.4564 | 961684.4564 | 3050.2384 | 49251.0534 | 13.91 | 77.02%
[5 empty] | 13.92 | 1144000 | 660 | 100% | 100% | 33.53% | 0.49159 | 54600 | 243540 | 664023.1412 | 962163.1412 | 3060.1699 | 49411.414 | 13.92 | 77.06%
[5 empty] | 13.93 | 1144000 | 660 | 100% | 100% | 33.64% | 0.49244 | 54600 | 243540 | 664501.826 | 962641.826 | 3070.1064 | 49571.8543 | 13.93 | 77.1%
[5 empty] | 13.94 | 1144000 | 660 | 100% | 100% | 33.75% | 0.49329 | 54600 | 243540 | 664980.5108 | 963120.5108 | 3080.0478 | 49732.3744 | 13.94 | 77.14%
[5 empty] | 13.95 | 1144000 | 660 | 100% | 100% | 33.86% | 0.49414 | 54600 | 243540 | 665459.1956 | 963599.1956 | 3089.9941 | 49892.9742 | 13.95 | 77.18%
[5 empty] | 13.96 | 1144000 | 660 | 100% | 100% | 33.97% | 0.49499 | 54600 | 243540 | 665937.8804 | 964077.8804 | 3099.9454 | 50053.6539 | 13.96 | 77.22%
[5 empty] | 13.97 | 1144000 | 660 | 100% | 100% | 34.08% | 0.49584 | 54600 | 243540 | 666416.5652 | 964556.5652 | 3109.9016 | 50214.4133 | 13.97 | 77.25%
[5 empty] | 13.98 | 1144000 | 660 | 100% | 100% | 34.19% | 0.49669 | 54600 | 243540 | 666895.25 | 965035.25 | 3119.8628 | 50375.2525 | 13.98 | 77.29%
[5 empty] | 13.99 | 1144000 | 660 | 100% | 100% | 34.3% | 0.49754 | 54600 | 243540 | 667373.9348 | 965513.9348 | 3129.8289 | 50536.1715 | 13.99 | 77.33%
[5 empty] | 14 | 1144000 | 660 | 100% | 100% | 34.42% | 0.49839 | 54600 | 243540 | 667852.6196 | 965992.6196 | 3139.8 | 50697.1703 | 14 | 77.37%
[5 empty] | 14.01 | 1144000 | 660 | 100% | 100% | 34.53% | 0.49924 | 54600 | 243540 | 668331.3044 | 966471.3044 | 3149.776 | 50858.2488 | 14.01 | 77.41%
[5 empty] | 14.02 | 1144000 | 660 | 100% | 100% | 34.64% | 0.50009 | 54600 | 243540 | 668809.9892 | 966949.9892 | 3159.7569 | 51019.4071 | 14.02 | 77.45%
[5 empty] | 14.03 | 1144000 | 660 | 100% | 100% | 34.75% | 0.50094 | 54600 | 243540 | 669288.674 | 967428.674 | 3169.7428 | 51180.6453 | 14.03 | 77.48%
[5 empty] | 14.04 | 1144000 | 660 | 100% | 100% | 34.86% | 0.50179 | 54600 | 243540 | 669767.3588 | 967907.3588 | 3179.7336 | 51341.9632 | 14.04 | 77.52%
[5 empty] | 14.05 | 1144000 | 660 | 100% | 100% | 34.97% | 0.50264 | 54600 | 243540 | 670246.0436 | 968386.0436 | 3189.7293 | 51503.3608 | 14.05 | 77.56%
[5 empty] | 14.06 | 1144000 | 660 | 100% | 100% | 35.08% | 0.50349 | 54600 | 243540 | 670724.7284 | 968864.7284 | 3199.73 | 51664.8383 | 14.06 | 77.6%
[5 empty] | 14.07 | 1144000 | 660 | 100% | 100% | 35.19% | 0.50434 | 54600 | 243540 | 671203.4132 | 969343.4132 | 3209.7357 | 51826.3955 | 14.07 | 77.64%
[5 empty] | 14.08 | 1144000 | 660 | 100% | 100% | 35.3% | 0.50519 | 54600 | 243540 | 671682.098 | 969822.098 | 3219.7462 | 51988.0325 | 14.08 | 77.68%
[5 empty] | 14.09 | 1144000 | 660 | 100% | 100% | 35.42% | 0.50604 | 54600 | 243540 | 672160.7828 | 970300.7828 | 3229.7617 | 52149.7493 | 14.09 | 77.71%
[5 empty] | 14.1 | 1144000 | 660 | 100% | 100% | 35.53% | 0.50689 | 54600 | 243540 | 672639.4676 | 970779.4676 | 3239.7822 | 52311.5459 | 14.1 | 77.75%
[5 empty] | 14.11 | 1144000 | 660 | 100% | 100% | 35.64% | 0.50774 | 54600 | 243540 | 673118.1524 | 971258.1524 | 3249.8076 | 52473.4223 | 14.11 | 77.79%
[5 empty] | 14.12 | 1144000 | 660 | 100% | 100% | 35.75% | 0.50859 | 54600 | 243540 | 673596.8372 | 971736.8372 | 3259.8379 | 52635.3784 | 14.12 | 77.83%
[5 empty] | 14.13 | 1144000 | 660 | 100% | 100% | 35.86% | 0.50944 | 54600 | 243540 | 674075.522 | 972215.522 | 3269.8732 | 52797.4143 | 14.13 | 77.87%
[5 empty] | 14.14 | 1144000 | 660 | 100% | 100% | 35.97% | 0.51029 | 54600 | 243540 | 674554.2068 | 972694.2068 | 3279.9134 | 52959.53 | 14.14 | 77.91%
[5 empty] | 14.15 | 1144000 | 660 | 100% | 100% | 36.08% | 0.51114 | 54600 | 243540 | 675032.8916 | 973172.8916 | 3289.9586 | 53121.7255 | 14.15 | 77.94%
[5 empty] | 14.16 | 1144000 | 660 | 100% | 100% | 36.19% | 0.51199 | 54600 | 243540 | 675511.5764 | 973651.5764 | 3300.0087 | 53284.0008 | 14.16 | 77.98%
[5 empty] | 14.17 | 1144000 | 660 | 100% | 100% | 36.3% | 0.51284 | 54600 | 243540 | 675990.2612 | 974130.2612 | 3310.0638 | 53446.3558 | 14.17 | 78.02%
[5 empty] | 14.18 | 1144000 | 660 | 100% | 100% | 36.42% | 0.51369 | 54600 | 243540 | 676468.946 | 974608.946 | 3320.1238 | 53608.7906 | 14.18 | 78.06%
[5 empty] | 14.19 | 1144000 | 660 | 100% | 100% | 36.53% | 0.51454 | 54600 | 243540 | 676947.6308 | 975087.6308 | 3330.1887 | 53771.3052 | 14.19 | 78.1%
[5 empty] | 14.2 | 1144000 | 660 | 100% | 100% | 36.64% | 0.51539 | 54600 | 243540 | 677426.3156 | 975566.3156 | 3340.2585 | 53933.8996 | 14.2 | 78.14%
[5 empty] | 14.21 | 1144000 | 660 | 100% | 100% | 36.75% | 0.51624 | 54600 | 243540 | 677905.0004 | 976045.0004 | 3350.3334 | 54096.5738 | 14.21 | 78.17%
[5 empty] | 14.22 | 1144000 | 660 | 100% | 100% | 36.86% | 0.51709 | 54600 | 243540 | 678383.6852 | 976523.6852 | 3360.4131 | 54259.3277 | 14.22 | 78.21%
[5 empty] | 14.23 | 1144000 | 660 | 100% | 100% | 36.97% | 0.51794 | 54600 | 243540 | 678862.37 | 977002.37 | 3370.4978 | 54422.1615 | 14.23 | 78.25%
[5 empty] | 14.24 | 1144000 | 660 | 100% | 100% | 37.08% | 0.51879 | 54600 | 243540 | 679341.0548 | 977481.0548 | 3380.5874 | 54585.075 | 14.24 | 78.29%
[5 empty] | 14.25 | 1144000 | 660 | 100% | 100% | 37.19% | 0.51964 | 54600 | 243540 | 679819.7396 | 977959.7396 | 3390.682 | 54748.0683 | 14.25 | 78.33%
[5 empty] | 14.26 | 1144000 | 660 | 100% | 100% | 37.3% | 0.52049 | 54600 | 243540 | 680298.4244 | 978438.4244 | 3400.7815 | 54911.1413 | 14.26 | 78.37%
[5 empty] | 14.27 | 1144000 | 660 | 100% | 100% | 37.42% | 0.52134 | 54600 | 243540 | 680777.1092 | 978917.1092 | 3410.886 | 55074.2942 | 14.27 | 78.4%
[5 empty] | 14.28 | 1144000 | 660 | 100% | 100% | 37.53% | 0.52219 | 54600 | 243540 | 681255.794 | 979395.794 | 3420.9954 | 55237.5268 | 14.28 | 78.44%
[5 empty] | 14.29 | 1144000 | 660 | 100% | 100% | 37.64% | 0.52304 | 54600 | 243540 | 681734.4788 | 979874.4788 | 3431.1097 | 55400.8392 | 14.29 | 78.48%
[5 empty] | 14.3 | 1144000 | 660 | 100% | 100% | 37.75% | 0.52389 | 54600 | 243540 | 682213.1636 | 980353.1636 | 3441.229 | 55564.2314 | 14.3 | 78.52%
[5 empty] | 14.31 | 1144000 | 660 | 100% | 100% | 37.86% | 0.52474 | 54600 | 243540 | 682691.8484 | 980831.8484 | 3451.3532 | 55727.7034 | 14.31 | 78.56%
[5 empty] | 14.32 | 1144000 | 660 | 100% | 100% | 37.97% | 0.52559 | 54600 | 243540 | 683170.5332 | 981310.5332 | 3461.4824 | 55891.2552 | 14.32 | 78.6%
[5 empty] | 14.33 | 1144000 | 660 | 100% | 100% | 38.08% | 0.52644 | 54600 | 243540 | 683649.218 | 981789.218 | 3471.6165 | 56054.8867 | 14.33 | 78.63%
[5 empty] | 14.34 | 1144000 | 660 | 100% | 100% | 38.19% | 0.52729 | 54600 | 243540 | 684127.9028 | 982267.9028 | 3481.7555 | 56218.598 | 14.34 | 78.67%
[5 empty] | 14.35 | 1144000 | 660 | 100% | 100% | 38.3% | 0.52814 | 54600 | 243540 | 684606.5876 | 982746.5876 | 3491.8995 | 56382.3891 | 14.35 | 78.71%
[5 empty] | 14.36 | 1144000 | 660 | 100% | 100% | 38.42% | 0.52899 | 54600 | 243540 | 685085.2724 | 983225.2724 | 3502.0484 | 56546.26 | 14.36 | 78.75%
[5 empty] | 14.37 | 1144000 | 660 | 100% | 100% | 38.53% | 0.52984 | 54600 | 243540 | 685563.9572 | 983703.9572 | 3512.2023 | 56710.2107 | 14.37 | 78.79%
[5 empty] | 14.38 | 1144000 | 660 | 100% | 100% | 38.64% | 0.53069 | 54600 | 243540 | 686042.642 | 984182.642 | 3522.3611 | 56874.2411 | 14.38 | 78.83%
[5 empty] | 14.39 | 1144000 | 660 | 100% | 100% | 38.75% | 0.53154 | 54600 | 243540 | 686521.3268 | 984661.3268 | 3532.5248 | 57038.3513 | 14.39 | 78.87%
[5 empty] | 14.4 | 1144000 | 660 | 100% | 100% | 38.86% | 0.53239 | 54600 | 243540 | 687000.0116 | 985140.0116 | 3542.6935 | 57202.5413 | 14.4 | 78.9%
[5 empty] | 14.41 | 1144000 | 660 | 100% | 100% | 38.97% | 0.53324 | 54600 | 243540 | 687478.6964 | 985618.6964 | 3552.8672 | 57366.8111 | 14.41 | 78.94%
[5 empty] | 14.42 | 1144000 | 660 | 100% | 100% | 39.08% | 0.53408 | 54600 | 243540 | 687957.3812 | 986097.3812 | 3563.0457 | 57531.1607 | 14.42 | 78.98%
[5 empty] | 14.43 | 1144000 | 660 | 100% | 100% | 39.19% | 0.53493 | 54600 | 243540 | 688436.066 | 986576.066 | 3573.2292 | 57695.59 | 14.43 | 79.02%
[5 empty] | 14.44 | 1144000 | 660 | 100% | 100% | 39.3% | 0.53578 | 54600 | 243540 | 688914.7508 | 987054.7508 | 3583.4177 | 57860.0991 | 14.44 | 79.06%
[5 empty] | 14.45 | 1144000 | 660 | 100% | 100% | 39.42% | 0.53663 | 54600 | 243540 | 689393.4356 | 987533.4356 | 3593.6111 | 58024.688 | 14.45 | 79.1%
[5 empty] | 14.46 | 1144000 | 660 | 100% | 100% | 39.53% | 0.53748 | 54600 | 243540 | 689872.1204 | 988012.1204 | 3603.8094 | 58189.3567 | 14.46 | 79.13%
[5 empty] | 14.47 | 1144000 | 660 | 100% | 100% | 39.64% | 0.53833 | 54600 | 243540 | 690350.8052 | 988490.8052 | 3614.0127 | 58354.1052 | 14.47 | 79.17%
[5 empty] | 14.48 | 1144000 | 660 | 100% | 100% | 39.75% | 0.53918 | 54600 | 243540 | 690829.49 | 988969.49 | 3624.2209 | 58518.9334 | 14.48 | 79.21%
[5 empty] | 14.49 | 1144000 | 660 | 100% | 100% | 39.86% | 0.54003 | 54600 | 243540 | 691308.1748 | 989448.1748 | 3634.4341 | 58683.8415 | 14.49 | 79.25%
[5 empty] | 14.5 | 1144000 | 660 | 100% | 100% | 39.97% | 0.54088 | 54600 | 243540 | 691786.8596 | 989926.8596 | 3644.6522 | 58848.8293 | 14.5 | 79.29%
[5 empty] | 14.51 | 1144000 | 660 | 100% | 100% | 40.08% | 0.54173 | 54600 | 243540 | 692265.5444 | 990405.5444 | 3654.8752 | 59013.8969 | 14.51 | 79.33%
[5 empty] | 14.52 | 1144000 | 660 | 100% | 100% | 40.19% | 0.54258 | 54600 | 243540 | 692744.2292 | 990884.2292 | 3665.1032 | 59179.0442 | 14.52 | 79.36%
[5 empty] | 14.53 | 1144000 | 660 | 100% | 100% | 40.3% | 0.54343 | 54600 | 243540 | 693222.914 | 991362.914 | 3675.3361 | 59344.2714 | 14.53 | 79.4%
[5 empty] | 14.54 | 1144000 | 660 | 100% | 100% | 40.42% | 0.54428 | 54600 | 243540 | 693701.5988 | 991841.5988 | 3685.574 | 59509.5783 | 14.54 | 79.44%
[5 empty] | 14.55 | 1144000 | 660 | 100% | 100% | 40.53% | 0.54513 | 54600 | 243540 | 694180.2836 | 992320.2836 | 3695.8168 | 59674.965 | 14.55 | 79.48%
[5 empty] | 14.56 | 1144000 | 660 | 100% | 100% | 40.64% | 0.54598 | 54600 | 243540 | 694658.9684 | 992798.9684 | 3706.0645 | 59840.4315 | 14.56 | 79.52%
[5 empty] | 14.57 | 1144000 | 660 | 100% | 100% | 40.75% | 0.54683 | 54600 | 243540 | 695137.6532 | 993277.6532 | 3716.3172 | 60005.9778 | 14.57 | 79.56%
[5 empty] | 14.58 | 1144000 | 660 | 100% | 100% | 40.86% | 0.54768 | 54600 | 243540 | 695616.338 | 993756.338 | 3726.5749 | 60171.6039 | 14.58 | 79.59%
[5 empty] | 14.59 | 1144000 | 660 | 100% | 100% | 40.97% | 0.54853 | 54600 | 243540 | 696095.0228 | 994235.0228 | 3736.8374 | 60337.3097 | 14.59 | 79.63%
[5 empty] | 14.6 | 1144000 | 660 | 100% | 100% | 41.08% | 0.54938 | 54600 | 243540 | 696573.7076 | 994713.7076 | 3747.1049 | 60503.0953 | 14.6 | 79.67%
[5 empty] | 14.61 | 1144000 | 660 | 100% | 100% | 41.19% | 0.55023 | 54600 | 243540 | 697052.3924 | 995192.3924 | 3757.3774 | 60668.9607 | 14.61 | 79.71%
[5 empty] | 14.62 | 1144000 | 660 | 100% | 100% | 41.3% | 0.55108 | 54600 | 243540 | 697531.0772 | 995671.0772 | 3767.6548 | 60834.9059 | 14.62 | 79.75%
[5 empty] | 14.63 | 1144000 | 660 | 100% | 100% | 41.42% | 0.55193 | 54600 | 243540 | 698009.762 | 996149.762 | 3777.9371 | 61000.9309 | 14.63 | 79.79%
[5 empty] | 14.64 | 1144000 | 660 | 100% | 100% | 41.53% | 0.55278 | 54600 | 243540 | 698488.4468 | 996628.4468 | 3788.2244 | 61167.0356 | 14.64 | 79.82%
[5 empty] | 14.65 | 1144000 | 660 | 100% | 100% | 41.64% | 0.55363 | 54600 | 243540 | 698967.1316 | 997107.1316 | 3798.5166 | 61333.2201 | 14.65 | 79.86%
[5 empty] | 14.66 | 1144000 | 660 | 100% | 100% | 41.75% | 0.55448 | 54600 | 243540 | 699445.8164 | 997585.8164 | 3808.8137 | 61499.4844 | 14.66 | 79.9%
[5 empty] | 14.67 | 1144000 | 660 | 100% | 100% | 41.86% | 0.55533 | 54600 | 243540 | 699924.5012 | 998064.5012 | 3819.1158 | 61665.8285 | 14.67 | 79.94%
[5 empty] | 14.68 | 1144000 | 660 | 100% | 100% | 41.97% | 0.55618 | 54600 | 243540 | 700403.186 | 998543.186 | 3829.4229 | 61832.2524 | 14.68 | 79.98%
[5 empty] | 14.69 | 1144000 | 660 | 100% | 100% | 42.08% | 0.55703 | 54600 | 243540 | 700881.8708 | 999021.8708 | 3839.7349 | 61998.756 | 14.69 | 80.02%
[5 empty] | 14.7 | 1144000 | 660 | 100% | 100% | 42.19% | 0.55788 | 54600 | 243540 | 701360.5556 | 999500.5556 | 3850.0518 | 62165.3394 | 14.7 | 80.05%
[5 empty] | 14.71 | 1144000 | 660 | 100% | 100% | 42.3% | 0.55873 | 54600 | 243540 | 701839.2404 | 999979.2404 | 3860.3736 | 62332.0027 | 14.71 | 80.09%
[5 empty] | 14.72 | 1144000 | 660 | 100% | 100% | 42.42% | 0.55958 | 54600 | 243540 | 702317.9252 | 1000457.9252 | 3870.7004 | 62498.7456 | 14.72 | 80.13%
[5 empty] | 14.73 | 1144000 | 660 | 100% | 100% | 42.53% | 0.56043 | 54600 | 243540 | 702796.61 | 1000936.61 | 3881.0322 | 62665.5684 | 14.73 | 80.17%
[5 empty] | 14.74 | 1144000 | 660 | 100% | 100% | 42.64% | 0.56128 | 54600 | 243540 | 703275.2948 | 1001415.2948 | 3891.3689 | 62832.471 | 14.74 | 80.21%
[5 empty] | 14.75 | 1144000 | 660 | 100% | 100% | 42.75% | 0.56213 | 54600 | 243540 | 703753.9796 | 1001893.9796 | 3901.7105 | 62999.4533 | 14.75 | 80.25%
[5 empty] | 14.76 | 1144000 | 660 | 100% | 100% | 42.86% | 0.56298 | 54600 | 243540 | 704232.6644 | 1002372.6644 | 3912.0571 | 63166.5154 | 14.76 | 80.28%
[5 empty] | 14.77 | 1144000 | 660 | 100% | 100% | 42.97% | 0.56383 | 54600 | 243540 | 704711.3492 | 1002851.3492 | 3922.4086 | 63333.6573 | 14.77 | 80.32%
[5 empty] | 14.78 | 1144000 | 660 | 100% | 100% | 43.08% | 0.56468 | 54600 | 243540 | 705190.034 | 1003330.034 | 3932.765 | 63500.879 | 14.78 | 80.36%
[5 empty] | 14.79 | 1144000 | 660 | 100% | 100% | 43.19% | 0.56553 | 54600 | 243540 | 705668.7188 | 1003808.7188 | 3943.1264 | 63668.1804 | 14.79 | 80.4%
[5 empty] | 14.8 | 1144000 | 660 | 100% | 100% | 43.3% | 0.56638 | 54600 | 243540 | 706147.4036 | 1004287.4036 | 3953.4927 | 63835.5617 | 14.8 | 80.44%
[5 empty] | 14.81 | 1144000 | 660 | 100% | 100% | 43.42% | 0.56723 | 54600 | 243540 | 706626.0884 | 1004766.0884 | 3963.864 | 64003.0227 | 14.81 | 80.48%
[5 empty] | 14.82 | 1144000 | 660 | 100% | 100% | 43.53% | 0.56808 | 54600 | 243540 | 707104.7732 | 1005244.7732 | 3974.2402 | 64170.5635 | 14.82 | 80.51%
[5 empty] | 14.83 | 1144000 | 660 | 100% | 100% | 43.64% | 0.56893 | 54600 | 243540 | 707583.458 | 1005723.458 | 3984.6214 | 64338.184 | 14.83 | 80.55%
[5 empty] | 14.84 | 1144000 | 660 | 100% | 100% | 43.75% | 0.56978 | 54600 | 243540 | 708062.1428 | 1006202.1428 | 3995.0075 | 64505.8844 | 14.84 | 80.59%
[5 empty] | 14.85 | 1144000 | 660 | 100% | 100% | 43.86% | 0.57063 | 54600 | 243540 | 708540.8276 | 1006680.8276 | 4005.3985 | 64673.6645 | 14.85 | 80.63%
[5 empty] | 14.86 | 1144000 | 660 | 100% | 100% | 43.97% | 0.57148 | 54600 | 243540 | 709019.5124 | 1007159.5124 | 4015.7945 | 64841.5245 | 14.86 | 80.67%
[5 empty] | 14.87 | 1144000 | 660 | 100% | 100% | 44.08% | 0.57233 | 54600 | 243540 | 709498.1972 | 1007638.1972 | 4026.1954 | 65009.4642 | 14.87 | 80.71%
[5 empty] | 14.88 | 1144000 | 660 | 100% | 100% | 44.19% | 0.57318 | 54600 | 243540 | 709976.882 | 1008116.882 | 4036.6013 | 65177.4836 | 14.88 | 80.74%
[5 empty] | 14.89 | 1144000 | 660 | 100% | 100% | 44.3% | 0.57403 | 54600 | 243540 | 710455.5668 | 1008595.5668 | 4047.0121 | 65345.5829 | 14.89 | 80.78%
[5 empty] | 14.9 | 1144000 | 660 | 100% | 100% | 44.42% | 0.57488 | 54600 | 243540 | 710934.2516 | 1009074.2516 | 4057.4278 | 65513.7619 | 14.9 | 80.82%
[5 empty] | 14.91 | 1144000 | 660 | 100% | 100% | 44.53% | 0.57573 | 54600 | 243540 | 711412.9364 | 1009552.9364 | 4067.8485 | 65682.0208 | 14.91 | 80.86%
[5 empty] | 14.92 | 1144000 | 660 | 100% | 100% | 44.64% | 0.57658 | 54600 | 243540 | 711891.6212 | 1010031.6212 | 4078.2741 | 65850.3594 | 14.92 | 80.9%
[5 empty] | 14.93 | 1144000 | 660 | 100% | 100% | 44.75% | 0.57743 | 54600 | 243540 | 712370.306 | 1010510.306 | 4088.7047 | 66018.7777 | 14.93 | 80.94%
[5 empty] | 14.94 | 1144000 | 660 | 100% | 100% | 44.86% | 0.57828 | 54600 | 243540 | 712848.9908 | 1010988.9908 | 4099.1402 | 66187.2759 | 14.94 | 80.97%
[5 empty] | 14.95 | 1144000 | 660 | 100% | 100% | 44.97% | 0.57912 | 54600 | 243540 | 713327.6756 | 1011467.6756 | 4109.5806 | 66355.8539 | 14.95 | 81.01%
[5 empty] | 14.96 | 1144000 | 660 | 100% | 100% | 45.08% | 0.57997 | 54600 | 243540 | 713806.3604 | 1011946.3604 | 4120.026 | 66524.5116 | 14.96 | 81.05%
[5 empty] | 14.97 | 1144000 | 660 | 100% | 100% | 45.19% | 0.58082 | 54600 | 243540 | 714285.0452 | 1012425.0452 | 4130.4763 | 66693.2491 | 14.97 | 81.09%
[5 empty] | 14.98 | 1144000 | 660 | 100% | 100% | 45.3% | 0.58167 | 54600 | 243540 | 714763.73 | 1012903.73 | 4140.9316 | 66862.0664 | 14.98 | 81.13%
[5 empty] | 14.99 | 1144000 | 660 | 100% | 100% | 45.42% | 0.58252 | 54600 | 243540 | 715242.4148 | 1013382.4148 | 4151.3918 | 67030.9634 | 14.99 | 81.17%
[5 empty] | 15 | 1144000 | 660 | 100% | 100% | 45.53% | 0.58337 | 54600 | 243540 | 715721.0996 | 1013861.0996 | 4161.8569 | 67199.9403 | 15 | 81.2%
[5 empty] | 15.01 | 1144000 | 660 | 100% | 100% | 45.64% | 0.58422 | 54600 | 243540 | 716199.7844 | 1014339.7844 | 4172.327 | 67368.9969 | 15.01 | 81.24%
[5 empty] | 15.02 | 1144000 | 660 | 100% | 100% | 45.75% | 0.58507 | 54600 | 243540 | 716678.4692 | 1014818.4692 | 4182.8021 | 67538.1333 | 15.02 | 81.28%
[5 empty] | 15.03 | 1144000 | 660 | 100% | 100% | 45.86% | 0.58592 | 54600 | 243540 | 717157.154 | 1015297.154 | 4193.282 | 67707.3495 | 15.03 | 81.32%
[5 empty] | 15.04 | 1144000 | 660 | 100% | 100% | 45.97% | 0.58677 | 54600 | 243540 | 717635.8388 | 1015775.8388 | 4203.767 | 67876.6455 | 15.04 | 81.36%
[5 empty] | 15.05 | 1144000 | 660 | 100% | 100% | 46.08% | 0.58762 | 54600 | 243540 | 718114.5236 | 1016254.5236 | 4214.2568 | 68046.0213 | 15.05 | 81.4%
[5 empty] | 15.06 | 1144000 | 660 | 100% | 100% | 46.19% | 0.58847 | 54600 | 243540 | 718593.2084 | 1016733.2084 | 4224.7516 | 68215.4768 | 15.06 | 81.43%
[5 empty] | 15.07 | 1144000 | 660 | 100% | 100% | 46.3% | 0.58932 | 54600 | 243540 | 719071.8932 | 1017211.8932 | 4235.2513 | 68385.0121 | 15.07 | 81.47%
[5 empty] | 15.08 | 1144000 | 660 | 100% | 100% | 46.42% | 0.59017 | 54600 | 243540 | 719550.578 | 1017690.578 | 4245.756 | 68554.6272 | 15.08 | 81.51%
[5 empty] | 15.09 | 1144000 | 660 | 100% | 100% | 46.53% | 0.59102 | 54600 | 243540 | 720029.2628 | 1018169.2628 | 4256.2656 | 68724.3221 | 15.09 | 81.55%
[5 empty] | 15.1 | 1144000 | 660 | 100% | 100% | 46.64% | 0.59187 | 54600 | 243540 | 720507.9476 | 1018647.9476 | 4266.7802 | 68894.0967 | 15.1 | 81.59%
[5 empty] | 15.11 | 1144000 | 660 | 100% | 100% | 46.75% | 0.59272 | 54600 | 243540 | 720986.6324 | 1019126.6324 | 4277.2997 | 69063.9512 | 15.11 | 81.63%
[5 empty] | 15.12 | 1144000 | 660 | 100% | 100% | 46.86% | 0.59357 | 54600 | 243540 | 721465.3172 | 1019605.3172 | 4287.8242 | 69233.8854 | 15.12 | 81.66%
[5 empty] | 15.13 | 1144000 | 660 | 100% | 100% | 46.97% | 0.59442 | 54600 | 243540 | 721944.002 | 1020084.002 | 4298.3535 | 69403.8994 | 15.13 | 81.7%
[5 empty] | 15.14 | 1144000 | 660 | 100% | 100% | 47.08% | 0.59527 | 54600 | 243540 | 722422.6868 | 1020562.6868 | 4308.8879 | 69573.9932 | 15.14 | 81.74%
[5 empty] | 15.15 | 1144000 | 660 | 100% | 100% | 47.19% | 0.59612 | 54600 | 243540 | 722901.3716 | 1021041.3716 | 4319.4271 | 69744.1667 | 15.15 | 81.78%
[5 empty] | 15.16 | 1144000 | 660 | 100% | 100% | 47.3% | 0.59697 | 54600 | 243540 | 723380.0564 | 1021520.0564 | 4329.9713 | 69914.4201 | 15.16 | 81.82%
[5 empty] | 15.17 | 1144000 | 660 | 100% | 100% | 47.42% | 0.59782 | 54600 | 243540 | 723858.7412 | 1021998.7412 | 4340.5205 | 70084.7532 | 15.17 | 81.86%
[5 empty] | 15.18 | 1144000 | 660 | 100% | 100% | 47.53% | 0.59867 | 54600 | 243540 | 724337.426 | 1022477.426 | 4351.0746 | 70255.1661 | 15.18 | 81.89%
[5 empty] | 15.19 | 1144000 | 660 | 100% | 100% | 47.64% | 0.59952 | 54600 | 243540 | 724816.1108 | 1022956.1108 | 4361.6336 | 70425.6588 | 15.19 | 81.93%
[5 empty] | 15.2 | 1144000 | 660 | 100% | 100% | 47.75% | 0.60037 | 54600 | 243540 | 725294.7956 | 1023434.7956 | 4372.1976 | 70596.2313 | 15.2 | 81.97%
[5 empty] | 15.21 | 1144000 | 660 | 100% | 100% | 47.86% | 0.60122 | 54600 | 243540 | 725773.4804 | 1023913.4804 | 4382.7665 | 70766.8835 | 15.21 | 82.01%
[5 empty] | 15.22 | 1144000 | 660 | 100% | 100% | 47.97% | 0.60207 | 54600 | 243540 | 726252.1652 | 1024392.1652 | 4393.3403 | 70937.6155 | 15.22 | 82.05%
[5 empty] | 15.23 | 1144000 | 660 | 100% | 100% | 48.08% | 0.60292 | 54600 | 243540 | 726730.85 | 1024870.85 | 4403.9191 | 71108.4273 | 15.23 | 82.09%
[5 empty] | 15.24 | 1144000 | 660 | 100% | 100% | 48.19% | 0.60377 | 54600 | 243540 | 727209.5348 | 1025349.5348 | 4414.5029 | 71279.3189 | 15.24 | 82.12%
[5 empty] | 15.25 | 1144000 | 660 | 100% | 100% | 48.3% | 0.60462 | 54600 | 243540 | 727688.2196 | 1025828.2196 | 4425.0915 | 71450.2903 | 15.25 | 82.16%
[5 empty] | 15.26 | 1144000 | 660 | 100% | 100% | 48.42% | 0.60547 | 54600 | 243540 | 728166.9044 | 1026306.9044 | 4435.6852 | 71621.3415 | 15.26 | 82.2%
[5 empty] | 15.27 | 1144000 | 660 | 100% | 100% | 48.53% | 0.60632 | 54600 | 243540 | 728645.5892 | 1026785.5892 | 4446.2837 | 71792.4724 | 15.27 | 82.24%
[5 empty] | 15.28 | 1144000 | 660 | 100% | 100% | 48.64% | 0.60717 | 54600 | 243540 | 729124.274 | 1027264.274 | 4456.8872 | 71963.6831 | 15.28 | 82.28%
[5 empty] | 15.29 | 1144000 | 660 | 100% | 100% | 48.75% | 0.60802 | 54600 | 243540 | 729602.9588 | 1027742.9588 | 4467.4957 | 72134.9736 | 15.29 | 82.32%
[5 empty] | 15.3 | 1144000 | 660 | 100% | 100% | 48.86% | 0.60887 | 54600 | 243540 | 730081.6436 | 1028221.6436 | 4478.109 | 72306.3439 | 15.3 | 82.35%
[5 empty] | 15.31 | 1144000 | 660 | 100% | 100% | 48.97% | 0.60972 | 54600 | 243540 | 730560.3284 | 1028700.3284 | 4488.7274 | 72477.7939 | 15.31 | 82.39%
[5 empty] | 15.32 | 1144000 | 660 | 100% | 100% | 49.08% | 0.61057 | 54600 | 243540 | 731039.0132 | 1029179.0132 | 4499.3506 | 72649.3238 | 15.32 | 82.43%
[5 empty] | 15.33 | 1144000 | 660 | 100% | 100% | 49.19% | 0.61142 | 54600 | 243540 | 731517.698 | 1029657.698 | 4509.9788 | 72820.9334 | 15.33 | 82.47%
[5 empty] | 15.34 | 1144000 | 660 | 100% | 100% | 49.3% | 0.61227 | 54600 | 243540 | 731996.3828 | 1030136.3828 | 4520.612 | 72992.6228 | 15.34 | 82.51%
[5 empty] | 15.35 | 1144000 | 660 | 100% | 100% | 49.42% | 0.61312 | 54600 | 243540 | 732475.0676 | 1030615.0676 | 4531.2501 | 73164.392 | 15.35 | 82.55%
[5 empty] | 15.36 | 1144000 | 660 | 100% | 100% | 49.53% | 0.61397 | 54600 | 243540 | 732953.7524 | 1031093.7524 | 4541.8931 | 73336.2409 | 15.36 | 82.58%
[5 empty] | 15.37 | 1144000 | 660 | 100% | 100% | 49.64% | 0.61482 | 54600 | 243540 | 733432.4372 | 1031572.4372 | 4552.541 | 73508.1696 | 15.37 | 82.62%
[5 empty] | 15.38 | 1144000 | 660 | 100% | 100% | 49.75% | 0.61567 | 54600 | 243540 | 733911.122 | 1032051.122 | 4563.194 | 73680.1782 | 15.38 | 82.66%
[5 empty] | 15.39 | 1144000 | 660 | 100% | 100% | 49.86% | 0.61652 | 54600 | 243540 | 734389.8068 | 1032529.8068 | 4573.8518 | 73852.2665 | 15.39 | 82.7%
[5 empty] | 15.4 | 1144000 | 660 | 100% | 100% | 49.97% | 0.61737 | 54600 | 243540 | 734868.4916 | 1033008.4916 | 4584.5146 | 74024.4346 | 15.4 | 82.74%
[5 empty] | 15.41 | 1144000 | 660 | 100% | 100% | 50.08% | 0.61822 | 54600 | 243540 | 735347.1764 | 1033487.1764 | 4595.1823 | 74196.6824 | 15.41 | 82.78%
[5 empty] | 15.42 | 1144000 | 660 | 100% | 100% | 50.19% | 0.61907 | 54600 | 243540 | 735825.8612 | 1033965.8612 | 4605.855 | 74369.0101 | 15.42 | 82.81%
[5 empty] | 15.43 | 1144000 | 660 | 100% | 100% | 50.3% | 0.61992 | 54600 | 243540 | 736304.546 | 1034444.546 | 4616.5326 | 74541.4175 | 15.43 | 82.85%
[5 empty] | 15.44 | 1144000 | 660 | 100% | 100% | 50.42% | 0.62077 | 54600 | 243540 | 736783.2308 | 1034923.2308 | 4627.2152 | 74713.9047 | 15.44 | 82.89%
[5 empty] | 15.45 | 1144000 | 660 | 100% | 100% | 50.53% | 0.62162 | 54600 | 243540 | 737261.9156 | 1035401.9156 | 4637.9027 | 74886.4717 | 15.45 | 82.93%
[5 empty] | 15.46 | 1144000 | 660 | 100% | 100% | 50.64% | 0.62247 | 54600 | 243540 | 737740.6004 | 1035880.6004 | 4648.5951 | 75059.1184 | 15.46 | 82.97%
[5 empty] | 15.47 | 1144000 | 660 | 100% | 100% | 50.75% | 0.62331 | 54600 | 243540 | 738219.2852 | 1036359.2852 | 4659.2925 | 75231.845 | 15.47 | 83.01%
[5 empty] | 15.48 | 1144000 | 660 | 100% | 100% | 50.86% | 0.62416 | 54600 | 243540 | 738697.97 | 1036837.97 | 4669.9948 | 75404.6513 | 15.48 | 83.04%
[5 empty] | 15.49 | 1144000 | 660 | 100% | 100% | 50.97% | 0.62501 | 54600 | 243540 | 739176.6548 | 1037316.6548 | 4680.7021 | 75577.5374 | 15.49 | 83.08%
[5 empty] | 15.5 | 1144000 | 660 | 100% | 100% | 51.08% | 0.62586 | 54600 | 243540 | 739655.3396 | 1037795.3396 | 4691.4143 | 75750.5033 | 15.5 | 83.12%
[5 empty] | 15.51 | 1144000 | 660 | 100% | 100% | 51.19% | 0.62671 | 54600 | 243540 | 740134.0244 | 1038274.0244 | 4702.1314 | 75923.549 | 15.51 | 83.16%
[5 empty] | 15.52 | 1144000 | 660 | 100% | 100% | 51.3% | 0.62756 | 54600 | 243540 | 740612.7092 | 1038752.7092 | 4712.8535 | 76096.6744 | 15.52 | 83.2%
[5 empty] | 15.53 | 1144000 | 660 | 100% | 100% | 51.42% | 0.62841 | 54600 | 243540 | 741091.394 | 1039231.394 | 4723.5805 | 76269.8797 | 15.53 | 83.24%
[5 empty] | 15.54 | 1144000 | 660 | 100% | 100% | 51.53% | 0.62926 | 54600 | 243540 | 741570.0788 | 1039710.0788 | 4734.3125 | 76443.1647 | 15.54 | 83.27%
[5 empty] | 15.55 | 1144000 | 660 | 100% | 100% | 51.64% | 0.63011 | 54600 | 243540 | 742048.7636 | 1040188.7636 | 4745.0494 | 76616.5295 | 15.55 | 83.31%
[5 empty] | 15.56 | 1144000 | 660 | 100% | 100% | 51.75% | 0.63096 | 54600 | 243540 | 742527.4484 | 1040667.4484 | 4755.7912 | 76789.9741 | 15.56 | 83.35%
[5 empty] | 15.57 | 1144000 | 660 | 100% | 100% | 51.86% | 0.63181 | 54600 | 243540 | 743006.1332 | 1041146.1332 | 4766.538 | 76963.4984 | 15.57 | 83.39%
[5 empty] | 15.58 | 1144000 | 660 | 100% | 100% | 51.97% | 0.63266 | 54600 | 243540 | 743484.818 | 1041624.818 | 4777.2898 | 77137.1025 | 15.58 | 83.43%
[5 empty] | 15.59 | 1144000 | 660 | 100% | 100% | 52.08% | 0.63351 | 54600 | 243540 | 743963.5028 | 1042103.5028 | 4788.0464 | 77310.7865 | 15.59 | 83.47%
[5 empty] | 15.6 | 1144000 | 660 | 100% | 100% | 52.19% | 0.63436 | 54600 | 243540 | 744442.1876 | 1042582.1876 | 4798.808 | 77484.5502 | 15.6 | 83.5%
[5 empty] | 15.61 | 1144000 | 660 | 100% | 100% | 52.3% | 0.63521 | 54600 | 243540 | 744920.8724 | 1043060.8724 | 4809.5746 | 77658.3936 | 15.61 | 83.54%
[5 empty] | 15.62 | 1144000 | 660 | 100% | 100% | 52.42% | 0.63606 | 54600 | 243540 | 745399.5572 | 1043539.5572 | 4820.3461 | 77832.3169 | 15.62 | 83.58%
[5 empty] | 15.63 | 1144000 | 660 | 100% | 100% | 52.53% | 0.63691 | 54600 | 243540 | 745878.242 | 1044018.242 | 4831.1225 | 78006.3199 | 15.63 | 83.62%
[5 empty] | 15.64 | 1144000 | 660 | 100% | 100% | 52.64% | 0.63776 | 54600 | 243540 | 746356.9268 | 1044496.9268 | 4841.9039 | 78180.4028 | 15.64 | 83.66%
[5 empty] | 15.65 | 1144000 | 660 | 100% | 100% | 52.75% | 0.63861 | 54600 | 243540 | 746835.6116 | 1044975.6116 | 4852.6902 | 78354.5654 | 15.65 | 83.7%
[5 empty] | 15.66 | 1144000 | 660 | 100% | 100% | 52.86% | 0.63946 | 54600 | 243540 | 747314.2964 | 1045454.2964 | 4863.4815 | 78528.8077 | 15.66 | 83.73%
[5 empty] | 15.67 | 1144000 | 660 | 100% | 100% | 52.97% | 0.64031 | 54600 | 243540 | 747792.9812 | 1045932.9812 | 4874.2777 | 78703.1299 | 15.67 | 83.77%
[5 empty] | 15.68 | 1144000 | 660 | 100% | 100% | 53.08% | 0.64116 | 54600 | 243540 | 748271.666 | 1046411.666 | 4885.0788 | 78877.5319 | 15.68 | 83.81%
[5 empty] | 15.69 | 1144000 | 660 | 100% | 100% | 53.19% | 0.64201 | 54600 | 243540 | 748750.3508 | 1046890.3508 | 4895.8849 | 79052.0136 | 15.69 | 83.85%
[5 empty] | 15.7 | 1144000 | 660 | 100% | 100% | 53.3% | 0.64286 | 54600 | 243540 | 749229.0356 | 1047369.0356 | 4906.6959 | 79226.5751 | 15.7 | 83.89%
[5 empty] | 15.71 | 1144000 | 660 | 100% | 100% | 53.42% | 0.64371 | 54600 | 243540 | 749707.7204 | 1047847.7204 | 4917.5119 | 79401.2164 | 15.71 | 83.93%
[5 empty] | 15.72 | 1144000 | 660 | 100% | 100% | 53.53% | 0.64456 | 54600 | 243540 | 750186.4052 | 1048326.4052 | 4928.3328 | 79575.9374 | 15.72 | 83.96%
[5 empty] | 15.73 | 1144000 | 660 | 100% | 100% | 53.64% | 0.64541 | 54600 | 243540 | 750665.09 | 1048805.09 | 4939.1586 | 79750.7383 | 15.73 | 84%
[5 empty] | 15.74 | 1144000 | 660 | 100% | 100% | 53.75% | 0.64626 | 54600 | 243540 | 751143.7748 | 1049283.7748 | 4949.9894 | 79925.6189 | 15.74 | 84.04%
[5 empty] | 15.75 | 1144000 | 660 | 100% | 100% | 53.86% | 0.64711 | 54600 | 243540 | 751622.4596 | 1049762.4596 | 4960.8251 | 80100.5793 | 15.75 | 84.08%
[5 empty] | 15.76 | 1144000 | 660 | 100% | 100% | 53.97% | 0.64796 | 54600 | 243540 | 752101.1444 | 1050241.1444 | 4971.6658 | 80275.6195 | 15.76 | 84.12%
[5 empty] | 15.77 | 1144000 | 660 | 100% | 100% | 54.08% | 0.64881 | 54600 | 243540 | 752579.8292 | 1050719.8292 | 4982.5114 | 80450.7395 | 15.77 | 84.16%
[5 empty] | 15.78 | 1144000 | 660 | 100% | 100% | 54.19% | 0.64966 | 54600 | 243540 | 753058.514 | 1051198.514 | 4993.362 | 80625.9392 | 15.78 | 84.19%
[5 empty] | 15.79 | 1144000 | 660 | 100% | 100% | 54.3% | 0.65051 | 54600 | 243540 | 753537.1988 | 1051677.1988 | 5004.2174 | 80801.2188 | 15.79 | 84.23%
[5 empty] | 15.8 | 1144000 | 660 | 100% | 100% | 54.42% | 0.65136 | 54600 | 243540 | 754015.8836 | 1052155.8836 | 5015.0779 | 80976.5781 | 15.8 | 84.27%
[5 empty] | 15.81 | 1144000 | 660 | 100% | 100% | 54.53% | 0.65221 | 54600 | 243540 | 754494.5684 | 1052634.5684 | 5025.9433 | 81152.0172 | 15.81 | 84.31%
[5 empty] | 15.82 | 1144000 | 660 | 100% | 100% | 54.64% | 0.65306 | 54600 | 243540 | 754973.2532 | 1053113.2532 | 5036.8136 | 81327.5361 | 15.82 | 84.35%
[5 empty] | 15.83 | 1144000 | 660 | 100% | 100% | 54.75% | 0.65391 | 54600 | 243540 | 755451.938 | 1053591.938 | 5047.6888 | 81503.1347 | 15.83 | 84.39%
[5 empty] | 15.84 | 1144000 | 660 | 100% | 100% | 54.86% | 0.65476 | 54600 | 243540 | 755930.6228 | 1054070.6228 | 5058.569 | 81678.8131 | 15.84 | 84.42%
[5 empty] | 15.85 | 1144000 | 660 | 100% | 100% | 54.97% | 0.65561 | 54600 | 243540 | 756409.3076 | 1054549.3076 | 5069.4542 | 81854.5714 | 15.85 | 84.46%
[5 empty] | 15.86 | 1144000 | 660 | 100% | 100% | 55.08% | 0.65646 | 54600 | 243540 | 756887.9924 | 1055027.9924 | 5080.3442 | 82030.4094 | 15.86 | 84.5%
[5 empty] | 15.87 | 1144000 | 660 | 100% | 100% | 55.19% | 0.65731 | 54600 | 243540 | 757366.6772 | 1055506.6772 | 5091.2393 | 82206.3271 | 15.87 | 84.54%
[5 empty] | 15.88 | 1144000 | 660 | 100% | 100% | 55.3% | 0.65816 | 54600 | 243540 | 757845.362 | 1055985.362 | 5102.1392 | 82382.3247 | 15.88 | 84.58%
[5 empty] | 15.89 | 1144000 | 660 | 100% | 100% | 55.42% | 0.65901 | 54600 | 243540 | 758324.0468 | 1056464.0468 | 5113.0441 | 82558.402 | 15.89 | 84.62%
[5 empty] | 15.9 | 1144000 | 660 | 100% | 100% | 55.53% | 0.65986 | 54600 | 243540 | 758802.7316 | 1056942.7316 | 5123.954 | 82734.5592 | 15.9 | 84.65%
[5 empty] | 15.91 | 1144000 | 660 | 100% | 100% | 55.64% | 0.66071 | 54600 | 243540 | 759281.4164 | 1057421.4164 | 5134.8687 | 82910.7961 | 15.91 | 84.69%
[5 empty] | 15.92 | 1144000 | 660 | 100% | 100% | 55.75% | 0.66156 | 54600 | 243540 | 759760.1012 | 1057900.1012 | 5145.7885 | 83087.1128 | 15.92 | 84.73%
[5 empty] | 15.93 | 1144000 | 660 | 100% | 100% | 55.86% | 0.66241 | 54600 | 243540 | 760238.786 | 1058378.786 | 5156.7131 | 83263.5092 | 15.93 | 84.77%
[5 empty] | 15.94 | 1144000 | 660 | 100% | 100% | 55.97% | 0.66326 | 54600 | 243540 | 760717.4708 | 1058857.4708 | 5167.6427 | 83439.9855 | 15.94 | 84.81%
[5 empty] | 15.95 | 1144000 | 660 | 100% | 100% | 56.08% | 0.66411 | 54600 | 243540 | 761196.1556 | 1059336.1556 | 5178.5773 | 83616.5415 | 15.95 | 84.85%
[5 empty] | 15.96 | 1144000 | 660 | 100% | 100% | 56.19% | 0.66496 | 54600 | 243540 | 761674.8404 | 1059814.8404 | 5189.5168 | 83793.1773 | 15.96 | 84.88%
[5 empty] | 15.97 | 1144000 | 660 | 100% | 100% | 56.3% | 0.66581 | 54600 | 243540 | 762153.5252 | 1060293.5252 | 5200.4612 | 83969.8929 | 15.97 | 84.92%
[5 empty] | 15.98 | 1144000 | 660 | 100% | 100% | 56.42% | 0.66666 | 54600 | 243540 | 762632.21 | 1060772.21 | 5211.4106 | 84146.6883 | 15.98 | 84.96%
[5 empty] | 15.99 | 1144000 | 660 | 100% | 100% | 56.53% | 0.66751 | 54600 | 243540 | 763110.8948 | 1061250.8948 | 5222.3649 | 84323.5634 | 15.99 | 85%
[5 empty] | 16 | 1144000 | 660 | 100% | 100% | 56.64% | 0.66835 | 54600 | 243540 | 763589.5796 | 1061729.5796 | 5233.3241 | 84500.5183 | 16 | 85.04%
[5 empty] | 16.01 | 1144000 | 660 | 100% | 100% | 56.75% | 0.6692 | 54600 | 243540 | 764068.2644 | 1062208.2644 | 5244.2883 | 84677.553 | 16.01 | 85.08%
[5 empty] | 16.02 | 1144000 | 660 | 100% | 100% | 56.86% | 0.67005 | 54600 | 243540 | 764546.9492 | 1062686.9492 | 5255.2575 | 84854.6675 | 16.02 | 85.11%
[5 empty] | 16.03 | 1144000 | 660 | 100% | 100% | 56.97% | 0.6709 | 54600 | 243540 | 765025.634 | 1063165.634 | 5266.2315 | 85031.8618 | 16.03 | 85.15%
[5 empty] | 16.04 | 1144000 | 660 | 100% | 100% | 57.08% | 0.67175 | 54600 | 243540 | 765504.3188 | 1063644.3188 | 5277.2106 | 85209.1359 | 16.04 | 85.19%
[5 empty] | 16.05 | 1144000 | 660 | 100% | 100% | 57.19% | 0.6726 | 54600 | 243540 | 765983.0036 | 1064123.0036 | 5288.1945 | 85386.4897 | 16.05 | 85.23%
[5 empty] | 16.06 | 1144000 | 660 | 100% | 100% | 57.3% | 0.67345 | 54600 | 243540 | 766461.6884 | 1064601.6884 | 5299.1834 | 85563.9233 | 16.06 | 85.27%
[5 empty] | 16.07 | 1144000 | 660 | 100% | 100% | 57.42% | 0.6743 | 54600 | 243540 | 766940.3732 | 1065080.3732 | 5310.1772 | 85741.4367 | 16.07 | 85.31%
[5 empty] | 16.08 | 1144000 | 660 | 100% | 100% | 57.53% | 0.67515 | 54600 | 243540 | 767419.058 | 1065559.058 | 5321.176 | 85919.0299 | 16.08 | 85.34%
[5 empty] | 16.09 | 1144000 | 660 | 100% | 100% | 57.64% | 0.676 | 54600 | 243540 | 767897.7428 | 1066037.7428 | 5332.1798 | 86096.7028 | 16.09 | 85.38%
[5 empty] | 16.1 | 1144000 | 660 | 100% | 100% | 57.75% | 0.67685 | 54600 | 243540 | 768376.4276 | 1066516.4276 | 5343.1884 | 86274.4556 | 16.1 | 85.42%
[5 empty] | 16.11 | 1144000 | 660 | 100% | 100% | 57.86% | 0.6777 | 54600 | 243540 | 768855.1124 | 1066995.1124 | 5354.202 | 86452.2881 | 16.11 | 85.46%
[5 empty] | 16.12 | 1144000 | 660 | 100% | 100% | 57.97% | 0.67855 | 54600 | 243540 | 769333.7972 | 1067473.7972 | 5365.2206 | 86630.2004 | 16.12 | 85.5%
[5 empty] | 16.13 | 1144000 | 660 | 100% | 100% | 58.08% | 0.6794 | 54600 | 243540 | 769812.482 | 1067952.482 | 5376.244 | 86808.1925 | 16.13 | 85.54%
[5 empty] | 16.14 | 1144000 | 660 | 100% | 100% | 58.19% | 0.68025 | 54600 | 243540 | 770291.1668 | 1068431.1668 | 5387.2725 | 86986.2643 | 16.14 | 85.57%
[5 empty] | 16.15 | 1144000 | 660 | 100% | 100% | 58.3% | 0.6811 | 54600 | 243540 | 770769.8516 | 1068909.8516 | 5398.3058 | 87164.416 | 16.15 | 85.61%
[5 empty] | 16.16 | 1144000 | 660 | 100% | 100% | 58.42% | 0.68195 | 54600 | 243540 | 771248.5364 | 1069388.5364 | 5409.3441 | 87342.6474 | 16.16 | 85.65%
[5 empty] | 16.17 | 1144000 | 660 | 100% | 100% | 58.53% | 0.6828 | 54600 | 243540 | 771727.2212 | 1069867.2212 | 5420.3874 | 87520.9586 | 16.17 | 85.69%
[5 empty] | 16.18 | 1144000 | 660 | 100% | 100% | 58.64% | 0.68365 | 54600 | 243540 | 772205.906 | 1070345.906 | 5431.4356 | 87699.3496 | 16.18 | 85.73%
[5 empty] | 16.19 | 1144000 | 660 | 100% | 100% | 58.75% | 0.6845 | 54600 | 243540 | 772684.5908 | 1070824.5908 | 5442.4887 | 87877.8204 | 16.19 | 85.77%
[5 empty] | 16.2 | 1144000 | 660 | 100% | 100% | 58.86% | 0.68535 | 54600 | 243540 | 773163.2756 | 1071303.2756 | 5453.5468 | 88056.3709 | 16.2 | 85.8%
[5 empty] | 16.21 | 1144000 | 660 | 100% | 100% | 58.97% | 0.6862 | 54600 | 243540 | 773641.9604 | 1071781.9604 | 5464.6098 | 88235.0012 | 16.21 | 85.84%
[5 empty] | 16.22 | 1144000 | 660 | 100% | 100% | 59.08% | 0.68705 | 54600 | 243540 | 774120.6452 | 1072260.6452 | 5475.6778 | 88413.7113 | 16.22 | 85.88%
[5 empty] | 16.23 | 1144000 | 660 | 100% | 100% | 59.19% | 0.6879 | 54600 | 243540 | 774599.33 | 1072739.33 | 5486.7507 | 88592.5012 | 16.23 | 85.92%
[5 empty] | 16.24 | 1144000 | 660 | 100% | 100% | 59.3% | 0.68875 | 54600 | 243540 | 775078.0148 | 1073218.0148 | 5497.8285 | 88771.3709 | 16.24 | 85.96%
[5 empty] | 16.25 | 1144000 | 660 | 100% | 100% | 59.42% | 0.6896 | 54600 | 243540 | 775556.6996 | 1073696.6996 | 5508.9113 | 88950.3203 | 16.25 | 86%
[5 empty] | 16.26 | 1144000 | 660 | 100% | 100% | 59.53% | 0.69045 | 54600 | 243540 | 776035.3844 | 1074175.3844 | 5519.999 | 89129.3496 | 16.26 | 86.03%
[5 empty] | 16.27 | 1144000 | 660 | 100% | 100% | 59.64% | 0.6913 | 54600 | 243540 | 776514.0692 | 1074654.0692 | 5531.0917 | 89308.4586 | 16.27 | 86.07%
[5 empty] | 16.28 | 1144000 | 660 | 100% | 100% | 59.75% | 0.69215 | 54600 | 243540 | 776992.754 | 1075132.754 | 5542.1893 | 89487.6474 | 16.28 | 86.11%
[5 empty] | 16.29 | 1144000 | 660 | 100% | 100% | 59.86% | 0.693 | 54600 | 243540 | 777471.4388 | 1075611.4388 | 5553.2918 | 89666.9159 | 16.29 | 86.15%
[5 empty] | 16.3 | 1144000 | 660 | 100% | 100% | 59.97% | 0.69385 | 54600 | 243540 | 777950.1236 | 1076090.1236 | 5564.3993 | 89846.2643 | 16.3 | 86.19%
[5 empty] | 16.31 | 1144000 | 660 | 100% | 100% | 60.08% | 0.6947 | 54600 | 243540 | 778428.8084 | 1076568.8084 | 5575.5117 | 90025.6924 | 16.31 | 86.23%
[5 empty] | 16.32 | 1144000 | 660 | 100% | 100% | 60.19% | 0.69555 | 54600 | 243540 | 778907.4932 | 1077047.4932 | 5586.6291 | 90205.2004 | 16.32 | 86.26%
[5 empty] | 16.33 | 1144000 | 660 | 100% | 100% | 60.3% | 0.6964 | 54600 | 243540 | 779386.178 | 1077526.178 | 5597.7514 | 90384.788 | 16.33 | 86.3%
[5 empty] | 16.34 | 1144000 | 660 | 100% | 100% | 60.42% | 0.69725 | 54600 | 243540 | 779864.8628 | 1078004.8628 | 5608.8786 | 90564.4555 | 16.34 | 86.34%
[5 empty] | 16.35 | 1144000 | 660 | 100% | 100% | 60.53% | 0.6981 | 54600 | 243540 | 780343.5476 | 1078483.5476 | 5620.0108 | 90744.2028 | 16.35 | 86.38%
[5 empty] | 16.36 | 1144000 | 660 | 100% | 100% | 60.64% | 0.69895 | 54600 | 243540 | 780822.2324 | 1078962.2324 | 5631.1479 | 90924.0298 | 16.36 | 86.42%
[5 empty] | 16.37 | 1144000 | 660 | 100% | 100% | 60.75% | 0.6998 | 54600 | 243540 | 781300.9172 | 1079440.9172 | 5642.29 | 91103.9366 | 16.37 | 86.46%
[5 empty] | 16.38 | 1144000 | 660 | 100% | 100% | 60.86% | 0.70065 | 54600 | 243540 | 781779.602 | 1079919.602 | 5653.437 | 91283.9232 | 16.38 | 86.49%
[5 empty] | 16.39 | 1144000 | 660 | 100% | 100% | 60.97% | 0.7015 | 54600 | 243540 | 782258.2868 | 1080398.2868 | 5664.589 | 91463.9896 | 16.39 | 86.53%
[5 empty] | 16.4 | 1144000 | 660 | 100% | 100% | 61.08% | 0.70235 | 54600 | 243540 | 782736.9716 | 1080876.9716 | 5675.7459 | 91644.1358 | 16.4 | 86.57%
[5 empty] | 16.41 | 1144000 | 660 | 100% | 100% | 61.19% | 0.7032 | 54600 | 243540 | 783215.6564 | 1081355.6564 | 5686.9077 | 91824.3617 | 16.41 | 86.61%
[5 empty] | 16.42 | 1144000 | 660 | 100% | 100% | 61.3% | 0.70405 | 54600 | 243540 | 783694.3412 | 1081834.3412 | 5698.0745 | 92004.6675 | 16.42 | 86.65%
[5 empty] | 16.43 | 1144000 | 660 | 100% | 100% | 61.42% | 0.7049 | 54600 | 243540 | 784173.026 | 1082313.026 | 5709.2462 | 92185.053 | 16.43 | 86.69%
[5 empty] | 16.44 | 1144000 | 660 | 100% | 100% | 61.53% | 0.70575 | 54600 | 243540 | 784651.7108 | 1082791.7108 | 5720.4228 | 92365.5182 | 16.44 | 86.72%
[5 empty] | 16.45 | 1144000 | 660 | 100% | 100% | 61.64% | 0.7066 | 54600 | 243540 | 785130.3956 | 1083270.3956 | 5731.6044 | 92546.0633 | 16.45 | 86.76%
[5 empty] | 16.46 | 1144000 | 660 | 100% | 100% | 61.75% | 0.70745 | 54600 | 243540 | 785609.0804 | 1083749.0804 | 5742.791 | 92726.6882 | 16.46 | 86.8%
[5 empty] | 16.47 | 1144000 | 660 | 100% | 100% | 61.86% | 0.7083 | 54600 | 243540 | 786087.7652 | 1084227.7652 | 5753.9825 | 92907.3928 | 16.47 | 86.84%
[5 empty] | 16.48 | 1144000 | 660 | 100% | 100% | 61.97% | 0.70915 | 54600 | 243540 | 786566.45 | 1084706.45 | 5765.1789 | 93088.1772 | 16.48 | 86.88%
[5 empty] | 16.49 | 1144000 | 660 | 100% | 100% | 62.08% | 0.71 | 54600 | 243540 | 787045.1348 | 1085185.1348 | 5776.3802 | 93269.0414 | 16.49 | 86.92%
[5 empty] | 16.5 | 1144000 | 660 | 100% | 100% | 62.19% | 0.71085 | 54600 | 243540 | 787523.8196 | 1085663.8196 | 5787.5866 | 93449.9853 | 16.5 | 86.95%
[5 empty] | 16.51 | 1144000 | 660 | 100% | 100% | 62.3% | 0.7117 | 54600 | 243540 | 788002.5044 | 1086142.5044 | 5798.7978 | 93631.0091 | 16.51 | 86.99%
[5 empty] | 16.52 | 1144000 | 660 | 100% | 100% | 62.42% | 0.71255 | 54600 | 243540 | 788481.1892 | 1086621.1892 | 5810.014 | 93812.1126 | 16.52 | 87.03%
[5 empty] | 16.53 | 1144000 | 660 | 100% | 100% | 62.53% | 0.71339 | 54600 | 243540 | 788959.874 | 1087099.874 | 5821.2351 | 93993.2959 | 16.53 | 87.07%
[5 empty] | 16.54 | 1144000 | 660 | 100% | 100% | 62.64% | 0.71424 | 54600 | 243540 | 789438.5588 | 1087578.5588 | 5832.4612 | 94174.559 | 16.54 | 87.11%
[5 empty] | 16.55 | 1144000 | 660 | 100% | 100% | 62.75% | 0.71509 | 54600 | 243540 | 789917.2436 | 1088057.2436 | 5843.6922 | 94355.9019 | 16.55 | 87.15%
[5 empty] | 16.56 | 1144000 | 660 | 100% | 100% | 62.86% | 0.71594 | 54600 | 243540 | 790395.9284 | 1088535.9284 | 5854.9281 | 94537.3246 | 16.56 | 87.18%
[5 empty] | 16.57 | 1144000 | 660 | 100% | 100% | 62.97% | 0.71679 | 54600 | 243540 | 790874.6132 | 1089014.6132 | 5866.169 | 94718.827 | 16.57 | 87.22%
[5 empty] | 16.58 | 1144000 | 660 | 100% | 100% | 63.08% | 0.71764 | 54600 | 243540 | 791353.298 | 1089493.298 | 5877.4149 | 94900.4092 | 16.58 | 87.26%
[5 empty] | 16.59 | 1144000 | 660 | 100% | 100% | 63.19% | 0.71849 | 54600 | 243540 | 791831.9828 | 1089971.9828 | 5888.6656 | 95082.0712 | 16.59 | 87.3%
[5 empty] | 16.6 | 1144000 | 660 | 100% | 100% | 63.3% | 0.71934 | 54600 | 243540 | 792310.6676 | 1090450.6676 | 5899.9213 | 95263.813 | 16.6 | 87.34%
[5 empty] | 16.61 | 1144000 | 660 | 100% | 100% | 63.42% | 0.72019 | 54600 | 243540 | 792789.3524 | 1090929.3524 | 5911.182 | 95445.6346 | 16.61 | 87.38%
[5 empty] | 16.62 | 1144000 | 660 | 100% | 100% | 63.53% | 0.72104 | 54600 | 243540 | 793268.0372 | 1091408.0372 | 5922.4476 | 95627.5359 | 16.62 | 87.41%
[5 empty] | 16.63 | 1144000 | 660 | 100% | 100% | 63.64% | 0.72189 | 54600 | 243540 | 793746.722 | 1091886.722 | 5933.7181 | 95809.517 | 16.63 | 87.45%
[5 empty] | 16.64 | 1144000 | 660 | 100% | 100% | 63.75% | 0.72274 | 54600 | 243540 | 794225.4068 | 1092365.4068 | 5944.9936 | 95991.5779 | 16.64 | 87.49%
[5 empty] | 16.65 | 1144000 | 660 | 100% | 100% | 63.86% | 0.72359 | 54600 | 243540 | 794704.0916 | 1092844.0916 | 5956.274 | 96173.7186 | 16.65 | 87.53%
[5 empty] | 16.66 | 1144000 | 660 | 100% | 100% | 63.97% | 0.72444 | 54600 | 243540 | 795182.7764 | 1093322.7764 | 5967.5594 | 96355.9391 | 16.66 | 87.57%
[5 empty] | 16.67 | 1144000 | 660 | 100% | 100% | 64.08% | 0.72529 | 54600 | 243540 | 795661.4612 | 1093801.4612 | 5978.8497 | 96538.2393 | 16.67 | 87.61%
[5 empty] | 16.68 | 1144000 | 660 | 100% | 100% | 64.19% | 0.72614 | 54600 | 243540 | 796140.146 | 1094280.146 | 5990.1449 | 96720.6193 | 16.68 | 87.64%
[5 empty] | 16.69 | 1144000 | 660 | 100% | 100% | 64.3% | 0.72699 | 54600 | 243540 | 796618.8308 | 1094758.8308 | 6001.4451 | 96903.0791 | 16.69 | 87.68%
[5 empty] | 16.7 | 1144000 | 660 | 100% | 100% | 64.42% | 0.72784 | 54600 | 243540 | 797097.5156 | 1095237.5156 | 6012.7502 | 97085.6187 | 16.7 | 87.72%
[5 empty] | 16.71 | 1144000 | 660 | 100% | 100% | 64.53% | 0.72869 | 54600 | 243540 | 797576.2004 | 1095716.2004 | 6024.0603 | 97268.2381 | 16.71 | 87.76%
[5 empty] | 16.72 | 1144000 | 660 | 100% | 100% | 64.64% | 0.72954 | 54600 | 243540 | 798054.8852 | 1096194.8852 | 6035.3753 | 97450.9372 | 16.72 | 87.8%
[5 empty] | 16.73 | 1144000 | 660 | 100% | 100% | 64.75% | 0.73039 | 54600 | 243540 | 798533.57 | 1096673.57 | 6046.6953 | 97633.7162 | 16.73 | 87.84%
[5 empty] | 16.74 | 1144000 | 660 | 100% | 100% | 64.86% | 0.73124 | 54600 | 243540 | 799012.2548 | 1097152.2548 | 6058.0201 | 97816.5749 | 16.74 | 87.87%
[5 empty] | 16.75 | 1144000 | 660 | 100% | 100% | 64.97% | 0.73209 | 54600 | 243540 | 799490.9396 | 1097630.9396 | 6069.35 | 97999.5134 | 16.75 | 87.91%
[5 empty] | 16.76 | 1144000 | 660 | 100% | 100% | 65.08% | 0.73294 | 54600 | 243540 | 799969.6244 | 1098109.6244 | 6080.6847 | 98182.5316 | 16.76 | 87.95%
[5 empty] | 16.77 | 1144000 | 660 | 100% | 100% | 65.19% | 0.73379 | 54600 | 243540 | 800448.3092 | 1098588.3092 | 6092.0244 | 98365.6297 | 16.77 | 87.99%
[5 empty] | 16.78 | 1144000 | 660 | 100% | 100% | 65.3% | 0.73464 | 54600 | 243540 | 800926.994 | 1099066.994 | 6103.3691 | 98548.8075 | 16.78 | 88.03%
[5 empty] | 16.79 | 1144000 | 660 | 100% | 100% | 65.42% | 0.73549 | 54600 | 243540 | 801405.6788 | 1099545.6788 | 6114.7187 | 98732.0651 | 16.79 | 88.07%
[5 empty] | 16.8 | 1144000 | 660 | 100% | 100% | 65.53% | 0.73634 | 54600 | 243540 | 801884.3636 | 1100024.3636 | 6126.0732 | 98915.4025 | 16.8 | 88.1%
[5 empty] | 16.81 | 1144000 | 660 | 100% | 100% | 65.64% | 0.73719 | 54600 | 243540 | 802363.0484 | 1100503.0484 | 6137.4327 | 99098.8197 | 16.81 | 88.14%
[5 empty] | 16.82 | 1144000 | 660 | 100% | 100% | 65.75% | 0.73804 | 54600 | 243540 | 802841.7332 | 1100981.7332 | 6148.7971 | 99282.3166 | 16.82 | 88.18%
[5 empty] | 16.83 | 1144000 | 660 | 100% | 100% | 65.86% | 0.73889 | 54600 | 243540 | 803320.418 | 1101460.418 | 6160.1665 | 99465.8934 | 16.83 | 88.22%
[5 empty] | 16.84 | 1144000 | 660 | 100% | 100% | 65.97% | 0.73974 | 54600 | 243540 | 803799.1028 | 1101939.1028 | 6171.5408 | 99649.5499 | 16.84 | 88.26%
[5 empty] | 16.85 | 1144000 | 660 | 100% | 100% | 66.08% | 0.74059 | 54600 | 243540 | 804277.7876 | 1102417.7876 | 6182.92 | 99833.2862 | 16.85 | 88.3%
[5 empty] | 16.86 | 1144000 | 660 | 100% | 100% | 66.19% | 0.74144 | 54600 | 243540 | 804756.4724 | 1102896.4724 | 6194.3042 | 100017.1023 | 16.86 | 88.33%
[5 empty] | 16.87 | 1144000 | 660 | 100% | 100% | 66.3% | 0.74229 | 54600 | 243540 | 805235.1572 | 1103375.1572 | 6205.6933 | 100200.9981 | 16.87 | 88.37%
[5 empty] | 16.88 | 1144000 | 660 | 100% | 100% | 66.42% | 0.74314 | 54600 | 243540 | 805713.842 | 1103853.842 | 6217.0874 | 100384.9738 | 16.88 | 88.41%
[5 empty] | 16.89 | 1144000 | 660 | 100% | 100% | 66.53% | 0.74399 | 54600 | 243540 | 806192.5268 | 1104332.5268 | 6228.4864 | 100569.0292 | 16.89 | 88.45%
[5 empty] | 16.9 | 1144000 | 660 | 100% | 100% | 66.64% | 0.74484 | 54600 | 243540 | 806671.2116 | 1104811.2116 | 6239.8903 | 100753.1644 | 16.9 | 88.49%
[5 empty] | 16.91 | 1144000 | 660 | 100% | 100% | 66.75% | 0.74569 | 54600 | 243540 | 807149.8964 | 1105289.8964 | 6251.2992 | 100937.3794 | 16.91 | 88.53%
[5 empty] | 16.92 | 1144000 | 660 | 100% | 100% | 66.86% | 0.74654 | 54600 | 243540 | 807628.5812 | 1105768.5812 | 6262.713 | 101121.6741 | 16.92 | 88.56%
[5 empty] | 16.93 | 1144000 | 660 | 100% | 100% | 66.97% | 0.74739 | 54600 | 243540 | 808107.266 | 1106247.266 | 6274.1318 | 101306.0487 | 16.93 | 88.6%
[5 empty] | 16.94 | 1144000 | 660 | 100% | 100% | 67.08% | 0.74824 | 54600 | 243540 | 808585.9508 | 1106725.9508 | 6285.5555 | 101490.503 | 16.94 | 88.64%
[5 empty] | 16.95 | 1144000 | 660 | 100% | 100% | 67.19% | 0.74909 | 54600 | 243540 | 809064.6356 | 1107204.6356 | 6296.9842 | 101675.0371 | 16.95 | 88.68%
[5 empty] | 16.96 | 1144000 | 660 | 100% | 100% | 67.3% | 0.74994 | 54600 | 243540 | 809543.3204 | 1107683.3204 | 6308.4178 | 101859.651 | 16.96 | 88.72%
[5 empty] | 16.97 | 1144000 | 660 | 100% | 100% | 67.42% | 0.75079 | 54600 | 243540 | 810022.0052 | 1108162.0052 | 6319.8563 | 102044.3447 | 16.97 | 88.76%
[5 empty] | 16.98 | 1144000 | 660 | 100% | 100% | 67.53% | 0.75164 | 54600 | 243540 | 810500.69 | 1108640.69 | 6331.2998 | 102229.1181 | 16.98 | 88.79%
[5 empty] | 16.99 | 1144000 | 660 | 100% | 100% | 67.64% | 0.75249 | 54600 | 243540 | 810979.3748 | 1109119.3748 | 6342.7482 | 102413.9714 | 16.99 | 88.83%
[5 empty] | 17 | 1144000 | 660 | 100% | 100% | 67.75% | 0.75334 | 54600 | 243540 | 811458.0596 | 1109598.0596 | 6354.2015 | 102598.9044 | 17 | 88.87%
[5 empty] | 17.01 | 1144000 | 660 | 100% | 100% | 67.86% | 0.75419 | 54600 | 243540 | 811936.7444 | 1110076.7444 | 6365.6598 | 102783.9172 | 17.01 | 88.91%
[5 empty] | 17.02 | 1144000 | 660 | 100% | 100% | 67.97% | 0.75504 | 54600 | 243540 | 812415.4292 | 1110555.4292 | 6377.1231 | 102969.0097 | 17.02 | 88.95%
[5 empty] | 17.03 | 1144000 | 660 | 100% | 100% | 68.08% | 0.75589 | 54600 | 243540 | 812894.114 | 1111034.114 | 6388.5912 | 103154.1821 | 17.03 | 88.99%
[5 empty] | 17.04 | 1144000 | 660 | 100% | 100% | 68.19% | 0.75674 | 54600 | 243540 | 813372.7988 | 1111512.7988 | 6400.0644 | 103339.4342 | 17.04 | 89.03%
[5 empty] | 17.05 | 1144000 | 660 | 100% | 100% | 68.3% | 0.75759 | 54600 | 243540 | 813851.4836 | 1111991.4836 | 6411.5424 | 103524.7661 | 17.05 | 89.06%
[5 empty] | 17.06 | 1144000 | 660 | 100% | 100% | 68.42% | 0.75843 | 54600 | 243540 | 814330.1684 | 1112470.1684 | 6423.0254 | 103710.1778 | 17.06 | 89.1%
[5 empty] | 17.07 | 1144000 | 660 | 100% | 100% | 68.53% | 0.75928 | 54600 | 243540 | 814808.8532 | 1112948.8532 | 6434.5134 | 103895.6693 | 17.07 | 89.14%
[5 empty] | 17.08 | 1144000 | 660 | 100% | 100% | 68.64% | 0.76013 | 54600 | 243540 | 815287.538 | 1113427.538 | 6446.0062 | 104081.2406 | 17.08 | 89.18%
[5 empty] | 17.09 | 1144000 | 660 | 100% | 100% | 68.75% | 0.76098 | 54600 | 243540 | 815766.2228 | 1113906.2228 | 6457.5041 | 104266.8916 | 17.09 | 89.22%
[5 empty] | 17.1 | 1144000 | 660 | 100% | 100% | 68.86% | 0.76183 | 54600 | 243540 | 816244.9076 | 1114384.9076 | 6469.0068 | 104452.6224 | 17.1 | 89.26%
[5 empty] | 17.11 | 1144000 | 660 | 100% | 100% | 68.97% | 0.76268 | 54600 | 243540 | 816723.5924 | 1114863.5924 | 6480.5145 | 104638.433 | 17.11 | 89.29%
[5 empty] | 17.12 | 1144000 | 660 | 100% | 100% | 69.08% | 0.76353 | 54600 | 243540 | 817202.2772 | 1115342.2772 | 6492.0272 | 104824.3234 | 17.12 | 89.33%
[5 empty] | 17.13 | 1144000 | 660 | 100% | 100% | 69.19% | 0.76438 | 54600 | 243540 | 817680.962 | 1115820.962 | 6503.5448 | 105010.2935 | 17.13 | 89.37%
[5 empty] | 17.14 | 1144000 | 660 | 100% | 100% | 69.3% | 0.76523 | 54600 | 243540 | 818159.6468 | 1116299.6468 | 6515.0673 | 105196.3435 | 17.14 | 89.41%
[5 empty] | 17.15 | 1144000 | 660 | 100% | 100% | 69.42% | 0.76608 | 54600 | 243540 | 818638.3316 | 1116778.3316 | 6526.5948 | 105382.4732 | 17.15 | 89.45%
[5 empty] | 17.16 | 1144000 | 660 | 100% | 100% | 69.53% | 0.76693 | 54600 | 243540 | 819117.0164 | 1117257.0164 | 6538.1272 | 105568.6827 | 17.16 | 89.49%
[5 empty] | 17.17 | 1144000 | 660 | 100% | 100% | 69.64% | 0.76778 | 54600 | 243540 | 819595.7012 | 1117735.7012 | 6549.6645 | 105754.972 | 17.17 | 89.52%
[5 empty] | 17.18 | 1144000 | 660 | 100% | 100% | 69.75% | 0.76863 | 54600 | 243540 | 820074.386 | 1118214.386 | 6561.2068 | 105941.3411 | 17.18 | 89.56%
[5 empty] | 17.19 | 1144000 | 660 | 100% | 100% | 69.86% | 0.76948 | 54600 | 243540 | 820553.0708 | 1118693.0708 | 6572.7541 | 106127.7899 | 17.19 | 89.6%
[5 empty] | 17.2 | 1144000 | 660 | 100% | 100% | 69.97% | 0.77033 | 54600 | 243540 | 821031.7556 | 1119171.7556 | 6584.3062 | 106314.3185 | 17.2 | 89.64%
[5 empty] | 17.21 | 1144000 | 660 | 100% | 100% | 70.08% | 0.77118 | 54600 | 243540 | 821510.4404 | 1119650.4404 | 6595.8633 | 106500.9269 | 17.21 | 89.68%
[5 empty] | 17.22 | 1144000 | 660 | 100% | 100% | 70.19% | 0.77203 | 54600 | 243540 | 821989.1252 | 1120129.1252 | 6607.4254 | 106687.6151 | 17.22 | 89.72%
[5 empty] | 17.23 | 1144000 | 660 | 100% | 100% | 70.3% | 0.77288 | 54600 | 243540 | 822467.81 | 1120607.81 | 6618.9924 | 106874.3831 | 17.23 | 89.75%
[5 empty] | 17.24 | 1144000 | 660 | 100% | 100% | 70.42% | 0.77373 | 54600 | 243540 | 822946.4948 | 1121086.4948 | 6630.5643 | 107061.2308 | 17.24 | 89.79%
[5 empty] | 17.25 | 1144000 | 660 | 100% | 100% | 70.53% | 0.77458 | 54600 | 243540 | 823425.1796 | 1121565.1796 | 6642.1412 | 107248.1584 | 17.25 | 89.83%
[5 empty] | 17.26 | 1144000 | 660 | 100% | 100% | 70.64% | 0.77543 | 54600 | 243540 | 823903.8644 | 1122043.8644 | 6653.723 | 107435.1657 | 17.26 | 89.87%
[5 empty] | 17.27 | 1144000 | 660 | 100% | 100% | 70.75% | 0.77628 | 54600 | 243540 | 824382.5492 | 1122522.5492 | 6665.3098 | 107622.2528 | 17.27 | 89.91%
[5 empty] | 17.28 | 1144000 | 660 | 100% | 100% | 70.86% | 0.77713 | 54600 | 243540 | 824861.234 | 1123001.234 | 6676.9015 | 107809.4196 | 17.28 | 89.95%
[5 empty] | 17.29 | 1144000 | 660 | 100% | 100% | 70.97% | 0.77798 | 54600 | 243540 | 825339.9188 | 1123479.9188 | 6688.4981 | 107996.6663 | 17.29 | 89.98%
[5 empty] | 17.3 | 1144000 | 660 | 100% | 100% | 71.08% | 0.77883 | 54600 | 243540 | 825818.6036 | 1123958.6036 | 6700.0997 | 108183.9927 | 17.3 | 90.02%
[5 empty] | 17.31 | 1144000 | 660 | 100% | 100% | 71.19% | 0.77968 | 54600 | 243540 | 826297.2884 | 1124437.2884 | 6711.7063 | 108371.399 | 17.31 | 90.06%
[5 empty] | 17.32 | 1144000 | 660 | 100% | 100% | 71.3% | 0.78053 | 54600 | 243540 | 826775.9732 | 1124915.9732 | 6723.3177 | 108558.8849 | 17.32 | 90.1%
[5 empty] | 17.33 | 1144000 | 660 | 100% | 100% | 71.42% | 0.78138 | 54600 | 243540 | 827254.658 | 1125394.658 | 6734.9341 | 108746.4507 | 17.33 | 90.14%
[5 empty] | 17.34 | 1144000 | 660 | 100% | 100% | 71.53% | 0.78223 | 54600 | 243540 | 827733.3428 | 1125873.3428 | 6746.5555 | 108934.0963 | 17.34 | 90.18%
[5 empty] | 17.35 | 1144000 | 660 | 100% | 100% | 71.64% | 0.78308 | 54600 | 243540 | 828212.0276 | 1126352.0276 | 6758.1818 | 109121.8216 | 17.35 | 90.21%
[5 empty] | 17.36 | 1144000 | 660 | 100% | 100% | 71.75% | 0.78393 | 54600 | 243540 | 828690.7124 | 1126830.7124 | 6769.813 | 109309.6267 | 17.36 | 90.25%
[5 empty] | 17.37 | 1144000 | 660 | 100% | 100% | 71.86% | 0.78478 | 54600 | 243540 | 829169.3972 | 1127309.3972 | 6781.4492 | 109497.5116 | 17.37 | 90.29%
[5 empty] | 17.38 | 1144000 | 660 | 100% | 100% | 71.97% | 0.78563 | 54600 | 243540 | 829648.082 | 1127788.082 | 6793.0903 | 109685.4763 | 17.38 | 90.33%
[5 empty] | 17.39 | 1144000 | 660 | 100% | 100% | 72.08% | 0.78648 | 54600 | 243540 | 830126.7668 | 1128266.7668 | 6804.7363 | 109873.5208 | 17.39 | 90.37%
[5 empty] | 17.4 | 1144000 | 660 | 100% | 100% | 72.19% | 0.78733 | 54600 | 243540 | 830605.4516 | 1128745.4516 | 6816.3873 | 110061.645 | 17.4 | 90.41%
[5 empty] | 17.41 | 1144000 | 660 | 100% | 100% | 72.3% | 0.78818 | 54600 | 243540 | 831084.1364 | 1129224.1364 | 6828.0433 | 110249.849 | 17.41 | 90.44%
[5 empty] | 17.42 | 1144000 | 660 | 100% | 100% | 72.42% | 0.78903 | 54600 | 243540 | 831562.8212 | 1129702.8212 | 6839.7041 | 110438.1328 | 17.42 | 90.48%
[5 empty] | 17.43 | 1144000 | 660 | 100% | 100% | 72.53% | 0.78988 | 54600 | 243540 | 832041.506 | 1130181.506 | 6851.37 | 110626.4964 | 17.43 | 90.52%
[5 empty] | 17.44 | 1144000 | 660 | 100% | 100% | 72.64% | 0.79073 | 54600 | 243540 | 832520.1908 | 1130660.1908 | 6863.0407 | 110814.9398 | 17.44 | 90.56%
[5 empty] | 17.45 | 1144000 | 660 | 100% | 100% | 72.75% | 0.79158 | 54600 | 243540 | 832998.8756 | 1131138.8756 | 6874.7164 | 111003.4629 | 17.45 | 90.6%
[5 empty] | 17.46 | 1144000 | 660 | 100% | 100% | 72.86% | 0.79243 | 54600 | 243540 | 833477.5604 | 1131617.5604 | 6886.3971 | 111192.0659 | 17.46 | 90.64%
[5 empty] | 17.47 | 1144000 | 660 | 100% | 100% | 72.97% | 0.79328 | 54600 | 243540 | 833956.2452 | 1132096.2452 | 6898.0827 | 111380.7486 | 17.47 | 90.67%
[5 empty] | 17.48 | 1144000 | 660 | 100% | 100% | 73.08% | 0.79413 | 54600 | 243540 | 834434.93 | 1132574.93 | 6909.7732 | 111569.5111 | 17.48 | 90.71%
[5 empty] | 17.49 | 1144000 | 660 | 100% | 100% | 73.19% | 0.79498 | 54600 | 243540 | 834913.6148 | 1133053.6148 | 6921.4686 | 111758.3533 | 17.49 | 90.75%
[5 empty] | 17.5 | 1144000 | 660 | 100% | 100% | 73.3% | 0.79583 | 54600 | 243540 | 835392.2996 | 1133532.2996 | 6933.169 | 111947.2754 | 17.5 | 90.79%
[5 empty] | 17.51 | 1144000 | 660 | 100% | 100% | 73.42% | 0.79668 | 54600 | 243540 | 835870.9844 | 1134010.9844 | 6944.8744 | 112136.2772 | 17.51 | 90.83%
[5 empty] | 17.52 | 1144000 | 660 | 100% | 100% | 73.53% | 0.79753 | 54600 | 243540 | 836349.6692 | 1134489.6692 | 6956.5847 | 112325.3588 | 17.52 | 90.87%
[5 empty] | 17.53 | 1144000 | 660 | 100% | 100% | 73.64% | 0.79838 | 54600 | 243540 | 836828.354 | 1134968.354 | 6968.2999 | 112514.5202 | 17.53 | 90.9%
[5 empty] | 17.54 | 1144000 | 660 | 100% | 100% | 73.75% | 0.79923 | 54600 | 243540 | 837307.0388 | 1135447.0388 | 6980.0201 | 112703.7614 | 17.54 | 90.94%
[5 empty] | 17.55 | 1144000 | 660 | 100% | 100% | 73.86% | 0.80008 | 54600 | 243540 | 837785.7236 | 1135925.7236 | 6991.7452 | 112893.0823 | 17.55 | 90.98%
[5 empty] | 17.56 | 1144000 | 660 | 100% | 100% | 73.97% | 0.80093 | 54600 | 243540 | 838264.4084 | 1136404.4084 | 7003.4752 | 113082.4831 | 17.56 | 91.02%
[5 empty] | 17.57 | 1144000 | 660 | 100% | 100% | 74.08% | 0.80178 | 54600 | 243540 | 838743.0932 | 1136883.0932 | 7015.2102 | 113271.9636 | 17.57 | 91.06%
[5 empty] | 17.58 | 1144000 | 660 | 100% | 100% | 74.19% | 0.80262 | 54600 | 243540 | 839221.778 | 1137361.778 | 7026.9502 | 113461.5239 | 17.58 | 91.1%
[5 empty] | 17.59 | 1144000 | 660 | 100% | 100% | 74.3% | 0.80347 | 54600 | 243540 | 839700.4628 | 1137840.4628 | 7038.695 | 113651.164 | 17.59 | 91.13%
[5 empty] | 17.6 | 1144000 | 660 | 100% | 100% | 74.42% | 0.80432 | 54600 | 243540 | 840179.1476 | 1138319.1476 | 7050.4449 | 113840.8838 | 17.6 | 91.17%
[5 empty] | 17.61 | 1144000 | 660 | 100% | 100% | 74.53% | 0.80517 | 54600 | 243540 | 840657.8324 | 1138797.8324 | 7062.1996 | 114030.6835 | 17.61 | 91.21%
[5 empty] | 17.62 | 1144000 | 660 | 100% | 100% | 74.64% | 0.80602 | 54600 | 243540 | 841136.5172 | 1139276.5172 | 7073.9593 | 114220.5629 | 17.62 | 91.25%
[5 empty] | 17.63 | 1144000 | 660 | 100% | 100% | 74.75% | 0.80687 | 54600 | 243540 | 841615.202 | 1139755.202 | 7085.7239 | 114410.5221 | 17.63 | 91.29%
[5 empty] | 17.64 | 1144000 | 660 | 100% | 100% | 74.86% | 0.80772 | 54600 | 243540 | 842093.8868 | 1140233.8868 | 7097.4935 | 114600.5611 | 17.64 | 91.33%
[5 empty] | 17.65 | 1144000 | 660 | 100% | 100% | 74.97% | 0.80857 | 54600 | 243540 | 842572.5716 | 1140712.5716 | 7109.268 | 114790.6798 | 17.65 | 91.36%
[5 empty] | 17.66 | 1144000 | 660 | 100% | 100% | 75.08% | 0.80942 | 54600 | 243540 | 843051.2564 | 1141191.2564 | 7121.0475 | 114980.8784 | 17.66 | 91.4%
[5 empty] | 17.67 | 1144000 | 660 | 100% | 100% | 75.19% | 0.81027 | 54600 | 243540 | 843529.9412 | 1141669.9412 | 7132.8319 | 115171.1567 | 17.67 | 91.44%
[5 empty] | 17.68 | 1144000 | 660 | 100% | 100% | 75.3% | 0.81112 | 54600 | 243540 | 844008.626 | 1142148.626 | 7144.6213 | 115361.5148 | 17.68 | 91.48%
[5 empty] | 17.69 | 1144000 | 660 | 100% | 100% | 75.42% | 0.81197 | 54600 | 243540 | 844487.3108 | 1142627.3108 | 7156.4155 | 115551.9527 | 17.69 | 91.52%
[5 empty] | 17.7 | 1144000 | 660 | 100% | 100% | 75.53% | 0.81282 | 54600 | 243540 | 844965.9956 | 1143105.9956 | 7168.2148 | 115742.4703 | 17.7 | 91.56%
[5 empty] | 17.71 | 1144000 | 660 | 100% | 100% | 75.64% | 0.81367 | 54600 | 243540 | 845444.6804 | 1143584.6804 | 7180.0189 | 115933.0678 | 17.71 | 91.59%
[5 empty] | 17.72 | 1144000 | 660 | 100% | 100% | 75.75% | 0.81452 | 54600 | 243540 | 845860 | 1144000 | 7191.8274 | 116123.7345 | 17.72 | 91.63%
[5 empty] | 17.73 | 1144000 | 660 | 100% | 100% | 75.86% | 0.81537 | 54600 | 243540 | 845860 | 1144000 | 7203.6358 | 116314.4011 | 17.73 | 91.63%
[5 empty] | 17.74 | 1144000 | 660 | 100% | 100% | 75.97% | 0.81622 | 54600 | 243540 | 845860 | 1144000 | 7215.4443 | 116505.0678 | 17.74 | 91.63%
[5 empty] | 17.75 | 1144000 | 660 | 100% | 100% | 76.08% | 0.81707 | 54600 | 243540 | 845860 | 1144000 | 7227.2527 | 116695.7345 | 17.75 | 91.63%
[5 empty] | 17.76 | 1144000 | 660 | 100% | 100% | 76.19% | 0.81792 | 54600 | 243540 | 845860 | 1144000 | 7239.0612 | 116886.4011 | 17.76 | 91.63%
[5 empty] | 17.77 | 1144000 | 660 | 100% | 100% | 76.3% | 0.81877 | 54600 | 243540 | 845860 | 1144000 | 7250.8697 | 117077.0678 | 17.77 | 91.63%
[5 empty] | 17.78 | 1144000 | 660 | 100% | 100% | 76.42% | 0.81962 | 54600 | 243540 | 845860 | 1144000 | 7262.6781 | 117267.7345 | 17.78 | 91.63%
[5 empty] | 17.79 | 1144000 | 660 | 100% | 100% | 76.53% | 0.82047 | 54600 | 243540 | 845860 | 1144000 | 7274.4866 | 117458.4011 | 17.79 | 91.63%
[5 empty] | 17.8 | 1144000 | 660 | 100% | 100% | 76.64% | 0.82132 | 54600 | 243540 | 845860 | 1144000 | 7286.295 | 117649.0678 | 17.8 | 91.63%
[5 empty] | 17.81 | 1144000 | 660 | 100% | 100% | 76.75% | 0.82217 | 54600 | 243540 | 845860 | 1144000 | 7298.1035 | 117839.7345 | 17.81 | 91.63%
[5 empty] | 17.82 | 1144000 | 660 | 100% | 100% | 76.86% | 0.82302 | 54600 | 243540 | 845860 | 1144000 | 7309.9119 | 118030.4011 | 17.82 | 91.63%
[5 empty] | 17.83 | 1144000 | 660 | 100% | 100% | 76.97% | 0.82387 | 54600 | 243540 | 845860 | 1144000 | 7321.7204 | 118221.0678 | 17.83 | 91.63%
[5 empty] | 17.84 | 1144000 | 660 | 100% | 100% | 77.08% | 0.82472 | 54600 | 243540 | 845860 | 1144000 | 7333.5288 | 118411.7345 | 17.84 | 91.63%
[5 empty] | 17.85 | 1144000 | 660 | 100% | 100% | 77.19% | 0.82557 | 54600 | 243540 | 845860 | 1144000 | 7345.3373 | 118602.4011 | 17.85 | 91.63%
[5 empty] | 17.86 | 1144000 | 660 | 100% | 100% | 77.3% | 0.82642 | 54600 | 243540 | 845860 | 1144000 | 7357.1457 | 118793.0678 | 17.86 | 91.63%
[5 empty] | 17.87 | 1144000 | 660 | 100% | 100% | 77.42% | 0.82727 | 54600 | 243540 | 845860 | 1144000 | 7368.9542 | 118983.7345 | 17.87 | 91.63%
[5 empty] | 17.88 | 1144000 | 660 | 100% | 100% | 77.53% | 0.82812 | 54600 | 243540 | 845860 | 1144000 | 7380.7626 | 119174.4011 | 17.88 | 91.63%
[5 empty] | 17.89 | 1144000 | 660 | 100% | 100% | 77.64% | 0.82897 | 54600 | 243540 | 845860 | 1144000 | 7392.5711 | 119365.0678 | 17.89 | 91.63%
[5 empty] | 17.9 | 1144000 | 660 | 100% | 100% | 77.75% | 0.82982 | 54600 | 243540 | 845860 | 1144000 | 7404.3796 | 119555.7345 | 17.9 | 91.63%
[5 empty] | 17.91 | 1144000 | 660 | 100% | 100% | 77.86% | 0.83067 | 54600 | 243540 | 845860 | 1144000 | 7416.188 | 119746.4011 | 17.91 | 91.63%
[5 empty] | 17.92 | 1144000 | 660 | 100% | 100% | 77.97% | 0.83152 | 54600 | 243540 | 845860 | 1144000 | 7427.9965 | 119937.0678 | 17.92 | 91.63%
[5 empty] | 17.93 | 1144000 | 660 | 100% | 100% | 78.08% | 0.83237 | 54600 | 243540 | 845860 | 1144000 | 7439.8049 | 120127.7345 | 17.93 | 91.63%
[5 empty] | 17.94 | 1144000 | 660 | 100% | 100% | 78.19% | 0.83322 | 54600 | 243540 | 845860 | 1144000 | 7451.6134 | 120318.4011 | 17.94 | 91.63%
[5 empty] | 17.95 | 1144000 | 660 | 100% | 100% | 78.3% | 0.83407 | 54600 | 243540 | 845860 | 1144000 | 7463.4218 | 120509.0678 | 17.95 | 91.63%
[5 empty] | 17.96 | 1144000 | 660 | 100% | 100% | 78.42% | 0.83492 | 54600 | 243540 | 845860 | 1144000 | 7475.2303 | 120699.7345 | 17.96 | 91.63%
[5 empty] | 17.97 | 1144000 | 660 | 100% | 100% | 78.53% | 0.83577 | 54600 | 243540 | 845860 | 1144000 | 7487.0387 | 120890.4011 | 17.97 | 91.63%
[5 empty] | 17.98 | 1144000 | 660 | 100% | 100% | 78.64% | 0.83662 | 54600 | 243540 | 845860 | 1144000 | 7498.8472 | 121081.0678 | 17.98 | 91.63%
[5 empty] | 17.99 | 1144000 | 660 | 100% | 100% | 78.75% | 0.83747 | 54600 | 243540 | 845860 | 1144000 | 7510.6556 | 121271.7345 | 17.99 | 91.63%
[5 empty] | 18 | 1144000 | 660 | 100% | 100% | 78.86% | 0.83832 | 54600 | 243540 | 845860 | 1144000 | 7522.4641 | 121462.4011 | 18 | 91.63%
[5 empty] | 18.01 | 1144000 | 660 | 100% | 100% | 78.97% | 0.83917 | 54600 | 243540 | 845860 | 1144000 | 7534.2725 | 121653.0678 | 18.01 | 91.63%
[5 empty] | 18.02 | 1144000 | 660 | 100% | 100% | 79.08% | 0.84002 | 54600 | 243540 | 845860 | 1144000 | 7546.081 | 121843.7345 | 18.02 | 91.63%
[5 empty] | 18.03 | 1144000 | 660 | 100% | 100% | 79.19% | 0.84087 | 54600 | 243540 | 845860 | 1144000 | 7557.8895 | 122034.4011 | 18.03 | 91.63%
[5 empty] | 18.04 | 1144000 | 660 | 100% | 100% | 79.3% | 0.84172 | 54600 | 243540 | 845860 | 1144000 | 7569.6979 | 122225.0678 | 18.04 | 91.63%
[5 empty] | 18.05 | 1144000 | 660 | 100% | 100% | 79.42% | 0.84257 | 54600 | 243540 | 845860 | 1144000 | 7581.5064 | 122415.7345 | 18.05 | 91.63%
[5 empty] | 18.06 | 1144000 | 660 | 100% | 100% | 79.53% | 0.84342 | 54600 | 243540 | 845860 | 1144000 | 7593.3148 | 122606.4011 | 18.06 | 91.63%
[5 empty] | 18.07 | 1144000 | 660 | 100% | 100% | 79.64% | 0.84427 | 54600 | 243540 | 845860 | 1144000 | 7605.1233 | 122797.0678 | 18.07 | 91.63%
[5 empty] | 18.08 | 1144000 | 660 | 100% | 100% | 79.75% | 0.84512 | 54600 | 243540 | 845860 | 1144000 | 7616.9317 | 122987.7345 | 18.08 | 91.63%
[5 empty] | 18.09 | 1144000 | 660 | 100% | 100% | 79.86% | 0.84597 | 54600 | 243540 | 845860 | 1144000 | 7628.7402 | 123178.4011 | 18.09 | 91.63%
[5 empty] | 18.1 | 1144000 | 660 | 100% | 100% | 79.97% | 0.84682 | 54600 | 243540 | 845860 | 1144000 | 7640.5486 | 123369.0678 | 18.1 | 91.63%
[5 empty] | 18.11 | 1144000 | 660 | 100% | 100% | 80.08% | 0.84766 | 54600 | 243540 | 845860 | 1144000 | 7652.3571 | 123559.7345 | 18.11 | 91.63%
[5 empty] | 18.12 | 1144000 | 660 | 100% | 100% | 80.19% | 0.84851 | 54600 | 243540 | 845860 | 1144000 | 7664.1655 | 123750.4011 | 18.12 | 91.63%
[5 empty] | 18.13 | 1144000 | 660 | 100% | 100% | 80.3% | 0.84936 | 54600 | 243540 | 845860 | 1144000 | 7675.974 | 123941.0678 | 18.13 | 91.63%
[5 empty] | 18.14 | 1144000 | 660 | 100% | 100% | 80.42% | 0.85021 | 54600 | 243540 | 845860 | 1144000 | 7687.7824 | 124131.7345 | 18.14 | 91.63%
[5 empty] | 18.15 | 1144000 | 660 | 100% | 100% | 80.53% | 0.85106 | 54600 | 243540 | 845860 | 1144000 | 7699.5909 | 124322.4011 | 18.15 | 91.63%
[5 empty] | 18.16 | 1144000 | 660 | 100% | 100% | 80.64% | 0.85191 | 54600 | 243540 | 845860 | 1144000 | 7711.3994 | 124513.0678 | 18.16 | 91.63%
[5 empty] | 18.17 | 1144000 | 660 | 100% | 100% | 80.75% | 0.85276 | 54600 | 243540 | 845860 | 1144000 | 7723.2078 | 124703.7345 | 18.17 | 91.63%
[5 empty] | 18.18 | 1144000 | 660 | 100% | 100% | 80.86% | 0.85361 | 54600 | 243540 | 845860 | 1144000 | 7735.0163 | 124894.4011 | 18.18 | 91.63%
[5 empty] | 18.19 | 1144000 | 660 | 100% | 100% | 80.97% | 0.85446 | 54600 | 243540 | 845860 | 1144000 | 7746.8247 | 125085.0678 | 18.19 | 91.63%
[5 empty] | 18.2 | 1144000 | 660 | 100% | 100% | 81.08% | 0.85531 | 54600 | 243540 | 845860 | 1144000 | 7758.6332 | 125275.7345 | 18.2 | 91.63%
[5 empty] | 18.21 | 1144000 | 660 | 100% | 100% | 81.19% | 0.85616 | 54600 | 243540 | 845860 | 1144000 | 7770.4416 | 125466.4011 | 18.21 | 91.63%
[5 empty] | 18.22 | 1144000 | 660 | 100% | 100% | 81.3% | 0.85701 | 54600 | 243540 | 845860 | 1144000 | 7782.2501 | 125657.0678 | 18.22 | 91.63%
[5 empty] | 18.23 | 1144000 | 660 | 100% | 100% | 81.42% | 0.85786 | 54600 | 243540 | 845860 | 1144000 | 7794.0585 | 125847.7345 | 18.23 | 91.63%
[5 empty] | 18.24 | 1144000 | 660 | 100% | 100% | 81.53% | 0.85871 | 54600 | 243540 | 845860 | 1144000 | 7805.867 | 126038.4011 | 18.24 | 91.63%
[5 empty] | 18.25 | 1144000 | 660 | 100% | 100% | 81.64% | 0.85956 | 54600 | 243540 | 845860 | 1144000 | 7817.6754 | 126229.0678 | 18.25 | 91.63%
[5 empty] | 18.26 | 1144000 | 660 | 100% | 100% | 81.75% | 0.86041 | 54600 | 243540 | 845860 | 1144000 | 7829.4839 | 126419.7345 | 18.26 | 91.63%
[5 empty] | 18.27 | 1144000 | 660 | 100% | 100% | 81.86% | 0.86126 | 54600 | 243540 | 845860 | 1144000 | 7841.2923 | 126610.4011 | 18.27 | 91.63%
[5 empty] | 18.28 | 1144000 | 660 | 100% | 100% | 81.97% | 0.86211 | 54600 | 243540 | 845860 | 1144000 | 7853.1008 | 126801.0678 | 18.28 | 91.63%
[5 empty] | 18.29 | 1144000 | 660 | 100% | 100% | 82.08% | 0.86296 | 54600 | 243540 | 845860 | 1144000 | 7864.9093 | 126991.7345 | 18.29 | 91.63%
[5 empty] | 18.3 | 1144000 | 660 | 100% | 100% | 82.19% | 0.86381 | 54600 | 243540 | 845860 | 1144000 | 7876.7177 | 127182.4011 | 18.3 | 91.63%
[5 empty] | 18.31 | 1144000 | 660 | 100% | 100% | 82.3% | 0.86466 | 54600 | 243540 | 845860 | 1144000 | 7888.5262 | 127373.0678 | 18.31 | 91.63%
[5 empty] | 18.32 | 1144000 | 660 | 100% | 100% | 82.42% | 0.86551 | 54600 | 243540 | 845860 | 1144000 | 7900.3346 | 127563.7345 | 18.32 | 91.63%
[5 empty] | 18.33 | 1144000 | 660 | 100% | 100% | 82.53% | 0.86636 | 54600 | 243540 | 845860 | 1144000 | 7912.1431 | 127754.4011 | 18.33 | 91.63%
[5 empty] | 18.34 | 1144000 | 660 | 100% | 100% | 82.64% | 0.86721 | 54600 | 243540 | 845860 | 1144000 | 7923.9515 | 127945.0678 | 18.34 | 91.63%
[5 empty] | 18.35 | 1144000 | 660 | 100% | 100% | 82.75% | 0.86806 | 54600 | 243540 | 845860 | 1144000 | 7935.76 | 128135.7345 | 18.35 | 91.63%
[5 empty] | 18.36 | 1144000 | 660 | 100% | 100% | 82.86% | 0.86891 | 54600 | 243540 | 845860 | 1144000 | 7947.5684 | 128326.4011 | 18.36 | 91.63%
[5 empty] | 18.37 | 1144000 | 660 | 100% | 100% | 82.97% | 0.86976 | 54600 | 243540 | 845860 | 1144000 | 7959.3769 | 128517.0678 | 18.37 | 91.63%
[5 empty] | 18.38 | 1144000 | 660 | 100% | 100% | 83.08% | 0.87061 | 54600 | 243540 | 845860 | 1144000 | 7971.1853 | 128707.7345 | 18.38 | 91.63%
[5 empty] | 18.39 | 1144000 | 660 | 100% | 100% | 83.19% | 0.87146 | 54600 | 243540 | 845860 | 1144000 | 7982.9938 | 128898.4011 | 18.39 | 91.63%
[5 empty] | 18.4 | 1144000 | 660 | 100% | 100% | 83.3% | 0.87231 | 54600 | 243540 | 845860 | 1144000 | 7994.8022 | 129089.0678 | 18.4 | 91.63%
[5 empty] | 18.41 | 1144000 | 660 | 100% | 100% | 83.42% | 0.87316 | 54600 | 243540 | 845860 | 1144000 | 8006.6107 | 129279.7345 | 18.41 | 91.63%
[5 empty] | 18.42 | 1144000 | 660 | 100% | 100% | 83.53% | 0.87401 | 54600 | 243540 | 845860 | 1144000 | 8018.4192 | 129470.4011 | 18.42 | 91.63%
[5 empty] | 18.43 | 1144000 | 660 | 100% | 100% | 83.64% | 0.87486 | 54600 | 243540 | 845860 | 1144000 | 8030.2276 | 129661.0678 | 18.43 | 91.63%
[5 empty] | 18.44 | 1144000 | 660 | 100% | 100% | 83.75% | 0.87571 | 54600 | 243540 | 845860 | 1144000 | 8042.0361 | 129851.7345 | 18.44 | 91.63%
[5 empty] | 18.45 | 1144000 | 660 | 100% | 100% | 83.86% | 0.87656 | 54600 | 243540 | 845860 | 1144000 | 8053.8445 | 130042.4011 | 18.45 | 91.63%
[5 empty] | 18.46 | 1144000 | 660 | 100% | 100% | 83.97% | 0.87741 | 54600 | 243540 | 845860 | 1144000 | 8065.653 | 130233.0678 | 18.46 | 91.63%
[5 empty] | 18.47 | 1144000 | 660 | 100% | 100% | 84.08% | 0.87826 | 54600 | 243540 | 845860 | 1144000 | 8077.4614 | 130423.7345 | 18.47 | 91.63%
[5 empty] | 18.48 | 1144000 | 660 | 100% | 100% | 84.19% | 0.87911 | 54600 | 243540 | 845860 | 1144000 | 8089.2699 | 130614.4011 | 18.48 | 91.63%
[5 empty] | 18.49 | 1144000 | 660 | 100% | 100% | 84.3% | 0.87996 | 54600 | 243540 | 845860 | 1144000 | 8101.0783 | 130805.0678 | 18.49 | 91.63%
[5 empty] | 18.5 | 1144000 | 660 | 100% | 100% | 84.42% | 0.88081 | 54600 | 243540 | 845860 | 1144000 | 8112.8868 | 130995.7345 | 18.5 | 91.63%
[5 empty] | 18.51 | 1144000 | 660 | 100% | 100% | 84.53% | 0.88166 | 54600 | 243540 | 845860 | 1144000 | 8124.6952 | 131186.4011 | 18.51 | 91.63%
[5 empty] | 18.52 | 1144000 | 660 | 100% | 100% | 84.64% | 0.88251 | 54600 | 243540 | 845860 | 1144000 | 8136.5037 | 131377.0678 | 18.52 | 91.63%
[5 empty] | 18.53 | 1144000 | 660 | 100% | 100% | 84.75% | 0.88336 | 54600 | 243540 | 845860 | 1144000 | 8148.3121 | 131567.7345 | 18.53 | 91.63%
[5 empty] | 18.54 | 1144000 | 660 | 100% | 100% | 84.86% | 0.88421 | 54600 | 243540 | 845860 | 1144000 | 8160.1206 | 131758.4011 | 18.54 | 91.63%
[5 empty] | 18.55 | 1144000 | 660 | 100% | 100% | 84.97% | 0.88506 | 54600 | 243540 | 845860 | 1144000 | 8171.9291 | 131949.0678 | 18.55 | 91.63%
[5 empty] | 18.56 | 1144000 | 660 | 100% | 100% | 85.08% | 0.88591 | 54600 | 243540 | 845860 | 1144000 | 8183.7375 | 132139.7345 | 18.56 | 91.63%
[5 empty] | 18.57 | 1144000 | 660 | 100% | 100% | 85.19% | 0.88676 | 54600 | 243540 | 845860 | 1144000 | 8195.546 | 132330.4011 | 18.57 | 91.63%
[5 empty] | 18.58 | 1144000 | 660 | 100% | 100% | 85.3% | 0.88761 | 54600 | 243540 | 845860 | 1144000 | 8207.3544 | 132521.0678 | 18.58 | 91.63%
[5 empty] | 18.59 | 1144000 | 660 | 100% | 100% | 85.42% | 0.88846 | 54600 | 243540 | 845860 | 1144000 | 8219.1629 | 132711.7345 | 18.59 | 91.63%
[5 empty] | 18.6 | 1144000 | 660 | 100% | 100% | 85.53% | 0.88931 | 54600 | 243540 | 845860 | 1144000 | 8230.9713 | 132902.4011 | 18.6 | 91.63%
[5 empty] | 18.61 | 1144000 | 660 | 100% | 100% | 85.64% | 0.89016 | 54600 | 243540 | 845860 | 1144000 | 8242.7798 | 133093.0678 | 18.61 | 91.63%
[5 empty] | 18.62 | 1144000 | 660 | 100% | 100% | 85.75% | 0.89101 | 54600 | 243540 | 845860 | 1144000 | 8254.5882 | 133283.7345 | 18.62 | 91.63%
[5 empty] | 18.63 | 1144000 | 660 | 100% | 100% | 85.86% | 0.89186 | 54600 | 243540 | 845860 | 1144000 | 8266.3967 | 133474.4011 | 18.63 | 91.63%
[5 empty] | 18.64 | 1144000 | 660 | 100% | 100% | 85.97% | 0.8927 | 54600 | 243540 | 845860 | 1144000 | 8278.2051 | 133665.0678 | 18.64 | 91.63%
[5 empty] | 18.65 | 1144000 | 660 | 100% | 100% | 86.08% | 0.89355 | 54600 | 243540 | 845860 | 1144000 | 8290.0136 | 133855.7345 | 18.65 | 91.63%
[5 empty] | 18.66 | 1144000 | 660 | 100% | 100% | 86.19% | 0.8944 | 54600 | 243540 | 845860 | 1144000 | 8301.822 | 134046.4011 | 18.66 | 91.63%
[5 empty] | 18.67 | 1144000 | 660 | 100% | 100% | 86.3% | 0.89525 | 54600 | 243540 | 845860 | 1144000 | 8313.6305 | 134237.0678 | 18.67 | 91.63%
[5 empty] | 18.68 | 1144000 | 660 | 100% | 100% | 86.42% | 0.8961 | 54600 | 243540 | 845860 | 1144000 | 8325.439 | 134427.7345 | 18.68 | 91.63%
[5 empty] | 18.69 | 1144000 | 660 | 100% | 100% | 86.53% | 0.89695 | 54600 | 243540 | 845860 | 1144000 | 8337.2474 | 134618.4011 | 18.69 | 91.63%
[5 empty] | 18.7 | 1144000 | 660 | 100% | 100% | 86.64% | 0.8978 | 54600 | 243540 | 845860 | 1144000 | 8349.0559 | 134809.0678 | 18.7 | 91.63%
[5 empty] | 18.71 | 1144000 | 660 | 100% | 100% | 86.75% | 0.89865 | 54600 | 243540 | 845860 | 1144000 | 8360.8643 | 134999.7345 | 18.71 | 91.63%
[5 empty] | 18.72 | 1144000 | 660 | 100% | 100% | 86.86% | 0.8995 | 54600 | 243540 | 845860 | 1144000 | 8372.6728 | 135190.4011 | 18.72 | 91.63%
[5 empty] | 18.73 | 1144000 | 660 | 100% | 100% | 86.97% | 0.90035 | 54600 | 243540 | 845860 | 1144000 | 8384.4812 | 135381.0678 | 18.73 | 91.63%
[5 empty] | 18.74 | 1144000 | 660 | 100% | 100% | 87.08% | 0.9012 | 54600 | 243540 | 845860 | 1144000 | 8396.2897 | 135571.7345 | 18.74 | 91.63%
[5 empty] | 18.75 | 1144000 | 660 | 100% | 100% | 87.19% | 0.90205 | 54600 | 243540 | 845860 | 1144000 | 8408.0981 | 135762.4011 | 18.75 | 91.63%
[5 empty] | 18.76 | 1144000 | 660 | 100% | 100% | 87.3% | 0.9029 | 54600 | 243540 | 845860 | 1144000 | 8419.9066 | 135953.0678 | 18.76 | 91.63%
[5 empty] | 18.77 | 1144000 | 660 | 100% | 100% | 87.42% | 0.90375 | 54600 | 243540 | 845860 | 1144000 | 8431.715 | 136143.7345 | 18.77 | 91.63%
[5 empty] | 18.78 | 1144000 | 660 | 100% | 100% | 87.53% | 0.9046 | 54600 | 243540 | 845860 | 1144000 | 8443.5235 | 136334.4011 | 18.78 | 91.63%
[5 empty] | 18.79 | 1144000 | 660 | 100% | 100% | 87.64% | 0.90545 | 54600 | 243540 | 845860 | 1144000 | 8455.3319 | 136525.0678 | 18.79 | 91.63%
[5 empty] | 18.8 | 1144000 | 660 | 100% | 100% | 87.75% | 0.9063 | 54600 | 243540 | 845860 | 1144000 | 8467.1404 | 136715.7345 | 18.8 | 91.63%
[5 empty] | 18.81 | 1144000 | 660 | 100% | 100% | 87.86% | 0.90715 | 54600 | 243540 | 845860 | 1144000 | 8478.9489 | 136906.4011 | 18.81 | 91.63%
[5 empty] | 18.82 | 1144000 | 660 | 100% | 100% | 87.97% | 0.908 | 54600 | 243540 | 845860 | 1144000 | 8490.7573 | 137097.0678 | 18.82 | 91.63%
[5 empty] | 18.83 | 1144000 | 660 | 100% | 100% | 88.08% | 0.90885 | 54600 | 243540 | 845860 | 1144000 | 8502.5658 | 137287.7345 | 18.83 | 91.63%
[5 empty] | 18.84 | 1144000 | 660 | 100% | 100% | 88.19% | 0.9097 | 54600 | 243540 | 845860 | 1144000 | 8514.3742 | 137478.4011 | 18.84 | 91.63%
[5 empty] | 18.85 | 1144000 | 660 | 100% | 100% | 88.3% | 0.91055 | 54600 | 243540 | 845860 | 1144000 | 8526.1827 | 137669.0678 | 18.85 | 91.63%
[5 empty] | 18.86 | 1144000 | 660 | 100% | 100% | 88.42% | 0.9114 | 54600 | 243540 | 845860 | 1144000 | 8537.9911 | 137859.7345 | 18.86 | 91.63%
[5 empty] | 18.87 | 1144000 | 660 | 100% | 100% | 88.53% | 0.91225 | 54600 | 243540 | 845860 | 1144000 | 8549.7996 | 138050.4011 | 18.87 | 91.63%
[5 empty] | 18.88 | 1144000 | 660 | 100% | 100% | 88.64% | 0.9131 | 54600 | 243540 | 845860 | 1144000 | 8561.608 | 138241.0678 | 18.88 | 91.63%
[5 empty] | 18.89 | 1144000 | 660 | 100% | 100% | 88.75% | 0.91395 | 54600 | 243540 | 845860 | 1144000 | 8573.4165 | 138431.7345 | 18.89 | 91.63%
[5 empty] | 18.9 | 1144000 | 660 | 100% | 100% | 88.86% | 0.9148 | 54600 | 243540 | 845860 | 1144000 | 8585.2249 | 138622.4011 | 18.9 | 91.63%
[5 empty] | 18.91 | 1144000 | 660 | 100% | 100% | 88.97% | 0.91565 | 54600 | 243540 | 845860 | 1144000 | 8597.0334 | 138813.0678 | 18.91 | 91.63%
[5 empty] | 18.92 | 1144000 | 660 | 100% | 100% | 89.08% | 0.9165 | 54600 | 243540 | 845860 | 1144000 | 8608.8418 | 139003.7345 | 18.92 | 91.63%
[5 empty] | 18.93 | 1144000 | 660 | 100% | 100% | 89.19% | 0.91735 | 54600 | 243540 | 845860 | 1144000 | 8620.6503 | 139194.4011 | 18.93 | 91.63%
[5 empty] | 18.94 | 1144000 | 660 | 100% | 100% | 89.3% | 0.9182 | 54600 | 243540 | 845860 | 1144000 | 8632.4588 | 139385.0678 | 18.94 | 91.63%
[5 empty] | 18.95 | 1144000 | 660 | 100% | 100% | 89.42% | 0.91905 | 54600 | 243540 | 845860 | 1144000 | 8644.2672 | 139575.7345 | 18.95 | 91.63%
[5 empty] | 18.96 | 1144000 | 660 | 100% | 100% | 89.53% | 0.9199 | 54600 | 243540 | 845860 | 1144000 | 8656.0757 | 139766.4011 | 18.96 | 91.63%
[5 empty] | 18.97 | 1144000 | 660 | 100% | 100% | 89.64% | 0.92075 | 54600 | 243540 | 845860 | 1144000 | 8667.8841 | 139957.0678 | 18.97 | 91.63%
[5 empty] | 18.98 | 1144000 | 660 | 100% | 100% | 89.75% | 0.9216 | 54600 | 243540 | 845860 | 1144000 | 8679.6926 | 140147.7345 | 18.98 | 91.63%
[5 empty] | 18.99 | 1144000 | 660 | 100% | 100% | 89.86% | 0.92245 | 54600 | 243540 | 845860 | 1144000 | 8691.501 | 140338.4011 | 18.99 | 91.63%
[5 empty] | 19 | 1144000 | 660 | 100% | 100% | 89.97% | 0.9233 | 54600 | 243540 | 845860 | 1144000 | 8703.3095 | 140529.0678 | 19 | 91.63%
[5 empty] | 19.01 | 1144000 | 660 | 100% | 100% | 90.08% | 0.92415 | 54600 | 243540 | 845860 | 1144000 | 8715.1179 | 140719.7345 | 19.01 | 91.63%
[5 empty] | 19.02 | 1144000 | 660 | 100% | 100% | 90.19% | 0.925 | 54600 | 243540 | 845860 | 1144000 | 8726.9264 | 140910.4011 | 19.02 | 91.63%
[5 empty] | 19.03 | 1144000 | 660 | 100% | 100% | 90.3% | 0.92585 | 54600 | 243540 | 845860 | 1144000 | 8738.7348 | 141101.0678 | 19.03 | 91.63%
[5 empty] | 19.04 | 1144000 | 660 | 100% | 100% | 90.42% | 0.9267 | 54600 | 243540 | 845860 | 1144000 | 8750.5433 | 141291.7345 | 19.04 | 91.63%
[5 empty] | 19.05 | 1144000 | 660 | 100% | 100% | 90.53% | 0.92755 | 54600 | 243540 | 845860 | 1144000 | 8762.3517 | 141482.4011 | 19.05 | 91.63%
[5 empty] | 19.06 | 1144000 | 660 | 100% | 100% | 90.64% | 0.9284 | 54600 | 243540 | 845860 | 1144000 | 8774.1602 | 141673.0678 | 19.06 | 91.63%
[5 empty] | 19.07 | 1144000 | 660 | 100% | 100% | 90.75% | 0.92925 | 54600 | 243540 | 845860 | 1144000 | 8785.9687 | 141863.7345 | 19.07 | 91.63%
[5 empty] | 19.08 | 1144000 | 660 | 100% | 100% | 90.86% | 0.9301 | 54600 | 243540 | 845860 | 1144000 | 8797.7771 | 142054.4011 | 19.08 | 91.63%
[5 empty] | 19.09 | 1144000 | 660 | 100% | 100% | 90.97% | 0.93095 | 54600 | 243540 | 845860 | 1144000 | 8809.5856 | 142245.0678 | 19.09 | 91.63%
[5 empty] | 19.1 | 1144000 | 660 | 100% | 100% | 91.08% | 0.9318 | 54600 | 243540 | 845860 | 1144000 | 8821.394 | 142435.7345 | 19.1 | 91.63%
[5 empty] | 19.11 | 1144000 | 660 | 100% | 100% | 91.19% | 0.93265 | 54600 | 243540 | 845860 | 1144000 | 8833.2025 | 142626.4011 | 19.11 | 91.63%
[5 empty] | 19.12 | 1144000 | 660 | 100% | 100% | 91.3% | 0.9335 | 54600 | 243540 | 845860 | 1144000 | 8845.0109 | 142817.0678 | 19.12 | 91.63%
[5 empty] | 19.13 | 1144000 | 660 | 100% | 100% | 91.42% | 0.93435 | 54600 | 243540 | 845860 | 1144000 | 8856.8194 | 143007.7345 | 19.13 | 91.63%
[5 empty] | 19.14 | 1144000 | 660 | 100% | 100% | 91.53% | 0.9352 | 54600 | 243540 | 845860 | 1144000 | 8868.6278 | 143198.4011 | 19.14 | 91.63%
[5 empty] | 19.15 | 1144000 | 660 | 100% | 100% | 91.64% | 0.93605 | 54600 | 243540 | 845860 | 1144000 | 8880.4363 | 143389.0678 | 19.15 | 91.63%
[5 empty] | 19.16 | 1144000 | 660 | 100% | 100% | 91.75% | 0.9369 | 54600 | 243540 | 845860 | 1144000 | 8892.2447 | 143579.7345 | 19.16 | 91.63%
[5 empty] | 19.17 | 1144000 | 660 | 100% | 100% | 91.86% | 0.93774 | 54600 | 243540 | 845860 | 1144000 | 8904.0532 | 143770.4011 | 19.17 | 91.63%
[5 empty] | 19.18 | 1144000 | 660 | 100% | 100% | 91.97% | 0.93859 | 54600 | 243540 | 845860 | 1144000 | 8915.8616 | 143961.0678 | 19.18 | 91.63%
[5 empty] | 19.19 | 1144000 | 660 | 100% | 100% | 92.08% | 0.93944 | 54600 | 243540 | 845860 | 1144000 | 8927.6701 | 144151.7345 | 19.19 | 91.63%
[5 empty] | 19.2 | 1144000 | 660 | 100% | 100% | 92.19% | 0.94029 | 54600 | 243540 | 845860 | 1144000 | 8939.4786 | 144342.4011 | 19.2 | 91.63%
[5 empty] | 19.21 | 1144000 | 660 | 100% | 100% | 92.3% | 0.94114 | 54600 | 243540 | 845860 | 1144000 | 8951.287 | 144533.0678 | 19.21 | 91.63%
[5 empty] | 19.22 | 1144000 | 660 | 100% | 100% | 92.42% | 0.94199 | 54600 | 243540 | 845860 | 1144000 | 8963.0955 | 144723.7345 | 19.22 | 91.63%
[5 empty] | 19.23 | 1144000 | 660 | 100% | 100% | 92.53% | 0.94284 | 54600 | 243540 | 845860 | 1144000 | 8974.9039 | 144914.4011 | 19.23 | 91.63%
[5 empty] | 19.24 | 1144000 | 660 | 100% | 100% | 92.64% | 0.94369 | 54600 | 243540 | 845860 | 1144000 | 8986.7124 | 145105.0678 | 19.24 | 91.63%
[5 empty] | 19.25 | 1144000 | 660 | 100% | 100% | 92.75% | 0.94454 | 54600 | 243540 | 845860 | 1144000 | 8998.5208 | 145295.7345 | 19.25 | 91.63%
[5 empty] | 19.26 | 1144000 | 660 | 100% | 100% | 92.86% | 0.94539 | 54600 | 243540 | 845860 | 1144000 | 9010.3293 | 145486.4011 | 19.26 | 91.63%
[5 empty] | 19.27 | 1144000 | 660 | 100% | 100% | 92.97% | 0.94624 | 54600 | 243540 | 845860 | 1144000 | 9022.1377 | 145677.0678 | 19.27 | 91.63%
[5 empty] | 19.28 | 1144000 | 660 | 100% | 100% | 93.08% | 0.94709 | 54600 | 243540 | 845860 | 1144000 | 9033.9462 | 145867.7345 | 19.28 | 91.63%
[5 empty] | 19.29 | 1144000 | 660 | 100% | 100% | 93.19% | 0.94794 | 54600 | 243540 | 845860 | 1144000 | 9045.7546 | 146058.4011 | 19.29 | 91.63%
[5 empty] | 19.3 | 1144000 | 660 | 100% | 100% | 93.3% | 0.94879 | 54600 | 243540 | 845860 | 1144000 | 9057.5631 | 146249.0678 | 19.3 | 91.63%
[5 empty] | 19.31 | 1144000 | 660 | 100% | 100% | 93.42% | 0.94964 | 54600 | 243540 | 845860 | 1144000 | 9069.3715 | 146439.7345 | 19.31 | 91.63%
[5 empty] | 19.32 | 1144000 | 660 | 100% | 100% | 93.53% | 0.95049 | 54600 | 243540 | 845860 | 1144000 | 9081.18 | 146630.4011 | 19.32 | 91.63%
[5 empty] | 19.33 | 1144000 | 660 | 100% | 100% | 93.64% | 0.95134 | 54600 | 243540 | 845860 | 1144000 | 9092.9885 | 146821.0678 | 19.33 | 91.63%
[5 empty] | 19.34 | 1144000 | 660 | 100% | 100% | 93.75% | 0.95219 | 54600 | 243540 | 845860 | 1144000 | 9104.7969 | 147011.7345 | 19.34 | 91.63%
[5 empty] | 19.35 | 1144000 | 660 | 100% | 100% | 93.86% | 0.95304 | 54600 | 243540 | 845860 | 1144000 | 9116.6054 | 147202.4011 | 19.35 | 91.63%
[5 empty] | 19.36 | 1144000 | 660 | 100% | 100% | 93.97% | 0.95389 | 54600 | 243540 | 845860 | 1144000 | 9128.4138 | 147393.0678 | 19.36 | 91.63%
[5 empty] | 19.37 | 1144000 | 660 | 100% | 100% | 94.08% | 0.95474 | 54600 | 243540 | 845860 | 1144000 | 9140.2223 | 147583.7345 | 19.37 | 91.63%
[5 empty] | 19.38 | 1144000 | 660 | 100% | 100% | 94.19% | 0.95559 | 54600 | 243540 | 845860 | 1144000 | 9152.0307 | 147774.4011 | 19.38 | 91.63%
[5 empty] | 19.39 | 1144000 | 660 | 100% | 100% | 94.3% | 0.95644 | 54600 | 243540 | 845860 | 1144000 | 9163.8392 | 147965.0678 | 19.39 | 91.63%
[5 empty] | 19.4 | 1144000 | 660 | 100% | 100% | 94.42% | 0.95729 | 54600 | 243540 | 845860 | 1144000 | 9175.6476 | 148155.7345 | 19.4 | 91.63%
[5 empty] | 19.41 | 1144000 | 660 | 100% | 100% | 94.53% | 0.95814 | 54600 | 243540 | 845860 | 1144000 | 9187.4561 | 148346.4011 | 19.41 | 91.63%
[5 empty] | 19.42 | 1144000 | 660 | 100% | 100% | 94.64% | 0.95899 | 54600 | 243540 | 845860 | 1144000 | 9199.2645 | 148537.0678 | 19.42 | 91.63%
[5 empty] | 19.43 | 1144000 | 660 | 100% | 100% | 94.75% | 0.95984 | 54600 | 243540 | 845860 | 1144000 | 9211.073 | 148727.7345 | 19.43 | 91.63%
[5 empty] | 19.44 | 1144000 | 660 | 100% | 100% | 94.86% | 0.96069 | 54600 | 243540 | 845860 | 1144000 | 9222.8814 | 148918.4011 | 19.44 | 91.63%
[5 empty] | 19.45 | 1144000 | 660 | 100% | 100% | 94.97% | 0.96154 | 54600 | 243540 | 845860 | 1144000 | 9234.6899 | 149109.0678 | 19.45 | 91.63%
[5 empty] | 19.46 | 1144000 | 660 | 100% | 100% | 95.08% | 0.96239 | 54600 | 243540 | 845860 | 1144000 | 9246.4984 | 149299.7345 | 19.46 | 91.63%
[5 empty] | 19.47 | 1144000 | 660 | 100% | 100% | 95.19% | 0.96324 | 54600 | 243540 | 845860 | 1144000 | 9258.3068 | 149490.4011 | 19.47 | 91.63%
[5 empty] | 19.48 | 1144000 | 660 | 100% | 100% | 95.3% | 0.96409 | 54600 | 243540 | 845860 | 1144000 | 9270.1153 | 149681.0678 | 19.48 | 91.63%
[5 empty] | 19.49 | 1144000 | 660 | 100% | 100% | 95.42% | 0.96494 | 54600 | 243540 | 845860 | 1144000 | 9281.9237 | 149871.7345 | 19.49 | 91.63%
[5 empty] | 19.5 | 1144000 | 660 | 100% | 100% | 95.53% | 0.96579 | 54600 | 243540 | 845860 | 1144000 | 9293.7322 | 150062.4011 | 19.5 | 91.63%
[5 empty] | 19.51 | 1144000 | 660 | 100% | 100% | 95.64% | 0.96664 | 54600 | 243540 | 845860 | 1144000 | 9305.5406 | 150253.0678 | 19.51 | 91.63%
[5 empty] | 19.52 | 1144000 | 660 | 100% | 100% | 95.75% | 0.96749 | 54600 | 243540 | 845860 | 1144000 | 9317.3491 | 150443.7345 | 19.52 | 91.63%
[5 empty] | 19.53 | 1144000 | 660 | 100% | 100% | 95.86% | 0.96834 | 54600 | 243540 | 845860 | 1144000 | 9329.1575 | 150634.4011 | 19.53 | 91.63%
[5 empty] | 19.54 | 1144000 | 660 | 100% | 100% | 95.97% | 0.96919 | 54600 | 243540 | 845860 | 1144000 | 9340.966 | 150825.0678 | 19.54 | 91.63%
[5 empty] | 19.55 | 1144000 | 660 | 100% | 100% | 96.08% | 0.97004 | 54600 | 243540 | 845860 | 1144000 | 9352.7744 | 151015.7345 | 19.55 | 91.63%
[5 empty] | 19.56 | 1144000 | 660 | 100% | 100% | 96.19% | 0.97089 | 54600 | 243540 | 845860 | 1144000 | 9364.5829 | 151206.4011 | 19.56 | 91.63%
[5 empty] | 19.57 | 1144000 | 660 | 100% | 100% | 96.3% | 0.97174 | 54600 | 243540 | 845860 | 1144000 | 9376.3913 | 151397.0678 | 19.57 | 91.63%
[5 empty] | 19.58 | 1144000 | 660 | 100% | 100% | 96.42% | 0.97259 | 54600 | 243540 | 845860 | 1144000 | 9388.1998 | 151587.7345 | 19.58 | 91.63%
[5 empty] | 19.59 | 1144000 | 660 | 100% | 100% | 96.53% | 0.97344 | 54600 | 243540 | 845860 | 1144000 | 9400.0083 | 151778.4011 | 19.59 | 91.63%
[5 empty] | 19.6 | 1144000 | 660 | 100% | 100% | 96.64% | 0.97429 | 54600 | 243540 | 845860 | 1144000 | 9411.8167 | 151969.0678 | 19.6 | 91.63%
[5 empty] | 19.61 | 1144000 | 660 | 100% | 100% | 96.75% | 0.97514 | 54600 | 243540 | 845860 | 1144000 | 9423.6252 | 152159.7345 | 19.61 | 91.63%
[5 empty] | 19.62 | 1144000 | 660 | 100% | 100% | 96.86% | 0.97599 | 54600 | 243540 | 845860 | 1144000 | 9435.4336 | 152350.4011 | 19.62 | 91.63%
[5 empty] | 19.63 | 1144000 | 660 | 100% | 100% | 96.97% | 0.97684 | 54600 | 243540 | 845860 | 1144000 | 9447.2421 | 152541.0678 | 19.63 | 91.63%
[5 empty] | 19.64 | 1144000 | 660 | 100% | 100% | 97.08% | 0.97769 | 54600 | 243540 | 845860 | 1144000 | 9459.0505 | 152731.7345 | 19.64 | 91.63%
[5 empty] | 19.65 | 1144000 | 660 | 100% | 100% | 97.19% | 0.97854 | 54600 | 243540 | 845860 | 1144000 | 9470.859 | 152922.4011 | 19.65 | 91.63%
[5 empty] | 19.66 | 1144000 | 660 | 100% | 100% | 97.3% | 0.97939 | 54600 | 243540 | 845860 | 1144000 | 9482.6674 | 153113.0678 | 19.66 | 91.63%
[5 empty] | 19.67 | 1144000 | 660 | 100% | 100% | 97.42% | 0.98024 | 54600 | 243540 | 845860 | 1144000 | 9494.4759 | 153303.7345 | 19.67 | 91.63%
[5 empty] | 19.68 | 1144000 | 660 | 100% | 100% | 97.53% | 0.98109 | 54600 | 243540 | 845860 | 1144000 | 9506.2843 | 153494.4011 | 19.68 | 91.63%
[5 empty] | 19.69 | 1144000 | 660 | 100% | 100% | 97.64% | 0.98193 | 54600 | 243540 | 845860 | 1144000 | 9518.0928 | 153685.0678 | 19.69 | 91.63%
[5 empty] | 19.7 | 1144000 | 660 | 100% | 100% | 97.75% | 0.98278 | 54600 | 243540 | 845860 | 1144000 | 9529.9012 | 153875.7345 | 19.7 | 91.63%
[5 empty] | 19.71 | 1144000 | 660 | 100% | 100% | 97.86% | 0.98363 | 54600 | 243540 | 845860 | 1144000 | 9541.7097 | 154066.4011 | 19.71 | 91.63%
[5 empty] | 19.72 | 1144000 | 660 | 100% | 100% | 97.97% | 0.98448 | 54600 | 243540 | 845860 | 1144000 | 9553.5182 | 154257.0678 | 19.72 | 91.63%
[5 empty] | 19.73 | 1144000 | 660 | 100% | 100% | 98.08% | 0.98533 | 54600 | 243540 | 845860 | 1144000 | 9565.3266 | 154447.7345 | 19.73 | 91.63%
[5 empty] | 19.74 | 1144000 | 660 | 100% | 100% | 98.19% | 0.98618 | 54600 | 243540 | 845860 | 1144000 | 9577.1351 | 154638.4011 | 19.74 | 91.63%
[5 empty] | 19.75 | 1144000 | 660 | 100% | 100% | 98.3% | 0.98703 | 54600 | 243540 | 845860 | 1144000 | 9588.9435 | 154829.0678 | 19.75 | 91.63%
[5 empty] | 19.76 | 1144000 | 660 | 100% | 100% | 98.42% | 0.98788 | 54600 | 243540 | 845860 | 1144000 | 9600.752 | 155019.7345 | 19.76 | 91.63%
[5 empty] | 19.77 | 1144000 | 660 | 100% | 100% | 98.53% | 0.98873 | 54600 | 243540 | 845860 | 1144000 | 9612.5604 | 155210.4011 | 19.77 | 91.63%
[5 empty] | 19.78 | 1144000 | 660 | 100% | 100% | 98.64% | 0.98958 | 54600 | 243540 | 845860 | 1144000 | 9624.3689 | 155401.0678 | 19.78 | 91.63%
[5 empty] | 19.79 | 1144000 | 660 | 100% | 100% | 98.75% | 0.99043 | 54600 | 243540 | 845860 | 1144000 | 9636.1773 | 155591.7345 | 19.79 | 91.63%
[5 empty] | 19.8 | 1144000 | 660 | 100% | 100% | 98.86% | 0.99128 | 54600 | 243540 | 845860 | 1144000 | 9647.9858 | 155782.4011 | 19.8 | 91.63%
[5 empty] | 19.81 | 1144000 | 660 | 100% | 100% | 98.97% | 0.99213 | 54600 | 243540 | 845860 | 1144000 | 9659.7942 | 155973.0678 | 19.81 | 91.63%
[5 empty] | 19.82 | 1144000 | 660 | 100% | 100% | 99.08% | 0.99298 | 54600 | 243540 | 845860 | 1144000 | 9671.6027 | 156163.7345 | 19.82 | 91.63%
[5 empty] | 19.83 | 1144000 | 660 | 100% | 100% | 99.19% | 0.99383 | 54600 | 243540 | 845860 | 1144000 | 9683.4111 | 156354.4011 | 19.83 | 91.63%
[5 empty] | 19.84 | 1144000 | 660 | 100% | 100% | 99.3% | 0.99468 | 54600 | 243540 | 845860 | 1144000 | 9695.2196 | 156545.0678 | 19.84 | 91.63%
[5 empty] | 19.85 | 1144000 | 660 | 100% | 100% | 99.42% | 0.99553 | 54600 | 243540 | 845860 | 1144000 | 9707.0281 | 156735.7345 | 19.85 | 91.63%
[5 empty] | 19.86 | 1144000 | 660 | 100% | 100% | 99.53% | 0.99638 | 54600 | 243540 | 845860 | 1144000 | 9718.8365 | 156926.4011 | 19.86 | 91.63%
[5 empty] | 19.87 | 1144000 | 660 | 100% | 100% | 99.64% | 0.99723 | 54600 | 243540 | 845860 | 1144000 | 9730.645 | 157117.0678 | 19.87 | 91.63%
[5 empty] | 19.88 | 1144000 | 660 | 100% | 100% | 99.75% | 0.99808 | 54600 | 243540 | 845860 | 1144000 | 9742.4534 | 157307.7345 | 19.88 | 91.63%
[5 empty] | 19.89 | 1144000 | 660 | 100% | 100% | 99.86% | 0.99893 | 54600 | 243540 | 845860 | 1144000 | 9754.2619 | 157498.4011 | 19.89 | 91.63%
[5 empty] | 19.9 | 1144000 | 660 | 100% | 100% | 99.97% | 0.99978 | 54600 | 243540 | 845860 | 1144000 | 9766.0703 | 157689.0678 | 19.9 | 91.63%
[5 empty] | 19.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9777.8788 | 157879.7345 | 19.91 | 91.63%
[5 empty] | 19.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9789.6872 | 158070.4011 | 19.92 | 91.63%
[5 empty] | 19.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9801.4957 | 158261.0678 | 19.93 | 91.63%
[5 empty] | 19.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9813.3041 | 158451.7345 | 19.94 | 91.63%
[5 empty] | 19.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9825.1126 | 158642.4011 | 19.95 | 91.63%
[5 empty] | 19.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9836.921 | 158833.0678 | 19.96 | 91.63%
[5 empty] | 19.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9848.7295 | 159023.7345 | 19.97 | 91.63%
[5 empty] | 19.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9860.5379 | 159214.4011 | 19.98 | 91.63%
[5 empty] | 19.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9872.3464 | 159405.0678 | 19.99 | 91.63%
[5 empty] | 20 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9884.1549 | 159595.7345 | 20 | 91.63%
[5 empty] | 20.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9895.9633 | 159786.4011 | 20.01 | 91.63%
[5 empty] | 20.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9907.7718 | 159977.0678 | 20.02 | 91.63%
[5 empty] | 20.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9919.5802 | 160167.7345 | 20.03 | 91.63%
[5 empty] | 20.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9931.3887 | 160358.4011 | 20.04 | 91.63%
[5 empty] | 20.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9943.1971 | 160549.0678 | 20.05 | 91.63%
[5 empty] | 20.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9955.0056 | 160739.7345 | 20.06 | 91.63%
[5 empty] | 20.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9966.814 | 160930.4011 | 20.07 | 91.63%
[5 empty] | 20.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9978.6225 | 161121.0678 | 20.08 | 91.63%
[5 empty] | 20.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 9990.4309 | 161311.7345 | 20.09 | 91.63%
[5 empty] | 20.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10002.2394 | 161502.4011 | 20.1 | 91.63%
[5 empty] | 20.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10014.0478 | 161693.0678 | 20.11 | 91.63%
[5 empty] | 20.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10025.8563 | 161883.7345 | 20.12 | 91.63%
[5 empty] | 20.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10037.6648 | 162074.4011 | 20.13 | 91.63%
[5 empty] | 20.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10049.4732 | 162265.0678 | 20.14 | 91.63%
[5 empty] | 20.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10061.2817 | 162455.7345 | 20.15 | 91.63%
[5 empty] | 20.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10073.0901 | 162646.4011 | 20.16 | 91.63%
[5 empty] | 20.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10084.8986 | 162837.0678 | 20.17 | 91.63%
[5 empty] | 20.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10096.707 | 163027.7345 | 20.18 | 91.63%
[5 empty] | 20.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10108.5155 | 163218.4011 | 20.19 | 91.63%
[5 empty] | 20.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10120.3239 | 163409.0678 | 20.2 | 91.63%
[5 empty] | 20.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10132.1324 | 163599.7345 | 20.21 | 91.63%
[5 empty] | 20.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10143.9408 | 163790.4011 | 20.22 | 91.63%
[5 empty] | 20.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10155.7493 | 163981.0678 | 20.23 | 91.63%
[5 empty] | 20.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10167.5577 | 164171.7345 | 20.24 | 91.63%
[5 empty] | 20.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10179.3662 | 164362.4011 | 20.25 | 91.63%
[5 empty] | 20.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10191.1747 | 164553.0678 | 20.26 | 91.63%
[5 empty] | 20.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10202.9831 | 164743.7345 | 20.27 | 91.63%
[5 empty] | 20.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10214.7916 | 164934.4011 | 20.28 | 91.63%
[5 empty] | 20.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10226.6 | 165125.0678 | 20.29 | 91.63%
[5 empty] | 20.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10238.4085 | 165315.7345 | 20.3 | 91.63%
[5 empty] | 20.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10250.2169 | 165506.4011 | 20.31 | 91.63%
[5 empty] | 20.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10262.0254 | 165697.0678 | 20.32 | 91.63%
[5 empty] | 20.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10273.8338 | 165887.7345 | 20.33 | 91.63%
[5 empty] | 20.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10285.6423 | 166078.4011 | 20.34 | 91.63%
[5 empty] | 20.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10297.4507 | 166269.0678 | 20.35 | 91.63%
[5 empty] | 20.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10309.2592 | 166459.7345 | 20.36 | 91.63%
[5 empty] | 20.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10321.0676 | 166650.4011 | 20.37 | 91.63%
[5 empty] | 20.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10332.8761 | 166841.0678 | 20.38 | 91.63%
[5 empty] | 20.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10344.6846 | 167031.7345 | 20.39 | 91.63%
[5 empty] | 20.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10356.493 | 167222.4011 | 20.4 | 91.63%
[5 empty] | 20.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10368.3015 | 167413.0678 | 20.41 | 91.63%
[5 empty] | 20.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10380.1099 | 167603.7345 | 20.42 | 91.63%
[5 empty] | 20.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10391.9184 | 167794.4011 | 20.43 | 91.63%
[5 empty] | 20.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10403.7268 | 167985.0678 | 20.44 | 91.63%
[5 empty] | 20.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10415.5353 | 168175.7345 | 20.45 | 91.63%
[5 empty] | 20.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10427.3437 | 168366.4011 | 20.46 | 91.63%
[5 empty] | 20.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10439.1522 | 168557.0678 | 20.47 | 91.63%
[5 empty] | 20.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10450.9606 | 168747.7345 | 20.48 | 91.63%
[5 empty] | 20.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10462.7691 | 168938.4011 | 20.49 | 91.63%
[5 empty] | 20.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10474.5775 | 169129.0678 | 20.5 | 91.63%
[5 empty] | 20.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10486.386 | 169319.7345 | 20.51 | 91.63%
[5 empty] | 20.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10498.1945 | 169510.4011 | 20.52 | 91.63%
[5 empty] | 20.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10510.0029 | 169701.0678 | 20.53 | 91.63%
[5 empty] | 20.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10521.8114 | 169891.7345 | 20.54 | 91.63%
[5 empty] | 20.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10533.6198 | 170082.4011 | 20.55 | 91.63%
[5 empty] | 20.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10545.4283 | 170273.0678 | 20.56 | 91.63%
[5 empty] | 20.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10557.2367 | 170463.7345 | 20.57 | 91.63%
[5 empty] | 20.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10569.0452 | 170654.4011 | 20.58 | 91.63%
[5 empty] | 20.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10580.8536 | 170845.0678 | 20.59 | 91.63%
[5 empty] | 20.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10592.6621 | 171035.7345 | 20.6 | 91.63%
[5 empty] | 20.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10604.4705 | 171226.4011 | 20.61 | 91.63%
[5 empty] | 20.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10616.279 | 171417.0678 | 20.62 | 91.63%
[5 empty] | 20.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10628.0874 | 171607.7345 | 20.63 | 91.63%
[5 empty] | 20.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10639.8959 | 171798.4011 | 20.64 | 91.63%
[5 empty] | 20.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10651.7044 | 171989.0678 | 20.65 | 91.63%
[5 empty] | 20.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10663.5128 | 172179.7345 | 20.66 | 91.63%
[5 empty] | 20.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10675.3213 | 172370.4011 | 20.67 | 91.63%
[5 empty] | 20.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10687.1297 | 172561.0678 | 20.68 | 91.63%
[5 empty] | 20.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10698.9382 | 172751.7345 | 20.69 | 91.63%
[5 empty] | 20.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10710.7466 | 172942.4011 | 20.7 | 91.63%
[5 empty] | 20.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10722.5551 | 173133.0678 | 20.71 | 91.63%
[5 empty] | 20.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10734.3635 | 173323.7345 | 20.72 | 91.63%
[5 empty] | 20.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10746.172 | 173514.4011 | 20.73 | 91.63%
[5 empty] | 20.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10757.9804 | 173705.0678 | 20.74 | 91.63%
[5 empty] | 20.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10769.7889 | 173895.7345 | 20.75 | 91.63%
[5 empty] | 20.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10781.5973 | 174086.4011 | 20.76 | 91.63%
[5 empty] | 20.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10793.4058 | 174277.0678 | 20.77 | 91.63%
[5 empty] | 20.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10805.2143 | 174467.7345 | 20.78 | 91.63%
[5 empty] | 20.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10817.0227 | 174658.4011 | 20.79 | 91.63%
[5 empty] | 20.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10828.8312 | 174849.0678 | 20.8 | 91.63%
[5 empty] | 20.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10840.6396 | 175039.7345 | 20.81 | 91.63%
[5 empty] | 20.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10852.4481 | 175230.4011 | 20.82 | 91.63%
[5 empty] | 20.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10864.2565 | 175421.0678 | 20.83 | 91.63%
[5 empty] | 20.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10876.065 | 175611.7345 | 20.84 | 91.63%
[5 empty] | 20.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10887.8734 | 175802.4011 | 20.85 | 91.63%
[5 empty] | 20.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10899.6819 | 175993.0678 | 20.86 | 91.63%
[5 empty] | 20.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10911.4903 | 176183.7345 | 20.87 | 91.63%
[5 empty] | 20.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10923.2988 | 176374.4011 | 20.88 | 91.63%
[5 empty] | 20.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10935.1072 | 176565.0678 | 20.89 | 91.63%
[5 empty] | 20.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10946.9157 | 176755.7345 | 20.9 | 91.63%
[5 empty] | 20.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10958.7242 | 176946.4011 | 20.91 | 91.63%
[5 empty] | 20.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10970.5326 | 177137.0678 | 20.92 | 91.63%
[5 empty] | 20.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10982.3411 | 177327.7345 | 20.93 | 91.63%
[5 empty] | 20.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 10994.1495 | 177518.4011 | 20.94 | 91.63%
[5 empty] | 20.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11005.958 | 177709.0678 | 20.95 | 91.63%
[5 empty] | 20.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11017.7664 | 177899.7345 | 20.96 | 91.63%
[5 empty] | 20.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11029.5749 | 178090.4011 | 20.97 | 91.63%
[5 empty] | 20.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11041.3833 | 178281.0678 | 20.98 | 91.63%
[5 empty] | 20.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11053.1918 | 178471.7345 | 20.99 | 91.63%
[5 empty] | 21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11065.0002 | 178662.4011 | 21 | 91.63%
[5 empty] | 21.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11076.8087 | 178853.0678 | 21.01 | 91.63%
[5 empty] | 21.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11088.6171 | 179043.7345 | 21.02 | 91.63%
[5 empty] | 21.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11100.4256 | 179234.4011 | 21.03 | 91.63%
[5 empty] | 21.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11112.2341 | 179425.0678 | 21.04 | 91.63%
[5 empty] | 21.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11124.0425 | 179615.7345 | 21.05 | 91.63%
[5 empty] | 21.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11135.851 | 179806.4011 | 21.06 | 91.63%
[5 empty] | 21.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11147.6594 | 179997.0678 | 21.07 | 91.63%
[5 empty] | 21.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11159.4679 | 180187.7345 | 21.08 | 91.63%
[5 empty] | 21.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11171.2763 | 180378.4011 | 21.09 | 91.63%
[5 empty] | 21.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11183.0848 | 180569.0678 | 21.1 | 91.63%
[5 empty] | 21.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11194.8932 | 180759.7345 | 21.11 | 91.63%
[5 empty] | 21.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11206.7017 | 180950.4011 | 21.12 | 91.63%
[5 empty] | 21.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11218.5101 | 181141.0678 | 21.13 | 91.63%
[5 empty] | 21.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11230.3186 | 181331.7345 | 21.14 | 91.63%
[5 empty] | 21.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11242.127 | 181522.4011 | 21.15 | 91.63%
[5 empty] | 21.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11253.9355 | 181713.0678 | 21.16 | 91.63%
[5 empty] | 21.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11265.744 | 181903.7345 | 21.17 | 91.63%
[5 empty] | 21.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11277.5524 | 182094.4011 | 21.18 | 91.63%
[5 empty] | 21.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11289.3609 | 182285.0678 | 21.19 | 91.63%
[5 empty] | 21.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11301.1693 | 182475.7345 | 21.2 | 91.63%
[5 empty] | 21.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11312.9778 | 182666.4011 | 21.21 | 91.63%
[5 empty] | 21.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11324.7862 | 182857.0678 | 21.22 | 91.63%
[5 empty] | 21.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11336.5947 | 183047.7345 | 21.23 | 91.63%
[5 empty] | 21.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11348.4031 | 183238.4011 | 21.24 | 91.63%
[5 empty] | 21.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11360.2116 | 183429.0678 | 21.25 | 91.63%
[5 empty] | 21.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11372.02 | 183619.7345 | 21.26 | 91.63%
[5 empty] | 21.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11383.8285 | 183810.4011 | 21.27 | 91.63%
[5 empty] | 21.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11395.6369 | 184001.0678 | 21.28 | 91.63%
[5 empty] | 21.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11407.4454 | 184191.7345 | 21.29 | 91.63%
[5 empty] | 21.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11419.2539 | 184382.4011 | 21.3 | 91.63%
[5 empty] | 21.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11431.0623 | 184573.0678 | 21.31 | 91.63%
[5 empty] | 21.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11442.8708 | 184763.7345 | 21.32 | 91.63%
[5 empty] | 21.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11454.6792 | 184954.4011 | 21.33 | 91.63%
[5 empty] | 21.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11466.4877 | 185145.0678 | 21.34 | 91.63%
[5 empty] | 21.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11478.2961 | 185335.7345 | 21.35 | 91.63%
[5 empty] | 21.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11490.1046 | 185526.4011 | 21.36 | 91.63%
[5 empty] | 21.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11501.913 | 185717.0678 | 21.37 | 91.63%
[5 empty] | 21.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11513.7215 | 185907.7345 | 21.38 | 91.63%
[5 empty] | 21.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11525.5299 | 186098.4011 | 21.39 | 91.63%
[5 empty] | 21.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11537.3384 | 186289.0678 | 21.4 | 91.63%
[5 empty] | 21.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11549.1468 | 186479.7345 | 21.41 | 91.63%
[5 empty] | 21.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11560.9553 | 186670.4011 | 21.42 | 91.63%
[5 empty] | 21.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11572.7638 | 186861.0678 | 21.43 | 91.63%
[5 empty] | 21.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11584.5722 | 187051.7345 | 21.44 | 91.63%
[5 empty] | 21.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11596.3807 | 187242.4011 | 21.45 | 91.63%
[5 empty] | 21.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11608.1891 | 187433.0678 | 21.46 | 91.63%
[5 empty] | 21.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11619.9976 | 187623.7345 | 21.47 | 91.63%
[5 empty] | 21.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11631.806 | 187814.4011 | 21.48 | 91.63%
[5 empty] | 21.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11643.6145 | 188005.0678 | 21.49 | 91.63%
[5 empty] | 21.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11655.4229 | 188195.7345 | 21.5 | 91.63%
[5 empty] | 21.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11667.2314 | 188386.4011 | 21.51 | 91.63%
[5 empty] | 21.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11679.0398 | 188577.0678 | 21.52 | 91.63%
[5 empty] | 21.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11690.8483 | 188767.7345 | 21.53 | 91.63%
[5 empty] | 21.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11702.6567 | 188958.4011 | 21.54 | 91.63%
[5 empty] | 21.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11714.4652 | 189149.0678 | 21.55 | 91.63%
[5 empty] | 21.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11726.2737 | 189339.7345 | 21.56 | 91.63%
[5 empty] | 21.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11738.0821 | 189530.4011 | 21.57 | 91.63%
[5 empty] | 21.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11749.8906 | 189721.0678 | 21.58 | 91.63%
[5 empty] | 21.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11761.699 | 189911.7345 | 21.59 | 91.63%
[5 empty] | 21.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11773.5075 | 190102.4011 | 21.6 | 91.63%
[5 empty] | 21.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11785.3159 | 190293.0678 | 21.61 | 91.63%
[5 empty] | 21.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11797.1244 | 190483.7345 | 21.62 | 91.63%
[5 empty] | 21.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11808.9328 | 190674.4011 | 21.63 | 91.63%
[5 empty] | 21.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11820.7413 | 190865.0678 | 21.64 | 91.63%
[5 empty] | 21.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11832.5497 | 191055.7345 | 21.65 | 91.63%
[5 empty] | 21.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11844.3582 | 191246.4011 | 21.66 | 91.63%
[5 empty] | 21.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11856.1666 | 191437.0678 | 21.67 | 91.63%
[5 empty] | 21.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11867.9751 | 191627.7345 | 21.68 | 91.63%
[5 empty] | 21.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11879.7836 | 191818.4011 | 21.69 | 91.63%
[5 empty] | 21.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11891.592 | 192009.0678 | 21.7 | 91.63%
[5 empty] | 21.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11903.4005 | 192199.7345 | 21.71 | 91.63%
[5 empty] | 21.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11915.2089 | 192390.4011 | 21.72 | 91.63%
[5 empty] | 21.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11927.0174 | 192581.0678 | 21.73 | 91.63%
[5 empty] | 21.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11938.8258 | 192771.7345 | 21.74 | 91.63%
[5 empty] | 21.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11950.6343 | 192962.4011 | 21.75 | 91.63%
[5 empty] | 21.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11962.4427 | 193153.0678 | 21.76 | 91.63%
[5 empty] | 21.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11974.2512 | 193343.7345 | 21.77 | 91.63%
[5 empty] | 21.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11986.0596 | 193534.4011 | 21.78 | 91.63%
[5 empty] | 21.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 11997.8681 | 193725.0678 | 21.79 | 91.63%
[5 empty] | 21.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12009.6765 | 193915.7345 | 21.8 | 91.63%
[5 empty] | 21.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12021.485 | 194106.4011 | 21.81 | 91.63%
[5 empty] | 21.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12033.2935 | 194297.0678 | 21.82 | 91.63%
[5 empty] | 21.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12045.1019 | 194487.7345 | 21.83 | 91.63%
[5 empty] | 21.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12056.9104 | 194678.4011 | 21.84 | 91.63%
[5 empty] | 21.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12068.7188 | 194869.0678 | 21.85 | 91.63%
[5 empty] | 21.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12080.5273 | 195059.7345 | 21.86 | 91.63%
[5 empty] | 21.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12092.3357 | 195250.4011 | 21.87 | 91.63%
[5 empty] | 21.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12104.1442 | 195441.0678 | 21.88 | 91.63%
[5 empty] | 21.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12115.9526 | 195631.7345 | 21.89 | 91.63%
[5 empty] | 21.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12127.7611 | 195822.4011 | 21.9 | 91.63%
[5 empty] | 21.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12139.5695 | 196013.0678 | 21.91 | 91.63%
[5 empty] | 21.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12151.378 | 196203.7345 | 21.92 | 91.63%
[5 empty] | 21.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12163.1864 | 196394.4011 | 21.93 | 91.63%
[5 empty] | 21.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12174.9949 | 196585.0678 | 21.94 | 91.63%
[5 empty] | 21.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12186.8034 | 196775.7345 | 21.95 | 91.63%
[5 empty] | 21.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12198.6118 | 196966.4011 | 21.96 | 91.63%
[5 empty] | 21.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12210.4203 | 197157.0678 | 21.97 | 91.63%
[5 empty] | 21.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12222.2287 | 197347.7345 | 21.98 | 91.63%
[5 empty] | 21.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12234.0372 | 197538.4011 | 21.99 | 91.63%
[5 empty] | 22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12245.8456 | 197729.0678 | 22 | 91.63%
[5 empty] | 22.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12257.6541 | 197919.7345 | 22.01 | 91.63%
[5 empty] | 22.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12269.4625 | 198110.4011 | 22.02 | 91.63%
[5 empty] | 22.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12281.271 | 198301.0678 | 22.03 | 91.63%
[5 empty] | 22.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12293.0794 | 198491.7345 | 22.04 | 91.63%
[5 empty] | 22.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12304.8879 | 198682.4011 | 22.05 | 91.63%
[5 empty] | 22.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12316.6963 | 198873.0678 | 22.06 | 91.63%
[5 empty] | 22.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12328.5048 | 199063.7345 | 22.07 | 91.63%
[5 empty] | 22.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12340.3133 | 199254.4011 | 22.08 | 91.63%
[5 empty] | 22.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12352.1217 | 199445.0678 | 22.09 | 91.63%
[5 empty] | 22.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12363.9302 | 199635.7345 | 22.1 | 91.63%
[5 empty] | 22.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12375.7386 | 199826.4011 | 22.11 | 91.63%
[5 empty] | 22.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12387.5471 | 200017.0678 | 22.12 | 91.63%
[5 empty] | 22.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12399.3555 | 200207.7345 | 22.13 | 91.63%
[5 empty] | 22.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12411.164 | 200398.4011 | 22.14 | 91.63%
[5 empty] | 22.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12422.9724 | 200589.0678 | 22.15 | 91.63%
[5 empty] | 22.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12434.7809 | 200779.7345 | 22.16 | 91.63%
[5 empty] | 22.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12446.5893 | 200970.4011 | 22.17 | 91.63%
[5 empty] | 22.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12458.3978 | 201161.0678 | 22.18 | 91.63%
[5 empty] | 22.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12470.2062 | 201351.7345 | 22.19 | 91.63%
[5 empty] | 22.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12482.0147 | 201542.4011 | 22.2 | 91.63%
[5 empty] | 22.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12493.8232 | 201733.0678 | 22.21 | 91.63%
[5 empty] | 22.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12505.6316 | 201923.7345 | 22.22 | 91.63%
[5 empty] | 22.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12517.4401 | 202114.4011 | 22.23 | 91.63%
[5 empty] | 22.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12529.2485 | 202305.0678 | 22.24 | 91.63%
[5 empty] | 22.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12541.057 | 202495.7345 | 22.25 | 91.63%
[5 empty] | 22.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12552.8654 | 202686.4011 | 22.26 | 91.63%
[5 empty] | 22.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12564.6739 | 202877.0678 | 22.27 | 91.63%
[5 empty] | 22.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12576.4823 | 203067.7345 | 22.28 | 91.63%
[5 empty] | 22.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12588.2908 | 203258.4011 | 22.29 | 91.63%
[5 empty] | 22.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12600.0992 | 203449.0678 | 22.3 | 91.63%
[5 empty] | 22.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12611.9077 | 203639.7345 | 22.31 | 91.63%
[5 empty] | 22.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12623.7161 | 203830.4011 | 22.32 | 91.63%
[5 empty] | 22.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12635.5246 | 204021.0678 | 22.33 | 91.63%
[5 empty] | 22.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12647.3331 | 204211.7345 | 22.34 | 91.63%
[5 empty] | 22.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12659.1415 | 204402.4011 | 22.35 | 91.63%
[5 empty] | 22.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12670.95 | 204593.0678 | 22.36 | 91.63%
[5 empty] | 22.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12682.7584 | 204783.7345 | 22.37 | 91.63%
[5 empty] | 22.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12694.5669 | 204974.4011 | 22.38 | 91.63%
[5 empty] | 22.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12706.3753 | 205165.0678 | 22.39 | 91.63%
[5 empty] | 22.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12718.1838 | 205355.7345 | 22.4 | 91.63%
[5 empty] | 22.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12729.9922 | 205546.4011 | 22.41 | 91.63%
[5 empty] | 22.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12741.8007 | 205737.0678 | 22.42 | 91.63%
[5 empty] | 22.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12753.6091 | 205927.7345 | 22.43 | 91.63%
[5 empty] | 22.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12765.4176 | 206118.4011 | 22.44 | 91.63%
[5 empty] | 22.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12777.226 | 206309.0678 | 22.45 | 91.63%
[5 empty] | 22.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12789.0345 | 206499.7345 | 22.46 | 91.63%
[5 empty] | 22.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12800.8429 | 206690.4011 | 22.47 | 91.63%
[5 empty] | 22.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12812.6514 | 206881.0678 | 22.48 | 91.63%
[5 empty] | 22.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12824.4599 | 207071.7345 | 22.49 | 91.63%
[5 empty] | 22.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12836.2683 | 207262.4011 | 22.5 | 91.63%
[5 empty] | 22.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12848.0768 | 207453.0678 | 22.51 | 91.63%
[5 empty] | 22.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12859.8852 | 207643.7345 | 22.52 | 91.63%
[5 empty] | 22.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12871.6937 | 207834.4011 | 22.53 | 91.63%
[5 empty] | 22.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12883.5021 | 208025.0678 | 22.54 | 91.63%
[5 empty] | 22.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12895.3106 | 208215.7345 | 22.55 | 91.63%
[5 empty] | 22.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12907.119 | 208406.4011 | 22.56 | 91.63%
[5 empty] | 22.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12918.9275 | 208597.0678 | 22.57 | 91.63%
[5 empty] | 22.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12930.7359 | 208787.7345 | 22.58 | 91.63%
[5 empty] | 22.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12942.5444 | 208978.4011 | 22.59 | 91.63%
[5 empty] | 22.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12954.3528 | 209169.0678 | 22.6 | 91.63%
[5 empty] | 22.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12966.1613 | 209359.7345 | 22.61 | 91.63%
[5 empty] | 22.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12977.9698 | 209550.4011 | 22.62 | 91.63%
[5 empty] | 22.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 12989.7782 | 209741.0678 | 22.63 | 91.63%
[5 empty] | 22.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13001.5867 | 209931.7345 | 22.64 | 91.63%
[5 empty] | 22.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13013.3951 | 210122.4011 | 22.65 | 91.63%
[5 empty] | 22.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13025.2036 | 210313.0678 | 22.66 | 91.63%
[5 empty] | 22.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13037.012 | 210503.7345 | 22.67 | 91.63%
[5 empty] | 22.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13048.8205 | 210694.4011 | 22.68 | 91.63%
[5 empty] | 22.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13060.6289 | 210885.0678 | 22.69 | 91.63%
[5 empty] | 22.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13072.4374 | 211075.7345 | 22.7 | 91.63%
[5 empty] | 22.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13084.2458 | 211266.4011 | 22.71 | 91.63%
[5 empty] | 22.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13096.0543 | 211457.0678 | 22.72 | 91.63%
[5 empty] | 22.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13107.8627 | 211647.7345 | 22.73 | 91.63%
[5 empty] | 22.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13119.6712 | 211838.4011 | 22.74 | 91.63%
[5 empty] | 22.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13131.4797 | 212029.0678 | 22.75 | 91.63%
[5 empty] | 22.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13143.2881 | 212219.7345 | 22.76 | 91.63%
[5 empty] | 22.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13155.0966 | 212410.4011 | 22.77 | 91.63%
[5 empty] | 22.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13166.905 | 212601.0678 | 22.78 | 91.63%
[5 empty] | 22.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13178.7135 | 212791.7345 | 22.79 | 91.63%
[5 empty] | 22.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13190.5219 | 212982.4011 | 22.8 | 91.63%
[5 empty] | 22.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13202.3304 | 213173.0678 | 22.81 | 91.63%
[5 empty] | 22.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13214.1388 | 213363.7345 | 22.82 | 91.63%
[5 empty] | 22.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13225.9473 | 213554.4011 | 22.83 | 91.63%
[5 empty] | 22.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13237.7557 | 213745.0678 | 22.84 | 91.63%
[5 empty] | 22.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13249.5642 | 213935.7345 | 22.85 | 91.63%
[5 empty] | 22.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13261.3726 | 214126.4011 | 22.86 | 91.63%
[5 empty] | 22.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13273.1811 | 214317.0678 | 22.87 | 91.63%
[5 empty] | 22.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13284.9896 | 214507.7345 | 22.88 | 91.63%
[5 empty] | 22.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13296.798 | 214698.4011 | 22.89 | 91.63%
[5 empty] | 22.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13308.6065 | 214889.0678 | 22.9 | 91.63%
[5 empty] | 22.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13320.4149 | 215079.7345 | 22.91 | 91.63%
[5 empty] | 22.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13332.2234 | 215270.4011 | 22.92 | 91.63%
[5 empty] | 22.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13344.0318 | 215461.0678 | 22.93 | 91.63%
[5 empty] | 22.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13355.8403 | 215651.7345 | 22.94 | 91.63%
[5 empty] | 22.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13367.6487 | 215842.4011 | 22.95 | 91.63%
[5 empty] | 22.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13379.4572 | 216033.0678 | 22.96 | 91.63%
[5 empty] | 22.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13391.2656 | 216223.7345 | 22.97 | 91.63%
[5 empty] | 22.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13403.0741 | 216414.4011 | 22.98 | 91.63%
[5 empty] | 22.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13414.8825 | 216605.0678 | 22.99 | 91.63%
[5 empty] | 23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13426.691 | 216795.7345 | 23 | 91.63%
[5 empty] | 23.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13438.4995 | 216986.4011 | 23.01 | 91.63%
[5 empty] | 23.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13450.3079 | 217177.0678 | 23.02 | 91.63%
[5 empty] | 23.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13462.1164 | 217367.7345 | 23.03 | 91.63%
[5 empty] | 23.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13473.9248 | 217558.4011 | 23.04 | 91.63%
[5 empty] | 23.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13485.7333 | 217749.0678 | 23.05 | 91.63%
[5 empty] | 23.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13497.5417 | 217939.7345 | 23.06 | 91.63%
[5 empty] | 23.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13509.3502 | 218130.4011 | 23.07 | 91.63%
[5 empty] | 23.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13521.1586 | 218321.0678 | 23.08 | 91.63%
[5 empty] | 23.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13532.9671 | 218511.7345 | 23.09 | 91.63%
[5 empty] | 23.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13544.7755 | 218702.4011 | 23.1 | 91.63%
[5 empty] | 23.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13556.584 | 218893.0678 | 23.11 | 91.63%
[5 empty] | 23.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13568.3924 | 219083.7345 | 23.12 | 91.63%
[5 empty] | 23.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13580.2009 | 219274.4011 | 23.13 | 91.63%
[5 empty] | 23.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13592.0094 | 219465.0678 | 23.14 | 91.63%
[5 empty] | 23.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13603.8178 | 219655.7345 | 23.15 | 91.63%
[5 empty] | 23.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13615.6263 | 219846.4011 | 23.16 | 91.63%
[5 empty] | 23.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13627.4347 | 220037.0678 | 23.17 | 91.63%
[5 empty] | 23.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13639.2432 | 220227.7345 | 23.18 | 91.63%
[5 empty] | 23.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13651.0516 | 220418.4011 | 23.19 | 91.63%
[5 empty] | 23.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13662.8601 | 220609.0678 | 23.2 | 91.63%
[5 empty] | 23.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13674.6685 | 220799.7345 | 23.21 | 91.63%
[5 empty] | 23.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13686.477 | 220990.4011 | 23.22 | 91.63%
[5 empty] | 23.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13698.2854 | 221181.0678 | 23.23 | 91.63%
[5 empty] | 23.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13710.0939 | 221371.7345 | 23.24 | 91.63%
[5 empty] | 23.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13721.9023 | 221562.4011 | 23.25 | 91.63%
[5 empty] | 23.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13733.7108 | 221753.0678 | 23.26 | 91.63%
[5 empty] | 23.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13745.5193 | 221943.7345 | 23.27 | 91.63%
[5 empty] | 23.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13757.3277 | 222134.4011 | 23.28 | 91.63%
[5 empty] | 23.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13769.1362 | 222325.0678 | 23.29 | 91.63%
[5 empty] | 23.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13780.9446 | 222515.7345 | 23.3 | 91.63%
[5 empty] | 23.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13792.7531 | 222706.4011 | 23.31 | 91.63%
[5 empty] | 23.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13804.5615 | 222897.0678 | 23.32 | 91.63%
[5 empty] | 23.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13816.37 | 223087.7345 | 23.33 | 91.63%
[5 empty] | 23.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13828.1784 | 223278.4011 | 23.34 | 91.63%
[5 empty] | 23.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13839.9869 | 223469.0678 | 23.35 | 91.63%
[5 empty] | 23.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13851.7953 | 223659.7345 | 23.36 | 91.63%
[5 empty] | 23.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13863.6038 | 223850.4011 | 23.37 | 91.63%
[5 empty] | 23.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13875.4122 | 224041.0678 | 23.38 | 91.63%
[5 empty] | 23.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13887.2207 | 224231.7345 | 23.39 | 91.63%
[5 empty] | 23.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13899.0292 | 224422.4011 | 23.4 | 91.63%
[5 empty] | 23.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13910.8376 | 224613.0678 | 23.41 | 91.63%
[5 empty] | 23.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13922.6461 | 224803.7345 | 23.42 | 91.63%
[5 empty] | 23.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13934.4545 | 224994.4011 | 23.43 | 91.63%
[5 empty] | 23.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13946.263 | 225185.0678 | 23.44 | 91.63%
[5 empty] | 23.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13958.0714 | 225375.7345 | 23.45 | 91.63%
[5 empty] | 23.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13969.8799 | 225566.4011 | 23.46 | 91.63%
[5 empty] | 23.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13981.6883 | 225757.0678 | 23.47 | 91.63%
[5 empty] | 23.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 13993.4968 | 225947.7345 | 23.48 | 91.63%
[5 empty] | 23.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14005.3052 | 226138.4011 | 23.49 | 91.63%
[5 empty] | 23.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14017.1137 | 226329.0678 | 23.5 | 91.63%
[5 empty] | 23.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14028.9221 | 226519.7345 | 23.51 | 91.63%
[5 empty] | 23.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14040.7306 | 226710.4011 | 23.52 | 91.63%
[5 empty] | 23.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14052.5391 | 226901.0678 | 23.53 | 91.63%
[5 empty] | 23.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14064.3475 | 227091.7345 | 23.54 | 91.63%
[5 empty] | 23.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14076.156 | 227282.4011 | 23.55 | 91.63%
[5 empty] | 23.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14087.9644 | 227473.0678 | 23.56 | 91.63%
[5 empty] | 23.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14099.7729 | 227663.7345 | 23.57 | 91.63%
[5 empty] | 23.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14111.5813 | 227854.4011 | 23.58 | 91.63%
[5 empty] | 23.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14123.3898 | 228045.0678 | 23.59 | 91.63%
[5 empty] | 23.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14135.1982 | 228235.7345 | 23.6 | 91.63%
[5 empty] | 23.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14147.0067 | 228426.4011 | 23.61 | 91.63%
[5 empty] | 23.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14158.8151 | 228617.0678 | 23.62 | 91.63%
[5 empty] | 23.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14170.6236 | 228807.7345 | 23.63 | 91.63%
[5 empty] | 23.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14182.432 | 228998.4011 | 23.64 | 91.63%
[5 empty] | 23.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14194.2405 | 229189.0678 | 23.65 | 91.63%
[5 empty] | 23.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14206.049 | 229379.7345 | 23.66 | 91.63%
[5 empty] | 23.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14217.8574 | 229570.4011 | 23.67 | 91.63%
[5 empty] | 23.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14229.6659 | 229761.0678 | 23.68 | 91.63%
[5 empty] | 23.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14241.4743 | 229951.7345 | 23.69 | 91.63%
[5 empty] | 23.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14253.2828 | 230142.4011 | 23.7 | 91.63%
[5 empty] | 23.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14265.0912 | 230333.0678 | 23.71 | 91.63%
[5 empty] | 23.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14276.8997 | 230523.7345 | 23.72 | 91.63%
[5 empty] | 23.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14288.7081 | 230714.4011 | 23.73 | 91.63%
[5 empty] | 23.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14300.5166 | 230905.0678 | 23.74 | 91.63%
[5 empty] | 23.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14312.325 | 231095.7345 | 23.75 | 91.63%
[5 empty] | 23.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14324.1335 | 231286.4011 | 23.76 | 91.63%
[5 empty] | 23.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14335.9419 | 231477.0678 | 23.77 | 91.63%
[5 empty] | 23.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14347.7504 | 231667.7345 | 23.78 | 91.63%
[5 empty] | 23.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14359.5589 | 231858.4011 | 23.79 | 91.63%
[5 empty] | 23.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14371.3673 | 232049.0678 | 23.8 | 91.63%
[5 empty] | 23.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14383.1758 | 232239.7345 | 23.81 | 91.63%
[5 empty] | 23.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14394.9842 | 232430.4011 | 23.82 | 91.63%
[5 empty] | 23.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14406.7927 | 232621.0678 | 23.83 | 91.63%
[5 empty] | 23.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14418.6011 | 232811.7345 | 23.84 | 91.63%
[5 empty] | 23.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14430.4096 | 233002.4011 | 23.85 | 91.63%
[5 empty] | 23.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14442.218 | 233193.0678 | 23.86 | 91.63%
[5 empty] | 23.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14454.0265 | 233383.7345 | 23.87 | 91.63%
[5 empty] | 23.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14465.8349 | 233574.4011 | 23.88 | 91.63%
[5 empty] | 23.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14477.6434 | 233765.0678 | 23.89 | 91.63%
[5 empty] | 23.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14489.4518 | 233955.7345 | 23.9 | 91.63%
[5 empty] | 23.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14501.2603 | 234146.4011 | 23.91 | 91.63%
[5 empty] | 23.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14513.0688 | 234337.0678 | 23.92 | 91.63%
[5 empty] | 23.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14524.8772 | 234527.7345 | 23.93 | 91.63%
[5 empty] | 23.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14536.6857 | 234718.4011 | 23.94 | 91.63%
[5 empty] | 23.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14548.4941 | 234909.0678 | 23.95 | 91.63%
[5 empty] | 23.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14560.3026 | 235099.7345 | 23.96 | 91.63%
[5 empty] | 23.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14572.111 | 235290.4011 | 23.97 | 91.63%
[5 empty] | 23.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14583.9195 | 235481.0678 | 23.98 | 91.63%
[5 empty] | 23.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14595.7279 | 235671.7345 | 23.99 | 91.63%
[5 empty] | 24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14607.5364 | 235862.4011 | 24 | 91.63%
[5 empty] | 24.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14619.3448 | 236053.0678 | 24.01 | 91.63%
[5 empty] | 24.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14631.1533 | 236243.7345 | 24.02 | 91.63%
[5 empty] | 24.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14642.9617 | 236434.4011 | 24.03 | 91.63%
[5 empty] | 24.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14654.7702 | 236625.0678 | 24.04 | 91.63%
[5 empty] | 24.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14666.5787 | 236815.7345 | 24.05 | 91.63%
[5 empty] | 24.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14678.3871 | 237006.4011 | 24.06 | 91.63%
[5 empty] | 24.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14690.1956 | 237197.0678 | 24.07 | 91.63%
[5 empty] | 24.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14702.004 | 237387.7345 | 24.08 | 91.63%
[5 empty] | 24.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14713.8125 | 237578.4011 | 24.09 | 91.63%
[5 empty] | 24.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14725.6209 | 237769.0678 | 24.1 | 91.63%
[5 empty] | 24.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14737.4294 | 237959.7345 | 24.11 | 91.63%
[5 empty] | 24.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14749.2378 | 238150.4011 | 24.12 | 91.63%
[5 empty] | 24.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14761.0463 | 238341.0678 | 24.13 | 91.63%
[5 empty] | 24.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14772.8547 | 238531.7345 | 24.14 | 91.63%
[5 empty] | 24.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14784.6632 | 238722.4011 | 24.15 | 91.63%
[5 empty] | 24.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14796.4716 | 238913.0678 | 24.16 | 91.63%
[5 empty] | 24.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14808.2801 | 239103.7345 | 24.17 | 91.63%
[5 empty] | 24.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14820.0886 | 239294.4011 | 24.18 | 91.63%
[5 empty] | 24.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14831.897 | 239485.0678 | 24.19 | 91.63%
[5 empty] | 24.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14843.7055 | 239675.7345 | 24.2 | 91.63%
[5 empty] | 24.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14855.5139 | 239866.4011 | 24.21 | 91.63%
[5 empty] | 24.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14867.3224 | 240057.0678 | 24.22 | 91.63%
[5 empty] | 24.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14879.1308 | 240247.7345 | 24.23 | 91.63%
[5 empty] | 24.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14890.9393 | 240438.4011 | 24.24 | 91.63%
[5 empty] | 24.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14902.7477 | 240629.0678 | 24.25 | 91.63%
[5 empty] | 24.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14914.5562 | 240819.7345 | 24.26 | 91.63%
[5 empty] | 24.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14926.3646 | 241010.4011 | 24.27 | 91.63%
[5 empty] | 24.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14938.1731 | 241201.0678 | 24.28 | 91.63%
[5 empty] | 24.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14949.9815 | 241391.7345 | 24.29 | 91.63%
[5 empty] | 24.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14961.79 | 241582.4011 | 24.3 | 91.63%
[5 empty] | 24.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14973.5985 | 241773.0678 | 24.31 | 91.63%
[5 empty] | 24.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14985.4069 | 241963.7345 | 24.32 | 91.63%
[5 empty] | 24.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 14997.2154 | 242154.4011 | 24.33 | 91.63%
[5 empty] | 24.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15009.0238 | 242345.0678 | 24.34 | 91.63%
[5 empty] | 24.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15020.8323 | 242535.7345 | 24.35 | 91.63%
[5 empty] | 24.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15032.6407 | 242726.4011 | 24.36 | 91.63%
[5 empty] | 24.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15044.4492 | 242917.0678 | 24.37 | 91.63%
[5 empty] | 24.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15056.2576 | 243107.7345 | 24.38 | 91.63%
[5 empty] | 24.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15068.0661 | 243298.4011 | 24.39 | 91.63%
[5 empty] | 24.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15079.8745 | 243489.0678 | 24.4 | 91.63%
[5 empty] | 24.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15091.683 | 243679.7345 | 24.41 | 91.63%
[5 empty] | 24.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15103.4914 | 243870.4011 | 24.42 | 91.63%
[5 empty] | 24.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15115.2999 | 244061.0678 | 24.43 | 91.63%
[5 empty] | 24.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15127.1084 | 244251.7345 | 24.44 | 91.63%
[5 empty] | 24.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15138.9168 | 244442.4011 | 24.45 | 91.63%
[5 empty] | 24.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15150.7253 | 244633.0678 | 24.46 | 91.63%
[5 empty] | 24.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15162.5337 | 244823.7345 | 24.47 | 91.63%
[5 empty] | 24.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15174.3422 | 245014.4011 | 24.48 | 91.63%
[5 empty] | 24.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15186.1506 | 245205.0678 | 24.49 | 91.63%
[5 empty] | 24.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15197.9591 | 245395.7345 | 24.5 | 91.63%
[5 empty] | 24.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15209.7675 | 245586.4011 | 24.51 | 91.63%
[5 empty] | 24.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15221.576 | 245777.0678 | 24.52 | 91.63%
[5 empty] | 24.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15233.3844 | 245967.7345 | 24.53 | 91.63%
[5 empty] | 24.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15245.1929 | 246158.4011 | 24.54 | 91.63%
[5 empty] | 24.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15257.0013 | 246349.0678 | 24.55 | 91.63%
[5 empty] | 24.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15268.8098 | 246539.7345 | 24.56 | 91.63%
[5 empty] | 24.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15280.6183 | 246730.4011 | 24.57 | 91.63%
[5 empty] | 24.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15292.4267 | 246921.0678 | 24.58 | 91.63%
[5 empty] | 24.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15304.2352 | 247111.7345 | 24.59 | 91.63%
[5 empty] | 24.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15316.0436 | 247302.4011 | 24.6 | 91.63%
[5 empty] | 24.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15327.8521 | 247493.0678 | 24.61 | 91.63%
[5 empty] | 24.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15339.6605 | 247683.7345 | 24.62 | 91.63%
[5 empty] | 24.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15351.469 | 247874.4011 | 24.63 | 91.63%
[5 empty] | 24.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15363.2774 | 248065.0678 | 24.64 | 91.63%
[5 empty] | 24.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15375.0859 | 248255.7345 | 24.65 | 91.63%
[5 empty] | 24.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15386.8943 | 248446.4011 | 24.66 | 91.63%
[5 empty] | 24.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15398.7028 | 248637.0678 | 24.67 | 91.63%
[5 empty] | 24.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15410.5112 | 248827.7345 | 24.68 | 91.63%
[5 empty] | 24.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15422.3197 | 249018.4011 | 24.69 | 91.63%
[5 empty] | 24.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15434.1282 | 249209.0678 | 24.7 | 91.63%
[5 empty] | 24.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15445.9366 | 249399.7345 | 24.71 | 91.63%
[5 empty] | 24.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15457.7451 | 249590.4011 | 24.72 | 91.63%
[5 empty] | 24.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15469.5535 | 249781.0678 | 24.73 | 91.63%
[5 empty] | 24.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15481.362 | 249971.7345 | 24.74 | 91.63%
[5 empty] | 24.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15493.1704 | 250162.4011 | 24.75 | 91.63%
[5 empty] | 24.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15504.9789 | 250353.0678 | 24.76 | 91.63%
[5 empty] | 24.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15516.7873 | 250543.7345 | 24.77 | 91.63%
[5 empty] | 24.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15528.5958 | 250734.4011 | 24.78 | 91.63%
[5 empty] | 24.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15540.4042 | 250925.0678 | 24.79 | 91.63%
[5 empty] | 24.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15552.2127 | 251115.7345 | 24.8 | 91.63%
[5 empty] | 24.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15564.0211 | 251306.4011 | 24.81 | 91.63%
[5 empty] | 24.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15575.8296 | 251497.0678 | 24.82 | 91.63%
[5 empty] | 24.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15587.638 | 251687.7345 | 24.83 | 91.63%
[5 empty] | 24.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15599.4465 | 251878.4011 | 24.84 | 91.63%
[5 empty] | 24.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15611.255 | 252069.0678 | 24.85 | 91.63%
[5 empty] | 24.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15623.0634 | 252259.7345 | 24.86 | 91.63%
[5 empty] | 24.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15634.8719 | 252450.4011 | 24.87 | 91.63%
[5 empty] | 24.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15646.6803 | 252641.0678 | 24.88 | 91.63%
[5 empty] | 24.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15658.4888 | 252831.7345 | 24.89 | 91.63%
[5 empty] | 24.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15670.2972 | 253022.4011 | 24.9 | 91.63%
[5 empty] | 24.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15682.1057 | 253213.0678 | 24.91 | 91.63%
[5 empty] | 24.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15693.9141 | 253403.7345 | 24.92 | 91.63%
[5 empty] | 24.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15705.7226 | 253594.4011 | 24.93 | 91.63%
[5 empty] | 24.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15717.531 | 253785.0678 | 24.94 | 91.63%
[5 empty] | 24.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15729.3395 | 253975.7345 | 24.95 | 91.63%
[5 empty] | 24.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15741.1479 | 254166.4011 | 24.96 | 91.63%
[5 empty] | 24.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15752.9564 | 254357.0678 | 24.97 | 91.63%
[5 empty] | 24.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15764.7649 | 254547.7345 | 24.98 | 91.63%
[5 empty] | 24.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15776.5733 | 254738.4011 | 24.99 | 91.63%
[5 empty] | 25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15788.3818 | 254929.0678 | 25 | 91.63%
[5 empty] | 25.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15800.1902 | 255119.7345 | 25.01 | 91.63%
[5 empty] | 25.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15811.9987 | 255310.4011 | 25.02 | 91.63%
[5 empty] | 25.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15823.8071 | 255501.0678 | 25.03 | 91.63%
[5 empty] | 25.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15835.6156 | 255691.7345 | 25.04 | 91.63%
[5 empty] | 25.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15847.424 | 255882.4011 | 25.05 | 91.63%
[5 empty] | 25.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15859.2325 | 256073.0678 | 25.06 | 91.63%
[5 empty] | 25.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15871.0409 | 256263.7345 | 25.07 | 91.63%
[5 empty] | 25.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15882.8494 | 256454.4011 | 25.08 | 91.63%
[5 empty] | 25.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15894.6578 | 256645.0678 | 25.09 | 91.63%
[5 empty] | 25.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15906.4663 | 256835.7345 | 25.1 | 91.63%
[5 empty] | 25.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15918.2748 | 257026.4011 | 25.11 | 91.63%
[5 empty] | 25.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15930.0832 | 257217.0678 | 25.12 | 91.63%
[5 empty] | 25.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15941.8917 | 257407.7345 | 25.13 | 91.63%
[5 empty] | 25.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15953.7001 | 257598.4011 | 25.14 | 91.63%
[5 empty] | 25.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15965.5086 | 257789.0678 | 25.15 | 91.63%
[5 empty] | 25.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15977.317 | 257979.7345 | 25.16 | 91.63%
[5 empty] | 25.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 15989.1255 | 258170.4011 | 25.17 | 91.63%
[5 empty] | 25.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16000.9339 | 258361.0678 | 25.18 | 91.63%
[5 empty] | 25.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16012.7424 | 258551.7345 | 25.19 | 91.63%
[5 empty] | 25.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16024.5508 | 258742.4011 | 25.2 | 91.63%
[5 empty] | 25.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16036.3593 | 258933.0678 | 25.21 | 91.63%
[5 empty] | 25.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16048.1677 | 259123.7345 | 25.22 | 91.63%
[5 empty] | 25.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16059.9762 | 259314.4011 | 25.23 | 91.63%
[5 empty] | 25.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16071.7847 | 259505.0678 | 25.24 | 91.63%
[5 empty] | 25.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16083.5931 | 259695.7345 | 25.25 | 91.63%
[5 empty] | 25.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16095.4016 | 259886.4011 | 25.26 | 91.63%
[5 empty] | 25.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16107.21 | 260077.0678 | 25.27 | 91.63%
[5 empty] | 25.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16119.0185 | 260267.7345 | 25.28 | 91.63%
[5 empty] | 25.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16130.8269 | 260458.4011 | 25.29 | 91.63%
[5 empty] | 25.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16142.6354 | 260649.0678 | 25.3 | 91.63%
[5 empty] | 25.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16154.4438 | 260839.7345 | 25.31 | 91.63%
[5 empty] | 25.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16166.2523 | 261030.4011 | 25.32 | 91.63%
[5 empty] | 25.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16178.0607 | 261221.0678 | 25.33 | 91.63%
[5 empty] | 25.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16189.8692 | 261411.7345 | 25.34 | 91.63%
[5 empty] | 25.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16201.6776 | 261602.4011 | 25.35 | 91.63%
[5 empty] | 25.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16213.4861 | 261793.0678 | 25.36 | 91.63%
[5 empty] | 25.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16225.2946 | 261983.7345 | 25.37 | 91.63%
[5 empty] | 25.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16237.103 | 262174.4011 | 25.38 | 91.63%
[5 empty] | 25.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16248.9115 | 262365.0678 | 25.39 | 91.63%
[5 empty] | 25.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16260.7199 | 262555.7345 | 25.4 | 91.63%
[5 empty] | 25.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16272.5284 | 262746.4011 | 25.41 | 91.63%
[5 empty] | 25.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16284.3368 | 262937.0678 | 25.42 | 91.63%
[5 empty] | 25.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16296.1453 | 263127.7345 | 25.43 | 91.63%
[5 empty] | 25.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16307.9537 | 263318.4011 | 25.44 | 91.63%
[5 empty] | 25.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16319.7622 | 263509.0678 | 25.45 | 91.63%
[5 empty] | 25.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16331.5706 | 263699.7345 | 25.46 | 91.63%
[5 empty] | 25.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16343.3791 | 263890.4011 | 25.47 | 91.63%
[5 empty] | 25.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16355.1875 | 264081.0678 | 25.48 | 91.63%
[5 empty] | 25.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16366.996 | 264271.7345 | 25.49 | 91.63%
[5 empty] | 25.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16378.8045 | 264462.4011 | 25.5 | 91.63%
[5 empty] | 25.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16390.6129 | 264653.0678 | 25.51 | 91.63%
[5 empty] | 25.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16402.4214 | 264843.7345 | 25.52 | 91.63%
[5 empty] | 25.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16414.2298 | 265034.4011 | 25.53 | 91.63%
[5 empty] | 25.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16426.0383 | 265225.0678 | 25.54 | 91.63%
[5 empty] | 25.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16437.8467 | 265415.7345 | 25.55 | 91.63%
[5 empty] | 25.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16449.6552 | 265606.4011 | 25.56 | 91.63%
[5 empty] | 25.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16461.4636 | 265797.0678 | 25.57 | 91.63%
[5 empty] | 25.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16473.2721 | 265987.7345 | 25.58 | 91.63%
[5 empty] | 25.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16485.0805 | 266178.4011 | 25.59 | 91.63%
[5 empty] | 25.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16496.889 | 266369.0678 | 25.6 | 91.63%
[5 empty] | 25.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16508.6974 | 266559.7345 | 25.61 | 91.63%
[5 empty] | 25.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16520.5059 | 266750.4011 | 25.62 | 91.63%
[5 empty] | 25.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16532.3144 | 266941.0678 | 25.63 | 91.63%
[5 empty] | 25.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16544.1228 | 267131.7345 | 25.64 | 91.63%
[5 empty] | 25.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16555.9313 | 267322.4011 | 25.65 | 91.63%
[5 empty] | 25.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16567.7397 | 267513.0678 | 25.66 | 91.63%
[5 empty] | 25.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16579.5482 | 267703.7345 | 25.67 | 91.63%
[5 empty] | 25.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16591.3566 | 267894.4011 | 25.68 | 91.63%
[5 empty] | 25.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16603.1651 | 268085.0678 | 25.69 | 91.63%
[5 empty] | 25.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16614.9735 | 268275.7345 | 25.7 | 91.63%
[5 empty] | 25.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16626.782 | 268466.4011 | 25.71 | 91.63%
[5 empty] | 25.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16638.5904 | 268657.0678 | 25.72 | 91.63%
[5 empty] | 25.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16650.3989 | 268847.7345 | 25.73 | 91.63%
[5 empty] | 25.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16662.2073 | 269038.4011 | 25.74 | 91.63%
[5 empty] | 25.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16674.0158 | 269229.0678 | 25.75 | 91.63%
[5 empty] | 25.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16685.8243 | 269419.7345 | 25.76 | 91.63%
[5 empty] | 25.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16697.6327 | 269610.4011 | 25.77 | 91.63%
[5 empty] | 25.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16709.4412 | 269801.0678 | 25.78 | 91.63%
[5 empty] | 25.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16721.2496 | 269991.7345 | 25.79 | 91.63%
[5 empty] | 25.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16733.0581 | 270182.4011 | 25.8 | 91.63%
[5 empty] | 25.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16744.8665 | 270373.0678 | 25.81 | 91.63%
[5 empty] | 25.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16756.675 | 270563.7345 | 25.82 | 91.63%
[5 empty] | 25.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16768.4834 | 270754.4011 | 25.83 | 91.63%
[5 empty] | 25.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16780.2919 | 270945.0678 | 25.84 | 91.63%
[5 empty] | 25.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16792.1003 | 271135.7345 | 25.85 | 91.63%
[5 empty] | 25.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16803.9088 | 271326.4011 | 25.86 | 91.63%
[5 empty] | 25.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16815.7172 | 271517.0678 | 25.87 | 91.63%
[5 empty] | 25.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16827.5257 | 271707.7345 | 25.88 | 91.63%
[5 empty] | 25.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16839.3342 | 271898.4011 | 25.89 | 91.63%
[5 empty] | 25.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16851.1426 | 272089.0678 | 25.9 | 91.63%
[5 empty] | 25.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16862.9511 | 272279.7345 | 25.91 | 91.63%
[5 empty] | 25.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16874.7595 | 272470.4011 | 25.92 | 91.63%
[5 empty] | 25.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16886.568 | 272661.0678 | 25.93 | 91.63%
[5 empty] | 25.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16898.3764 | 272851.7345 | 25.94 | 91.63%
[5 empty] | 25.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16910.1849 | 273042.4011 | 25.95 | 91.63%
[5 empty] | 25.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16921.9933 | 273233.0678 | 25.96 | 91.63%
[5 empty] | 25.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16933.8018 | 273423.7345 | 25.97 | 91.63%
[5 empty] | 25.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16945.6102 | 273614.4011 | 25.98 | 91.63%
[5 empty] | 25.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16957.4187 | 273805.0678 | 25.99 | 91.63%
[5 empty] | 26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16969.2271 | 273995.7345 | 26 | 91.63%
[5 empty] | 26.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16981.0356 | 274186.4011 | 26.01 | 91.63%
[5 empty] | 26.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 16992.8441 | 274377.0678 | 26.02 | 91.63%
[5 empty] | 26.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17004.6525 | 274567.7345 | 26.03 | 91.63%
[5 empty] | 26.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17016.461 | 274758.4011 | 26.04 | 91.63%
[5 empty] | 26.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17028.2694 | 274949.0678 | 26.05 | 91.63%
[5 empty] | 26.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17040.0779 | 275139.7345 | 26.06 | 91.63%
[5 empty] | 26.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17051.8863 | 275330.4011 | 26.07 | 91.63%
[5 empty] | 26.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17063.6948 | 275521.0678 | 26.08 | 91.63%
[5 empty] | 26.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17075.5032 | 275711.7345 | 26.09 | 91.63%
[5 empty] | 26.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17087.3117 | 275902.4011 | 26.1 | 91.63%
[5 empty] | 26.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17099.1201 | 276093.0678 | 26.11 | 91.63%
[5 empty] | 26.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17110.9286 | 276283.7345 | 26.12 | 91.63%
[5 empty] | 26.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17122.737 | 276474.4011 | 26.13 | 91.63%
[5 empty] | 26.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17134.5455 | 276665.0678 | 26.14 | 91.63%
[5 empty] | 26.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17146.354 | 276855.7345 | 26.15 | 91.63%
[5 empty] | 26.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17158.1624 | 277046.4011 | 26.16 | 91.63%
[5 empty] | 26.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17169.9709 | 277237.0678 | 26.17 | 91.63%
[5 empty] | 26.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17181.7793 | 277427.7345 | 26.18 | 91.63%
[5 empty] | 26.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17193.5878 | 277618.4011 | 26.19 | 91.63%
[5 empty] | 26.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17205.3962 | 277809.0678 | 26.2 | 91.63%
[5 empty] | 26.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17217.2047 | 277999.7345 | 26.21 | 91.63%
[5 empty] | 26.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17229.0131 | 278190.4011 | 26.22 | 91.63%
[5 empty] | 26.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17240.8216 | 278381.0678 | 26.23 | 91.63%
[5 empty] | 26.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17252.63 | 278571.7345 | 26.24 | 91.63%
[5 empty] | 26.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17264.4385 | 278762.4011 | 26.25 | 91.63%
[5 empty] | 26.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17276.2469 | 278953.0678 | 26.26 | 91.63%
[5 empty] | 26.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17288.0554 | 279143.7345 | 26.27 | 91.63%
[5 empty] | 26.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17299.8639 | 279334.4011 | 26.28 | 91.63%
[5 empty] | 26.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17311.6723 | 279525.0678 | 26.29 | 91.63%
[5 empty] | 26.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17323.4808 | 279715.7345 | 26.3 | 91.63%
[5 empty] | 26.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17335.2892 | 279906.4011 | 26.31 | 91.63%
[5 empty] | 26.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17347.0977 | 280097.0678 | 26.32 | 91.63%
[5 empty] | 26.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17358.9061 | 280287.7345 | 26.33 | 91.63%
[5 empty] | 26.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17370.7146 | 280478.4011 | 26.34 | 91.63%
[5 empty] | 26.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17382.523 | 280669.0678 | 26.35 | 91.63%
[5 empty] | 26.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17394.3315 | 280859.7345 | 26.36 | 91.63%
[5 empty] | 26.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17406.1399 | 281050.4011 | 26.37 | 91.63%
[5 empty] | 26.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17417.9484 | 281241.0678 | 26.38 | 91.63%
[5 empty] | 26.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17429.7568 | 281431.7345 | 26.39 | 91.63%
[5 empty] | 26.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17441.5653 | 281622.4011 | 26.4 | 91.63%
[5 empty] | 26.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17453.3738 | 281813.0678 | 26.41 | 91.63%
[5 empty] | 26.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17465.1822 | 282003.7345 | 26.42 | 91.63%
[5 empty] | 26.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17476.9907 | 282194.4011 | 26.43 | 91.63%
[5 empty] | 26.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17488.7991 | 282385.0678 | 26.44 | 91.63%
[5 empty] | 26.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17500.6076 | 282575.7345 | 26.45 | 91.63%
[5 empty] | 26.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17512.416 | 282766.4011 | 26.46 | 91.63%
[5 empty] | 26.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17524.2245 | 282957.0678 | 26.47 | 91.63%
[5 empty] | 26.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17536.0329 | 283147.7345 | 26.48 | 91.63%
[5 empty] | 26.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17547.8414 | 283338.4011 | 26.49 | 91.63%
[5 empty] | 26.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17559.6498 | 283529.0678 | 26.5 | 91.63%
[5 empty] | 26.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17571.4583 | 283719.7345 | 26.51 | 91.63%
[5 empty] | 26.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17583.2667 | 283910.4011 | 26.52 | 91.63%
[5 empty] | 26.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17595.0752 | 284101.0678 | 26.53 | 91.63%
[5 empty] | 26.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17606.8837 | 284291.7345 | 26.54 | 91.63%
[5 empty] | 26.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17618.6921 | 284482.4011 | 26.55 | 91.63%
[5 empty] | 26.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17630.5006 | 284673.0678 | 26.56 | 91.63%
[5 empty] | 26.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17642.309 | 284863.7345 | 26.57 | 91.63%
[5 empty] | 26.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17654.1175 | 285054.4011 | 26.58 | 91.63%
[5 empty] | 26.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17665.9259 | 285245.0678 | 26.59 | 91.63%
[5 empty] | 26.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17677.7344 | 285435.7345 | 26.6 | 91.63%
[5 empty] | 26.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17689.5428 | 285626.4011 | 26.61 | 91.63%
[5 empty] | 26.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17701.3513 | 285817.0678 | 26.62 | 91.63%
[5 empty] | 26.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17713.1597 | 286007.7345 | 26.63 | 91.63%
[5 empty] | 26.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17724.9682 | 286198.4011 | 26.64 | 91.63%
[5 empty] | 26.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17736.7766 | 286389.0678 | 26.65 | 91.63%
[5 empty] | 26.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17748.5851 | 286579.7345 | 26.66 | 91.63%
[5 empty] | 26.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17760.3936 | 286770.4011 | 26.67 | 91.63%
[5 empty] | 26.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17772.202 | 286961.0678 | 26.68 | 91.63%
[5 empty] | 26.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17784.0105 | 287151.7345 | 26.69 | 91.63%
[5 empty] | 26.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17795.8189 | 287342.4011 | 26.7 | 91.63%
[5 empty] | 26.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17807.6274 | 287533.0678 | 26.71 | 91.63%
[5 empty] | 26.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17819.4358 | 287723.7345 | 26.72 | 91.63%
[5 empty] | 26.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17831.2443 | 287914.4011 | 26.73 | 91.63%
[5 empty] | 26.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17843.0527 | 288105.0678 | 26.74 | 91.63%
[5 empty] | 26.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17854.8612 | 288295.7345 | 26.75 | 91.63%
[5 empty] | 26.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17866.6696 | 288486.4011 | 26.76 | 91.63%
[5 empty] | 26.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17878.4781 | 288677.0678 | 26.77 | 91.63%
[5 empty] | 26.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17890.2865 | 288867.7345 | 26.78 | 91.63%
[5 empty] | 26.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17902.095 | 289058.4011 | 26.79 | 91.63%
[5 empty] | 26.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17913.9035 | 289249.0678 | 26.8 | 91.63%
[5 empty] | 26.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17925.7119 | 289439.7345 | 26.81 | 91.63%
[5 empty] | 26.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17937.5204 | 289630.4011 | 26.82 | 91.63%
[5 empty] | 26.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17949.3288 | 289821.0678 | 26.83 | 91.63%
[5 empty] | 26.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17961.1373 | 290011.7345 | 26.84 | 91.63%
[5 empty] | 26.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17972.9457 | 290202.4011 | 26.85 | 91.63%
[5 empty] | 26.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17984.7542 | 290393.0678 | 26.86 | 91.63%
[5 empty] | 26.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 17996.5626 | 290583.7345 | 26.87 | 91.63%
[5 empty] | 26.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18008.3711 | 290774.4011 | 26.88 | 91.63%
[5 empty] | 26.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18020.1795 | 290965.0678 | 26.89 | 91.63%
[5 empty] | 26.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18031.988 | 291155.7345 | 26.9 | 91.63%
[5 empty] | 26.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18043.7964 | 291346.4011 | 26.91 | 91.63%
[5 empty] | 26.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18055.6049 | 291537.0678 | 26.92 | 91.63%
[5 empty] | 26.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18067.4134 | 291727.7345 | 26.93 | 91.63%
[5 empty] | 26.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18079.2218 | 291918.4011 | 26.94 | 91.63%
[5 empty] | 26.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18091.0303 | 292109.0678 | 26.95 | 91.63%
[5 empty] | 26.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18102.8387 | 292299.7345 | 26.96 | 91.63%
[5 empty] | 26.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18114.6472 | 292490.4011 | 26.97 | 91.63%
[5 empty] | 26.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18126.4556 | 292681.0678 | 26.98 | 91.63%
[5 empty] | 26.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18138.2641 | 292871.7345 | 26.99 | 91.63%
[5 empty] | 27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18150.0725 | 293062.4011 | 27 | 91.63%
[5 empty] | 27.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18161.881 | 293253.0678 | 27.01 | 91.63%
[5 empty] | 27.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18173.6894 | 293443.7345 | 27.02 | 91.63%
[5 empty] | 27.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18185.4979 | 293634.4011 | 27.03 | 91.63%
[5 empty] | 27.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18197.3063 | 293825.0678 | 27.04 | 91.63%
[5 empty] | 27.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18209.1148 | 294015.7345 | 27.05 | 91.63%
[5 empty] | 27.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18220.9233 | 294206.4011 | 27.06 | 91.63%
[5 empty] | 27.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18232.7317 | 294397.0678 | 27.07 | 91.63%
[5 empty] | 27.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18244.5402 | 294587.7345 | 27.08 | 91.63%
[5 empty] | 27.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18256.3486 | 294778.4011 | 27.09 | 91.63%
[5 empty] | 27.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18268.1571 | 294969.0678 | 27.1 | 91.63%
[5 empty] | 27.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18279.9655 | 295159.7345 | 27.11 | 91.63%
[5 empty] | 27.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18291.774 | 295350.4011 | 27.12 | 91.63%
[5 empty] | 27.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18303.5824 | 295541.0678 | 27.13 | 91.63%
[5 empty] | 27.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18315.3909 | 295731.7345 | 27.14 | 91.63%
[5 empty] | 27.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18327.1993 | 295922.4011 | 27.15 | 91.63%
[5 empty] | 27.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18339.0078 | 296113.0678 | 27.16 | 91.63%
[5 empty] | 27.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18350.8162 | 296303.7345 | 27.17 | 91.63%
[5 empty] | 27.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18362.6247 | 296494.4011 | 27.18 | 91.63%
[5 empty] | 27.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18374.4332 | 296685.0678 | 27.19 | 91.63%
[5 empty] | 27.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18386.2416 | 296875.7345 | 27.2 | 91.63%
[5 empty] | 27.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18398.0501 | 297066.4011 | 27.21 | 91.63%
[5 empty] | 27.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18409.8585 | 297257.0678 | 27.22 | 91.63%
[5 empty] | 27.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18421.667 | 297447.7345 | 27.23 | 91.63%
[5 empty] | 27.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18433.4754 | 297638.4011 | 27.24 | 91.63%
[5 empty] | 27.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18445.2839 | 297829.0678 | 27.25 | 91.63%
[5 empty] | 27.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18457.0923 | 298019.7345 | 27.26 | 91.63%
[5 empty] | 27.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18468.9008 | 298210.4011 | 27.27 | 91.63%
[5 empty] | 27.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18480.7092 | 298401.0678 | 27.28 | 91.63%
[5 empty] | 27.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18492.5177 | 298591.7345 | 27.29 | 91.63%
[5 empty] | 27.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18504.3261 | 298782.4011 | 27.3 | 91.63%
[5 empty] | 27.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18516.1346 | 298973.0678 | 27.31 | 91.63%
[5 empty] | 27.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18527.943 | 299163.7345 | 27.32 | 91.63%
[5 empty] | 27.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18539.7515 | 299354.4011 | 27.33 | 91.63%
[5 empty] | 27.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18551.56 | 299545.0678 | 27.34 | 91.63%
[5 empty] | 27.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18563.3684 | 299735.7345 | 27.35 | 91.63%
[5 empty] | 27.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18575.1769 | 299926.4011 | 27.36 | 91.63%
[5 empty] | 27.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18586.9853 | 300117.0678 | 27.37 | 91.63%
[5 empty] | 27.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18598.7938 | 300307.7345 | 27.38 | 91.63%
[5 empty] | 27.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18610.6022 | 300498.4011 | 27.39 | 91.63%
[5 empty] | 27.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18622.4107 | 300689.0678 | 27.4 | 91.63%
[5 empty] | 27.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18634.2191 | 300879.7345 | 27.41 | 91.63%
[5 empty] | 27.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18646.0276 | 301070.4011 | 27.42 | 91.63%
[5 empty] | 27.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18657.836 | 301261.0678 | 27.43 | 91.63%
[5 empty] | 27.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18669.6445 | 301451.7345 | 27.44 | 91.63%
[5 empty] | 27.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18681.4529 | 301642.4011 | 27.45 | 91.63%
[5 empty] | 27.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18693.2614 | 301833.0678 | 27.46 | 91.63%
[5 empty] | 27.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18705.0699 | 302023.7345 | 27.47 | 91.63%
[5 empty] | 27.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18716.8783 | 302214.4011 | 27.48 | 91.63%
[5 empty] | 27.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18728.6868 | 302405.0678 | 27.49 | 91.63%
[5 empty] | 27.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18740.4952 | 302595.7345 | 27.5 | 91.63%
[5 empty] | 27.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18752.3037 | 302786.4011 | 27.51 | 91.63%
[5 empty] | 27.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18764.1121 | 302977.0678 | 27.52 | 91.63%
[5 empty] | 27.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18775.9206 | 303167.7345 | 27.53 | 91.63%
[5 empty] | 27.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18787.729 | 303358.4011 | 27.54 | 91.63%
[5 empty] | 27.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18799.5375 | 303549.0678 | 27.55 | 91.63%
[5 empty] | 27.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18811.3459 | 303739.7345 | 27.56 | 91.63%
[5 empty] | 27.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18823.1544 | 303930.4011 | 27.57 | 91.63%
[5 empty] | 27.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18834.9628 | 304121.0678 | 27.58 | 91.63%
[5 empty] | 27.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18846.7713 | 304311.7345 | 27.59 | 91.63%
[5 empty] | 27.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18858.5798 | 304502.4011 | 27.6 | 91.63%
[5 empty] | 27.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18870.3882 | 304693.0678 | 27.61 | 91.63%
[5 empty] | 27.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18882.1967 | 304883.7345 | 27.62 | 91.63%
[5 empty] | 27.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18894.0051 | 305074.4011 | 27.63 | 91.63%
[5 empty] | 27.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18905.8136 | 305265.0678 | 27.64 | 91.63%
[5 empty] | 27.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18917.622 | 305455.7345 | 27.65 | 91.63%
[5 empty] | 27.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18929.4305 | 305646.4011 | 27.66 | 91.63%
[5 empty] | 27.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18941.2389 | 305837.0678 | 27.67 | 91.63%
[5 empty] | 27.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18953.0474 | 306027.7345 | 27.68 | 91.63%
[5 empty] | 27.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18964.8558 | 306218.4011 | 27.69 | 91.63%
[5 empty] | 27.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18976.6643 | 306409.0678 | 27.7 | 91.63%
[5 empty] | 27.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 18988.4727 | 306599.7345 | 27.71 | 91.63%
[5 empty] | 27.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19000.2812 | 306790.4011 | 27.72 | 91.63%
[5 empty] | 27.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19012.0897 | 306981.0678 | 27.73 | 91.63%
[5 empty] | 27.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19023.8981 | 307171.7345 | 27.74 | 91.63%
[5 empty] | 27.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19035.7066 | 307362.4011 | 27.75 | 91.63%
[5 empty] | 27.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19047.515 | 307553.0678 | 27.76 | 91.63%
[5 empty] | 27.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19059.3235 | 307743.7345 | 27.77 | 91.63%
[5 empty] | 27.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19071.1319 | 307934.4011 | 27.78 | 91.63%
[5 empty] | 27.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19082.9404 | 308125.0678 | 27.79 | 91.63%
[5 empty] | 27.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19094.7488 | 308315.7345 | 27.8 | 91.63%
[5 empty] | 27.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19106.5573 | 308506.4011 | 27.81 | 91.63%
[5 empty] | 27.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19118.3657 | 308697.0678 | 27.82 | 91.63%
[5 empty] | 27.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19130.1742 | 308887.7345 | 27.83 | 91.63%
[5 empty] | 27.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19141.9826 | 309078.4011 | 27.84 | 91.63%
[5 empty] | 27.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19153.7911 | 309269.0678 | 27.85 | 91.63%
[5 empty] | 27.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19165.5996 | 309459.7345 | 27.86 | 91.63%
[5 empty] | 27.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19177.408 | 309650.4011 | 27.87 | 91.63%
[5 empty] | 27.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19189.2165 | 309841.0678 | 27.88 | 91.63%
[5 empty] | 27.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19201.0249 | 310031.7345 | 27.89 | 91.63%
[5 empty] | 27.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19212.8334 | 310222.4011 | 27.9 | 91.63%
[5 empty] | 27.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19224.6418 | 310413.0678 | 27.91 | 91.63%
[5 empty] | 27.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19236.4503 | 310603.7345 | 27.92 | 91.63%
[5 empty] | 27.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19248.2587 | 310794.4011 | 27.93 | 91.63%
[5 empty] | 27.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19260.0672 | 310985.0678 | 27.94 | 91.63%
[5 empty] | 27.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19271.8756 | 311175.7345 | 27.95 | 91.63%
[5 empty] | 27.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19283.6841 | 311366.4011 | 27.96 | 91.63%
[5 empty] | 27.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19295.4925 | 311557.0678 | 27.97 | 91.63%
[5 empty] | 27.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19307.301 | 311747.7345 | 27.98 | 91.63%
[5 empty] | 27.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19319.1095 | 311938.4011 | 27.99 | 91.63%
[5 empty] | 28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19330.9179 | 312129.0678 | 28 | 91.63%
[5 empty] | 28.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19342.7264 | 312319.7345 | 28.01 | 91.63%
[5 empty] | 28.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19354.5348 | 312510.4011 | 28.02 | 91.63%
[5 empty] | 28.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19366.3433 | 312701.0678 | 28.03 | 91.63%
[5 empty] | 28.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19378.1517 | 312891.7345 | 28.04 | 91.63%
[5 empty] | 28.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19389.9602 | 313082.4011 | 28.05 | 91.63%
[5 empty] | 28.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19401.7686 | 313273.0678 | 28.06 | 91.63%
[5 empty] | 28.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19413.5771 | 313463.7345 | 28.07 | 91.63%
[5 empty] | 28.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19425.3855 | 313654.4011 | 28.08 | 91.63%
[5 empty] | 28.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19437.194 | 313845.0678 | 28.09 | 91.63%
[5 empty] | 28.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19449.0024 | 314035.7345 | 28.1 | 91.63%
[5 empty] | 28.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19460.8109 | 314226.4011 | 28.11 | 91.63%
[5 empty] | 28.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19472.6194 | 314417.0678 | 28.12 | 91.63%
[5 empty] | 28.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19484.4278 | 314607.7345 | 28.13 | 91.63%
[5 empty] | 28.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19496.2363 | 314798.4011 | 28.14 | 91.63%
[5 empty] | 28.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19508.0447 | 314989.0678 | 28.15 | 91.63%
[5 empty] | 28.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19519.8532 | 315179.7345 | 28.16 | 91.63%
[5 empty] | 28.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19531.6616 | 315370.4011 | 28.17 | 91.63%
[5 empty] | 28.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19543.4701 | 315561.0678 | 28.18 | 91.63%
[5 empty] | 28.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19555.2785 | 315751.7345 | 28.19 | 91.63%
[5 empty] | 28.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19567.087 | 315942.4011 | 28.2 | 91.63%
[5 empty] | 28.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19578.8954 | 316133.0678 | 28.21 | 91.63%
[5 empty] | 28.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19590.7039 | 316323.7345 | 28.22 | 91.63%
[5 empty] | 28.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19602.5123 | 316514.4011 | 28.23 | 91.63%
[5 empty] | 28.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19614.3208 | 316705.0678 | 28.24 | 91.63%
[5 empty] | 28.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19626.1293 | 316895.7345 | 28.25 | 91.63%
[5 empty] | 28.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19637.9377 | 317086.4011 | 28.26 | 91.63%
[5 empty] | 28.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19649.7462 | 317277.0678 | 28.27 | 91.63%
[5 empty] | 28.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19661.5546 | 317467.7345 | 28.28 | 91.63%
[5 empty] | 28.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19673.3631 | 317658.4011 | 28.29 | 91.63%
[5 empty] | 28.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19685.1715 | 317849.0678 | 28.3 | 91.63%
[5 empty] | 28.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19696.98 | 318039.7345 | 28.31 | 91.63%
[5 empty] | 28.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19708.7884 | 318230.4011 | 28.32 | 91.63%
[5 empty] | 28.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19720.5969 | 318421.0678 | 28.33 | 91.63%
[5 empty] | 28.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19732.4053 | 318611.7345 | 28.34 | 91.63%
[5 empty] | 28.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19744.2138 | 318802.4011 | 28.35 | 91.63%
[5 empty] | 28.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19756.0222 | 318993.0678 | 28.36 | 91.63%
[5 empty] | 28.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19767.8307 | 319183.7345 | 28.37 | 91.63%
[5 empty] | 28.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19779.6392 | 319374.4011 | 28.38 | 91.63%
[5 empty] | 28.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19791.4476 | 319565.0678 | 28.39 | 91.63%
[5 empty] | 28.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19803.2561 | 319755.7345 | 28.4 | 91.63%
[5 empty] | 28.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19815.0645 | 319946.4011 | 28.41 | 91.63%
[5 empty] | 28.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19826.873 | 320137.0678 | 28.42 | 91.63%
[5 empty] | 28.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19838.6814 | 320327.7345 | 28.43 | 91.63%
[5 empty] | 28.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19850.4899 | 320518.4011 | 28.44 | 91.63%
[5 empty] | 28.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19862.2983 | 320709.0678 | 28.45 | 91.63%
[5 empty] | 28.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19874.1068 | 320899.7345 | 28.46 | 91.63%
[5 empty] | 28.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19885.9152 | 321090.4011 | 28.47 | 91.63%
[5 empty] | 28.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19897.7237 | 321281.0678 | 28.48 | 91.63%
[5 empty] | 28.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19909.5321 | 321471.7345 | 28.49 | 91.63%
[5 empty] | 28.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19921.3406 | 321662.4011 | 28.5 | 91.63%
[5 empty] | 28.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19933.1491 | 321853.0678 | 28.51 | 91.63%
[5 empty] | 28.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19944.9575 | 322043.7345 | 28.52 | 91.63%
[5 empty] | 28.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19956.766 | 322234.4011 | 28.53 | 91.63%
[5 empty] | 28.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19968.5744 | 322425.0678 | 28.54 | 91.63%
[5 empty] | 28.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19980.3829 | 322615.7345 | 28.55 | 91.63%
[5 empty] | 28.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 19992.1913 | 322806.4011 | 28.56 | 91.63%
[5 empty] | 28.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20003.9998 | 322997.0678 | 28.57 | 91.63%
[5 empty] | 28.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20015.8082 | 323187.7345 | 28.58 | 91.63%
[5 empty] | 28.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20027.6167 | 323378.4011 | 28.59 | 91.63%
[5 empty] | 28.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20039.4251 | 323569.0678 | 28.6 | 91.63%
[5 empty] | 28.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20051.2336 | 323759.7345 | 28.61 | 91.63%
[5 empty] | 28.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20063.042 | 323950.4011 | 28.62 | 91.63%
[5 empty] | 28.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20074.8505 | 324141.0678 | 28.63 | 91.63%
[5 empty] | 28.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20086.659 | 324331.7345 | 28.64 | 91.63%
[5 empty] | 28.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20098.4674 | 324522.4011 | 28.65 | 91.63%
[5 empty] | 28.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20110.2759 | 324713.0678 | 28.66 | 91.63%
[5 empty] | 28.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20122.0843 | 324903.7345 | 28.67 | 91.63%
[5 empty] | 28.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20133.8928 | 325094.4011 | 28.68 | 91.63%
[5 empty] | 28.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20145.7012 | 325285.0678 | 28.69 | 91.63%
[5 empty] | 28.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20157.5097 | 325475.7345 | 28.7 | 91.63%
[5 empty] | 28.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20169.3181 | 325666.4011 | 28.71 | 91.63%
[5 empty] | 28.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20181.1266 | 325857.0678 | 28.72 | 91.63%
[5 empty] | 28.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20192.935 | 326047.7345 | 28.73 | 91.63%
[5 empty] | 28.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20204.7435 | 326238.4011 | 28.74 | 91.63%
[5 empty] | 28.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20216.5519 | 326429.0678 | 28.75 | 91.63%
[5 empty] | 28.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20228.3604 | 326619.7345 | 28.76 | 91.63%
[5 empty] | 28.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20240.1689 | 326810.4011 | 28.77 | 91.63%
[5 empty] | 28.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20251.9773 | 327001.0678 | 28.78 | 91.63%
[5 empty] | 28.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20263.7858 | 327191.7345 | 28.79 | 91.63%
[5 empty] | 28.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20275.5942 | 327382.4011 | 28.8 | 91.63%
[5 empty] | 28.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20287.4027 | 327573.0678 | 28.81 | 91.63%
[5 empty] | 28.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20299.2111 | 327763.7345 | 28.82 | 91.63%
[5 empty] | 28.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20311.0196 | 327954.4011 | 28.83 | 91.63%
[5 empty] | 28.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20322.828 | 328145.0678 | 28.84 | 91.63%
[5 empty] | 28.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20334.6365 | 328335.7345 | 28.85 | 91.63%
[5 empty] | 28.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20346.4449 | 328526.4011 | 28.86 | 91.63%
[5 empty] | 28.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20358.2534 | 328717.0678 | 28.87 | 91.63%
[5 empty] | 28.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20370.0618 | 328907.7345 | 28.88 | 91.63%
[5 empty] | 28.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20381.8703 | 329098.4011 | 28.89 | 91.63%
[5 empty] | 28.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20393.6788 | 329289.0678 | 28.9 | 91.63%
[5 empty] | 28.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20405.4872 | 329479.7345 | 28.91 | 91.63%
[5 empty] | 28.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20417.2957 | 329670.4011 | 28.92 | 91.63%
[5 empty] | 28.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20429.1041 | 329861.0678 | 28.93 | 91.63%
[5 empty] | 28.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20440.9126 | 330051.7345 | 28.94 | 91.63%
[5 empty] | 28.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20452.721 | 330242.4011 | 28.95 | 91.63%
[5 empty] | 28.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20464.5295 | 330433.0678 | 28.96 | 91.63%
[5 empty] | 28.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20476.3379 | 330623.7345 | 28.97 | 91.63%
[5 empty] | 28.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20488.1464 | 330814.4011 | 28.98 | 91.63%
[5 empty] | 28.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20499.9548 | 331005.0678 | 28.99 | 91.63%
[5 empty] | 29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20511.7633 | 331195.7345 | 29 | 91.63%
[5 empty] | 29.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20523.5717 | 331386.4011 | 29.01 | 91.63%
[5 empty] | 29.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20535.3802 | 331577.0678 | 29.02 | 91.63%
[5 empty] | 29.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20547.1887 | 331767.7345 | 29.03 | 91.63%
[5 empty] | 29.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20558.9971 | 331958.4011 | 29.04 | 91.63%
[5 empty] | 29.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20570.8056 | 332149.0678 | 29.05 | 91.63%
[5 empty] | 29.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20582.614 | 332339.7345 | 29.06 | 91.63%
[5 empty] | 29.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20594.4225 | 332530.4011 | 29.07 | 91.63%
[5 empty] | 29.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20606.2309 | 332721.0678 | 29.08 | 91.63%
[5 empty] | 29.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20618.0394 | 332911.7345 | 29.09 | 91.63%
[5 empty] | 29.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20629.8478 | 333102.4011 | 29.1 | 91.63%
[5 empty] | 29.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20641.6563 | 333293.0678 | 29.11 | 91.63%
[5 empty] | 29.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20653.4647 | 333483.7345 | 29.12 | 91.63%
[5 empty] | 29.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20665.2732 | 333674.4011 | 29.13 | 91.63%
[5 empty] | 29.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20677.0816 | 333865.0678 | 29.14 | 91.63%
[5 empty] | 29.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20688.8901 | 334055.7345 | 29.15 | 91.63%
[5 empty] | 29.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20700.6986 | 334246.4011 | 29.16 | 91.63%
[5 empty] | 29.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20712.507 | 334437.0678 | 29.17 | 91.63%
[5 empty] | 29.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20724.3155 | 334627.7345 | 29.18 | 91.63%
[5 empty] | 29.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20736.1239 | 334818.4011 | 29.19 | 91.63%
[5 empty] | 29.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20747.9324 | 335009.0678 | 29.2 | 91.63%
[5 empty] | 29.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20759.7408 | 335199.7345 | 29.21 | 91.63%
[5 empty] | 29.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20771.5493 | 335390.4011 | 29.22 | 91.63%
[5 empty] | 29.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20783.3577 | 335581.0678 | 29.23 | 91.63%
[5 empty] | 29.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20795.1662 | 335771.7345 | 29.24 | 91.63%
[5 empty] | 29.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20806.9746 | 335962.4011 | 29.25 | 91.63%
[5 empty] | 29.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20818.7831 | 336153.0678 | 29.26 | 91.63%
[5 empty] | 29.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20830.5915 | 336343.7345 | 29.27 | 91.63%
[5 empty] | 29.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20842.4 | 336534.4011 | 29.28 | 91.63%
[5 empty] | 29.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20854.2085 | 336725.0678 | 29.29 | 91.63%
[5 empty] | 29.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20866.0169 | 336915.7345 | 29.3 | 91.63%
[5 empty] | 29.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20877.8254 | 337106.4011 | 29.31 | 91.63%
[5 empty] | 29.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20889.6338 | 337297.0678 | 29.32 | 91.63%
[5 empty] | 29.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20901.4423 | 337487.7345 | 29.33 | 91.63%
[5 empty] | 29.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20913.2507 | 337678.4011 | 29.34 | 91.63%
[5 empty] | 29.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20925.0592 | 337869.0678 | 29.35 | 91.63%
[5 empty] | 29.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20936.8676 | 338059.7345 | 29.36 | 91.63%
[5 empty] | 29.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20948.6761 | 338250.4011 | 29.37 | 91.63%
[5 empty] | 29.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20960.4845 | 338441.0678 | 29.38 | 91.63%
[5 empty] | 29.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20972.293 | 338631.7345 | 29.39 | 91.63%
[5 empty] | 29.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20984.1014 | 338822.4011 | 29.4 | 91.63%
[5 empty] | 29.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 20995.9099 | 339013.0678 | 29.41 | 91.63%
[5 empty] | 29.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21007.7184 | 339203.7345 | 29.42 | 91.63%
[5 empty] | 29.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21019.5268 | 339394.4011 | 29.43 | 91.63%
[5 empty] | 29.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21031.3353 | 339585.0678 | 29.44 | 91.63%
[5 empty] | 29.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21043.1437 | 339775.7345 | 29.45 | 91.63%
[5 empty] | 29.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21054.9522 | 339966.4011 | 29.46 | 91.63%
[5 empty] | 29.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21066.7606 | 340157.0678 | 29.47 | 91.63%
[5 empty] | 29.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21078.5691 | 340347.7345 | 29.48 | 91.63%
[5 empty] | 29.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21090.3775 | 340538.4011 | 29.49 | 91.63%
[5 empty] | 29.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21102.186 | 340729.0678 | 29.5 | 91.63%
[5 empty] | 29.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21113.9944 | 340919.7345 | 29.51 | 91.63%
[5 empty] | 29.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21125.8029 | 341110.4011 | 29.52 | 91.63%
[5 empty] | 29.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21137.6113 | 341301.0678 | 29.53 | 91.63%
[5 empty] | 29.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21149.4198 | 341491.7345 | 29.54 | 91.63%
[5 empty] | 29.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21161.2283 | 341682.4011 | 29.55 | 91.63%
[5 empty] | 29.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21173.0367 | 341873.0678 | 29.56 | 91.63%
[5 empty] | 29.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21184.8452 | 342063.7345 | 29.57 | 91.63%
[5 empty] | 29.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21196.6536 | 342254.4011 | 29.58 | 91.63%
[5 empty] | 29.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21208.4621 | 342445.0678 | 29.59 | 91.63%
[5 empty] | 29.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21220.2705 | 342635.7345 | 29.6 | 91.63%
[5 empty] | 29.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21232.079 | 342826.4011 | 29.61 | 91.63%
[5 empty] | 29.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21243.8874 | 343017.0678 | 29.62 | 91.63%
[5 empty] | 29.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21255.6959 | 343207.7345 | 29.63 | 91.63%
[5 empty] | 29.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21267.5043 | 343398.4011 | 29.64 | 91.63%
[5 empty] | 29.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21279.3128 | 343589.0678 | 29.65 | 91.63%
[5 empty] | 29.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21291.1212 | 343779.7345 | 29.66 | 91.63%
[5 empty] | 29.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21302.9297 | 343970.4011 | 29.67 | 91.63%
[5 empty] | 29.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21314.7382 | 344161.0678 | 29.68 | 91.63%
[5 empty] | 29.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21326.5466 | 344351.7345 | 29.69 | 91.63%
[5 empty] | 29.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21338.3551 | 344542.4011 | 29.7 | 91.63%
[5 empty] | 29.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21350.1635 | 344733.0678 | 29.71 | 91.63%
[5 empty] | 29.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21361.972 | 344923.7345 | 29.72 | 91.63%
[5 empty] | 29.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21373.7804 | 345114.4011 | 29.73 | 91.63%
[5 empty] | 29.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21385.5889 | 345305.0678 | 29.74 | 91.63%
[5 empty] | 29.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21397.3973 | 345495.7345 | 29.75 | 91.63%
[5 empty] | 29.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21409.2058 | 345686.4011 | 29.76 | 91.63%
[5 empty] | 29.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21421.0142 | 345877.0678 | 29.77 | 91.63%
[5 empty] | 29.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21432.8227 | 346067.7345 | 29.78 | 91.63%
[5 empty] | 29.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21444.6311 | 346258.4011 | 29.79 | 91.63%
[5 empty] | 29.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21456.4396 | 346449.0678 | 29.8 | 91.63%
[5 empty] | 29.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21468.248 | 346639.7345 | 29.81 | 91.63%
[5 empty] | 29.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21480.0565 | 346830.4011 | 29.82 | 91.63%
[5 empty] | 29.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21491.865 | 347021.0678 | 29.83 | 91.63%
[5 empty] | 29.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21503.6734 | 347211.7345 | 29.84 | 91.63%
[5 empty] | 29.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21515.4819 | 347402.4011 | 29.85 | 91.63%
[5 empty] | 29.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21527.2903 | 347593.0678 | 29.86 | 91.63%
[5 empty] | 29.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21539.0988 | 347783.7345 | 29.87 | 91.63%
[5 empty] | 29.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21550.9072 | 347974.4011 | 29.88 | 91.63%
[5 empty] | 29.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21562.7157 | 348165.0678 | 29.89 | 91.63%
[5 empty] | 29.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21574.5241 | 348355.7345 | 29.9 | 91.63%
[5 empty] | 29.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21586.3326 | 348546.4011 | 29.91 | 91.63%
[5 empty] | 29.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21598.141 | 348737.0678 | 29.92 | 91.63%
[5 empty] | 29.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21609.9495 | 348927.7345 | 29.93 | 91.63%
[5 empty] | 29.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21621.7579 | 349118.4011 | 29.94 | 91.63%
[5 empty] | 29.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21633.5664 | 349309.0678 | 29.95 | 91.63%
[5 empty] | 29.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21645.3749 | 349499.7345 | 29.96 | 91.63%
[5 empty] | 29.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21657.1833 | 349690.4011 | 29.97 | 91.63%
[5 empty] | 29.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21668.9918 | 349881.0678 | 29.98 | 91.63%
[5 empty] | 29.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21680.8002 | 350071.7345 | 29.99 | 91.63%
[5 empty] | 30 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21692.6087 | 350262.4011 | 30 | 91.63%
[5 empty] | 30.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21704.4171 | 350453.0678 | 30.01 | 91.63%
[5 empty] | 30.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21716.2256 | 350643.7345 | 30.02 | 91.63%
[5 empty] | 30.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21728.034 | 350834.4011 | 30.03 | 91.63%
[5 empty] | 30.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21739.8425 | 351025.0678 | 30.04 | 91.63%
[5 empty] | 30.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21751.6509 | 351215.7345 | 30.05 | 91.63%
[5 empty] | 30.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21763.4594 | 351406.4011 | 30.06 | 91.63%
[5 empty] | 30.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21775.2678 | 351597.0678 | 30.07 | 91.63%
[5 empty] | 30.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21787.0763 | 351787.7345 | 30.08 | 91.63%
[5 empty] | 30.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21798.8848 | 351978.4011 | 30.09 | 91.63%
[5 empty] | 30.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21810.6932 | 352169.0678 | 30.1 | 91.63%
[5 empty] | 30.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21822.5017 | 352359.7345 | 30.11 | 91.63%
[5 empty] | 30.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21834.3101 | 352550.4011 | 30.12 | 91.63%
[5 empty] | 30.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21846.1186 | 352741.0678 | 30.13 | 91.63%
[5 empty] | 30.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21857.927 | 352931.7345 | 30.14 | 91.63%
[5 empty] | 30.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21869.7355 | 353122.4011 | 30.15 | 91.63%
[5 empty] | 30.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21881.5439 | 353313.0678 | 30.16 | 91.63%
[5 empty] | 30.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21893.3524 | 353503.7345 | 30.17 | 91.63%
[5 empty] | 30.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21905.1608 | 353694.4011 | 30.18 | 91.63%
[5 empty] | 30.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21916.9693 | 353885.0678 | 30.19 | 91.63%
[5 empty] | 30.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21928.7777 | 354075.7345 | 30.2 | 91.63%
[5 empty] | 30.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21940.5862 | 354266.4011 | 30.21 | 91.63%
[5 empty] | 30.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21952.3947 | 354457.0678 | 30.22 | 91.63%
[5 empty] | 30.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21964.2031 | 354647.7345 | 30.23 | 91.63%
[5 empty] | 30.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21976.0116 | 354838.4011 | 30.24 | 91.63%
[5 empty] | 30.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21987.82 | 355029.0678 | 30.25 | 91.63%
[5 empty] | 30.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 21999.6285 | 355219.7345 | 30.26 | 91.63%
[5 empty] | 30.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22011.4369 | 355410.4011 | 30.27 | 91.63%
[5 empty] | 30.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22023.2454 | 355601.0678 | 30.28 | 91.63%
[5 empty] | 30.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22035.0538 | 355791.7345 | 30.29 | 91.63%
[5 empty] | 30.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22046.8623 | 355982.4011 | 30.3 | 91.63%
[5 empty] | 30.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22058.6707 | 356173.0678 | 30.31 | 91.63%
[5 empty] | 30.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22070.4792 | 356363.7345 | 30.32 | 91.63%
[5 empty] | 30.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22082.2876 | 356554.4011 | 30.33 | 91.63%
[5 empty] | 30.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22094.0961 | 356745.0678 | 30.34 | 91.63%
[5 empty] | 30.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22105.9046 | 356935.7345 | 30.35 | 91.63%
[5 empty] | 30.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22117.713 | 357126.4011 | 30.36 | 91.63%
[5 empty] | 30.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22129.5215 | 357317.0678 | 30.37 | 91.63%
[5 empty] | 30.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22141.3299 | 357507.7345 | 30.38 | 91.63%
[5 empty] | 30.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22153.1384 | 357698.4011 | 30.39 | 91.63%
[5 empty] | 30.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22164.9468 | 357889.0678 | 30.4 | 91.63%
[5 empty] | 30.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22176.7553 | 358079.7345 | 30.41 | 91.63%
[5 empty] | 30.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22188.5637 | 358270.4011 | 30.42 | 91.63%
[5 empty] | 30.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22200.3722 | 358461.0678 | 30.43 | 91.63%
[5 empty] | 30.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22212.1806 | 358651.7345 | 30.44 | 91.63%
[5 empty] | 30.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22223.9891 | 358842.4011 | 30.45 | 91.63%
[5 empty] | 30.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22235.7975 | 359033.0678 | 30.46 | 91.63%
[5 empty] | 30.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22247.606 | 359223.7345 | 30.47 | 91.63%
[5 empty] | 30.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22259.4145 | 359414.4011 | 30.48 | 91.63%
[5 empty] | 30.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22271.2229 | 359605.0678 | 30.49 | 91.63%
[5 empty] | 30.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22283.0314 | 359795.7345 | 30.5 | 91.63%
[5 empty] | 30.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22294.8398 | 359986.4011 | 30.51 | 91.63%
[5 empty] | 30.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22306.6483 | 360177.0678 | 30.52 | 91.63%
[5 empty] | 30.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22318.4567 | 360367.7345 | 30.53 | 91.63%
[5 empty] | 30.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22330.2652 | 360558.4011 | 30.54 | 91.63%
[5 empty] | 30.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22342.0736 | 360749.0678 | 30.55 | 91.63%
[5 empty] | 30.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22353.8821 | 360939.7345 | 30.56 | 91.63%
[5 empty] | 30.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22365.6905 | 361130.4011 | 30.57 | 91.63%
[5 empty] | 30.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22377.499 | 361321.0678 | 30.58 | 91.63%
[5 empty] | 30.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22389.3074 | 361511.7345 | 30.59 | 91.63%
[5 empty] | 30.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22401.1159 | 361702.4011 | 30.6 | 91.63%
[5 empty] | 30.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22412.9244 | 361893.0678 | 30.61 | 91.63%
[5 empty] | 30.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22424.7328 | 362083.7345 | 30.62 | 91.63%
[5 empty] | 30.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22436.5413 | 362274.4011 | 30.63 | 91.63%
[5 empty] | 30.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22448.3497 | 362465.0678 | 30.64 | 91.63%
[5 empty] | 30.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22460.1582 | 362655.7345 | 30.65 | 91.63%
[5 empty] | 30.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22471.9666 | 362846.4011 | 30.66 | 91.63%
[5 empty] | 30.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22483.7751 | 363037.0678 | 30.67 | 91.63%
[5 empty] | 30.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22495.5835 | 363227.7345 | 30.68 | 91.63%
[5 empty] | 30.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22507.392 | 363418.4011 | 30.69 | 91.63%
[5 empty] | 30.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22519.2004 | 363609.0678 | 30.7 | 91.63%
[5 empty] | 30.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22531.0089 | 363799.7345 | 30.71 | 91.63%
[5 empty] | 30.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22542.8173 | 363990.4011 | 30.72 | 91.63%
[5 empty] | 30.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22554.6258 | 364181.0678 | 30.73 | 91.63%
[5 empty] | 30.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22566.4343 | 364371.7345 | 30.74 | 91.63%
[5 empty] | 30.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22578.2427 | 364562.4011 | 30.75 | 91.63%
[5 empty] | 30.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22590.0512 | 364753.0678 | 30.76 | 91.63%
[5 empty] | 30.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22601.8596 | 364943.7345 | 30.77 | 91.63%
[5 empty] | 30.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22613.6681 | 365134.4011 | 30.78 | 91.63%
[5 empty] | 30.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22625.4765 | 365325.0678 | 30.79 | 91.63%
[5 empty] | 30.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22637.285 | 365515.7345 | 30.8 | 91.63%
[5 empty] | 30.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22649.0934 | 365706.4011 | 30.81 | 91.63%
[5 empty] | 30.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22660.9019 | 365897.0678 | 30.82 | 91.63%
[5 empty] | 30.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22672.7103 | 366087.7345 | 30.83 | 91.63%
[5 empty] | 30.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22684.5188 | 366278.4011 | 30.84 | 91.63%
[5 empty] | 30.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22696.3272 | 366469.0678 | 30.85 | 91.63%
[5 empty] | 30.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22708.1357 | 366659.7345 | 30.86 | 91.63%
[5 empty] | 30.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22719.9442 | 366850.4011 | 30.87 | 91.63%
[5 empty] | 30.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22731.7526 | 367041.0678 | 30.88 | 91.63%
[5 empty] | 30.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22743.5611 | 367231.7345 | 30.89 | 91.63%
[5 empty] | 30.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22755.3695 | 367422.4011 | 30.9 | 91.63%
[5 empty] | 30.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22767.178 | 367613.0678 | 30.91 | 91.63%
[5 empty] | 30.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22778.9864 | 367803.7345 | 30.92 | 91.63%
[5 empty] | 30.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22790.7949 | 367994.4011 | 30.93 | 91.63%
[5 empty] | 30.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22802.6033 | 368185.0678 | 30.94 | 91.63%
[5 empty] | 30.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22814.4118 | 368375.7345 | 30.95 | 91.63%
[5 empty] | 30.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22826.2202 | 368566.4011 | 30.96 | 91.63%
[5 empty] | 30.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22838.0287 | 368757.0678 | 30.97 | 91.63%
[5 empty] | 30.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22849.8371 | 368947.7345 | 30.98 | 91.63%
[5 empty] | 30.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22861.6456 | 369138.4011 | 30.99 | 91.63%
[5 empty] | 31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22873.4541 | 369329.0678 | 31 | 91.63%
[5 empty] | 31.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22885.2625 | 369519.7345 | 31.01 | 91.63%
[5 empty] | 31.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22897.071 | 369710.4011 | 31.02 | 91.63%
[5 empty] | 31.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22908.8794 | 369901.0678 | 31.03 | 91.63%
[5 empty] | 31.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22920.6879 | 370091.7345 | 31.04 | 91.63%
[5 empty] | 31.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22932.4963 | 370282.4011 | 31.05 | 91.63%
[5 empty] | 31.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22944.3048 | 370473.0678 | 31.06 | 91.63%
[5 empty] | 31.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22956.1132 | 370663.7345 | 31.07 | 91.63%
[5 empty] | 31.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22967.9217 | 370854.4011 | 31.08 | 91.63%
[5 empty] | 31.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22979.7301 | 371045.0678 | 31.09 | 91.63%
[5 empty] | 31.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 22991.5386 | 371235.7345 | 31.1 | 91.63%
[5 empty] | 31.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23003.347 | 371426.4011 | 31.11 | 91.63%
[5 empty] | 31.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23015.1555 | 371617.0678 | 31.12 | 91.63%
[5 empty] | 31.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23026.964 | 371807.7345 | 31.13 | 91.63%
[5 empty] | 31.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23038.7724 | 371998.4011 | 31.14 | 91.63%
[5 empty] | 31.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23050.5809 | 372189.0678 | 31.15 | 91.63%
[5 empty] | 31.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23062.3893 | 372379.7345 | 31.16 | 91.63%
[5 empty] | 31.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23074.1978 | 372570.4011 | 31.17 | 91.63%
[5 empty] | 31.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23086.0062 | 372761.0678 | 31.18 | 91.63%
[5 empty] | 31.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23097.8147 | 372951.7345 | 31.19 | 91.63%
[5 empty] | 31.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23109.6231 | 373142.4011 | 31.2 | 91.63%
[5 empty] | 31.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23121.4316 | 373333.0678 | 31.21 | 91.63%
[5 empty] | 31.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23133.24 | 373523.7345 | 31.22 | 91.63%
[5 empty] | 31.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23145.0485 | 373714.4011 | 31.23 | 91.63%
[5 empty] | 31.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23156.8569 | 373905.0678 | 31.24 | 91.63%
[5 empty] | 31.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23168.6654 | 374095.7345 | 31.25 | 91.63%
[5 empty] | 31.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23180.4739 | 374286.4011 | 31.26 | 91.63%
[5 empty] | 31.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23192.2823 | 374477.0678 | 31.27 | 91.63%
[5 empty] | 31.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23204.0908 | 374667.7345 | 31.28 | 91.63%
[5 empty] | 31.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23215.8992 | 374858.4011 | 31.29 | 91.63%
[5 empty] | 31.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23227.7077 | 375049.0678 | 31.3 | 91.63%
[5 empty] | 31.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23239.5161 | 375239.7345 | 31.31 | 91.63%
[5 empty] | 31.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23251.3246 | 375430.4011 | 31.32 | 91.63%
[5 empty] | 31.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23263.133 | 375621.0678 | 31.33 | 91.63%
[5 empty] | 31.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23274.9415 | 375811.7345 | 31.34 | 91.63%
[5 empty] | 31.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23286.7499 | 376002.4011 | 31.35 | 91.63%
[5 empty] | 31.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23298.5584 | 376193.0678 | 31.36 | 91.63%
[5 empty] | 31.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23310.3668 | 376383.7345 | 31.37 | 91.63%
[5 empty] | 31.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23322.1753 | 376574.4011 | 31.38 | 91.63%
[5 empty] | 31.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23333.9838 | 376765.0678 | 31.39 | 91.63%
[5 empty] | 31.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23345.7922 | 376955.7345 | 31.4 | 91.63%
[5 empty] | 31.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23357.6007 | 377146.4011 | 31.41 | 91.63%
[5 empty] | 31.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23369.4091 | 377337.0678 | 31.42 | 91.63%
[5 empty] | 31.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23381.2176 | 377527.7345 | 31.43 | 91.63%
[5 empty] | 31.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23393.026 | 377718.4011 | 31.44 | 91.63%
[5 empty] | 31.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23404.8345 | 377909.0678 | 31.45 | 91.63%
[5 empty] | 31.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23416.6429 | 378099.7345 | 31.46 | 91.63%
[5 empty] | 31.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23428.4514 | 378290.4011 | 31.47 | 91.63%
[5 empty] | 31.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23440.2598 | 378481.0678 | 31.48 | 91.63%
[5 empty] | 31.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23452.0683 | 378671.7345 | 31.49 | 91.63%
[5 empty] | 31.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23463.8767 | 378862.4011 | 31.5 | 91.63%
[5 empty] | 31.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23475.6852 | 379053.0678 | 31.51 | 91.63%
[5 empty] | 31.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23487.4937 | 379243.7345 | 31.52 | 91.63%
[5 empty] | 31.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23499.3021 | 379434.4011 | 31.53 | 91.63%
[5 empty] | 31.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23511.1106 | 379625.0678 | 31.54 | 91.63%
[5 empty] | 31.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23522.919 | 379815.7345 | 31.55 | 91.63%
[5 empty] | 31.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23534.7275 | 380006.4011 | 31.56 | 91.63%
[5 empty] | 31.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23546.5359 | 380197.0678 | 31.57 | 91.63%
[5 empty] | 31.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23558.3444 | 380387.7345 | 31.58 | 91.63%
[5 empty] | 31.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23570.1528 | 380578.4011 | 31.59 | 91.63%
[5 empty] | 31.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23581.9613 | 380769.0678 | 31.6 | 91.63%
[5 empty] | 31.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23593.7697 | 380959.7345 | 31.61 | 91.63%
[5 empty] | 31.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23605.5782 | 381150.4011 | 31.62 | 91.63%
[5 empty] | 31.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23617.3866 | 381341.0678 | 31.63 | 91.63%
[5 empty] | 31.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23629.1951 | 381531.7345 | 31.64 | 91.63%
[5 empty] | 31.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23641.0036 | 381722.4011 | 31.65 | 91.63%
[5 empty] | 31.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23652.812 | 381913.0678 | 31.66 | 91.63%
[5 empty] | 31.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23664.6205 | 382103.7345 | 31.67 | 91.63%
[5 empty] | 31.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23676.4289 | 382294.4011 | 31.68 | 91.63%
[5 empty] | 31.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23688.2374 | 382485.0678 | 31.69 | 91.63%
[5 empty] | 31.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23700.0458 | 382675.7345 | 31.7 | 91.63%
[5 empty] | 31.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23711.8543 | 382866.4011 | 31.71 | 91.63%
[5 empty] | 31.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23723.6627 | 383057.0678 | 31.72 | 91.63%
[5 empty] | 31.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23735.4712 | 383247.7345 | 31.73 | 91.63%
[5 empty] | 31.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23747.2796 | 383438.4011 | 31.74 | 91.63%
[5 empty] | 31.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23759.0881 | 383629.0678 | 31.75 | 91.63%
[5 empty] | 31.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23770.8965 | 383819.7345 | 31.76 | 91.63%
[5 empty] | 31.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23782.705 | 384010.4011 | 31.77 | 91.63%
[5 empty] | 31.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23794.5135 | 384201.0678 | 31.78 | 91.63%
[5 empty] | 31.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23806.3219 | 384391.7345 | 31.79 | 91.63%
[5 empty] | 31.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23818.1304 | 384582.4011 | 31.8 | 91.63%
[5 empty] | 31.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23829.9388 | 384773.0678 | 31.81 | 91.63%
[5 empty] | 31.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23841.7473 | 384963.7345 | 31.82 | 91.63%
[5 empty] | 31.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23853.5557 | 385154.4011 | 31.83 | 91.63%
[5 empty] | 31.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23865.3642 | 385345.0678 | 31.84 | 91.63%
[5 empty] | 31.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23877.1726 | 385535.7345 | 31.85 | 91.63%
[5 empty] | 31.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23888.9811 | 385726.4011 | 31.86 | 91.63%
[5 empty] | 31.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23900.7895 | 385917.0678 | 31.87 | 91.63%
[5 empty] | 31.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23912.598 | 386107.7345 | 31.88 | 91.63%
[5 empty] | 31.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23924.4064 | 386298.4011 | 31.89 | 91.63%
[5 empty] | 31.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23936.2149 | 386489.0678 | 31.9 | 91.63%
[5 empty] | 31.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23948.0234 | 386679.7345 | 31.91 | 91.63%
[5 empty] | 31.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23959.8318 | 386870.4011 | 31.92 | 91.63%
[5 empty] | 31.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23971.6403 | 387061.0678 | 31.93 | 91.63%
[5 empty] | 31.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23983.4487 | 387251.7345 | 31.94 | 91.63%
[5 empty] | 31.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 23995.2572 | 387442.4011 | 31.95 | 91.63%
[5 empty] | 31.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24007.0656 | 387633.0678 | 31.96 | 91.63%
[5 empty] | 31.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24018.8741 | 387823.7345 | 31.97 | 91.63%
[5 empty] | 31.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24030.6825 | 388014.4011 | 31.98 | 91.63%
[5 empty] | 31.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24042.491 | 388205.0678 | 31.99 | 91.63%
[5 empty] | 32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24054.2994 | 388395.7345 | 32 | 91.63%
[5 empty] | 32.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24066.1079 | 388586.4011 | 32.01 | 91.63%
[5 empty] | 32.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24077.9163 | 388777.0678 | 32.02 | 91.63%
[5 empty] | 32.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24089.7248 | 388967.7345 | 32.03 | 91.63%
[5 empty] | 32.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24101.5333 | 389158.4011 | 32.04 | 91.63%
[5 empty] | 32.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24113.3417 | 389349.0678 | 32.05 | 91.63%
[5 empty] | 32.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24125.1502 | 389539.7345 | 32.06 | 91.63%
[5 empty] | 32.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24136.9586 | 389730.4011 | 32.07 | 91.63%
[5 empty] | 32.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24148.7671 | 389921.0678 | 32.08 | 91.63%
[5 empty] | 32.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24160.5755 | 390111.7345 | 32.09 | 91.63%
[5 empty] | 32.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24172.384 | 390302.4011 | 32.1 | 91.63%
[5 empty] | 32.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24184.1924 | 390493.0678 | 32.11 | 91.63%
[5 empty] | 32.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24196.0009 | 390683.7345 | 32.12 | 91.63%
[5 empty] | 32.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24207.8093 | 390874.4011 | 32.13 | 91.63%
[5 empty] | 32.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24219.6178 | 391065.0678 | 32.14 | 91.63%
[5 empty] | 32.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24231.4262 | 391255.7345 | 32.15 | 91.63%
[5 empty] | 32.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24243.2347 | 391446.4011 | 32.16 | 91.63%
[5 empty] | 32.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24255.0432 | 391637.0678 | 32.17 | 91.63%
[5 empty] | 32.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24266.8516 | 391827.7345 | 32.18 | 91.63%
[5 empty] | 32.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24278.6601 | 392018.4011 | 32.19 | 91.63%
[5 empty] | 32.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24290.4685 | 392209.0678 | 32.2 | 91.63%
[5 empty] | 32.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24302.277 | 392399.7345 | 32.21 | 91.63%
[5 empty] | 32.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24314.0854 | 392590.4011 | 32.22 | 91.63%
[5 empty] | 32.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24325.8939 | 392781.0678 | 32.23 | 91.63%
[5 empty] | 32.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24337.7023 | 392971.7345 | 32.24 | 91.63%
[5 empty] | 32.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24349.5108 | 393162.4011 | 32.25 | 91.63%
[5 empty] | 32.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24361.3192 | 393353.0678 | 32.26 | 91.63%
[5 empty] | 32.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24373.1277 | 393543.7345 | 32.27 | 91.63%
[5 empty] | 32.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24384.9361 | 393734.4011 | 32.28 | 91.63%
[5 empty] | 32.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24396.7446 | 393925.0678 | 32.29 | 91.63%
[5 empty] | 32.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24408.553 | 394115.7345 | 32.3 | 91.63%
[5 empty] | 32.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24420.3615 | 394306.4011 | 32.31 | 91.63%
[5 empty] | 32.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24432.17 | 394497.0678 | 32.32 | 91.63%
[5 empty] | 32.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24443.9784 | 394687.7345 | 32.33 | 91.63%
[5 empty] | 32.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24455.7869 | 394878.4011 | 32.34 | 91.63%
[5 empty] | 32.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24467.5953 | 395069.0678 | 32.35 | 91.63%
[5 empty] | 32.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24479.4038 | 395259.7345 | 32.36 | 91.63%
[5 empty] | 32.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24491.2122 | 395450.4011 | 32.37 | 91.63%
[5 empty] | 32.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24503.0207 | 395641.0678 | 32.38 | 91.63%
[5 empty] | 32.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24514.8291 | 395831.7345 | 32.39 | 91.63%
[5 empty] | 32.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24526.6376 | 396022.4011 | 32.4 | 91.63%
[5 empty] | 32.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24538.446 | 396213.0678 | 32.41 | 91.63%
[5 empty] | 32.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24550.2545 | 396403.7345 | 32.42 | 91.63%
[5 empty] | 32.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24562.0629 | 396594.4011 | 32.43 | 91.63%
[5 empty] | 32.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24573.8714 | 396785.0678 | 32.44 | 91.63%
[5 empty] | 32.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24585.6799 | 396975.7345 | 32.45 | 91.63%
[5 empty] | 32.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24597.4883 | 397166.4011 | 32.46 | 91.63%
[5 empty] | 32.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24609.2968 | 397357.0678 | 32.47 | 91.63%
[5 empty] | 32.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24621.1052 | 397547.7345 | 32.48 | 91.63%
[5 empty] | 32.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24632.9137 | 397738.4011 | 32.49 | 91.63%
[5 empty] | 32.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24644.7221 | 397929.0678 | 32.5 | 91.63%
[5 empty] | 32.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24656.5306 | 398119.7345 | 32.51 | 91.63%
[5 empty] | 32.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24668.339 | 398310.4011 | 32.52 | 91.63%
[5 empty] | 32.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24680.1475 | 398501.0678 | 32.53 | 91.63%
[5 empty] | 32.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24691.9559 | 398691.7345 | 32.54 | 91.63%
[5 empty] | 32.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24703.7644 | 398882.4011 | 32.55 | 91.63%
[5 empty] | 32.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24715.5728 | 399073.0678 | 32.56 | 91.63%
[5 empty] | 32.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24727.3813 | 399263.7345 | 32.57 | 91.63%
[5 empty] | 32.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24739.1898 | 399454.4011 | 32.58 | 91.63%
[5 empty] | 32.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24750.9982 | 399645.0678 | 32.59 | 91.63%
[5 empty] | 32.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24762.8067 | 399835.7345 | 32.6 | 91.63%
[5 empty] | 32.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24774.6151 | 400026.4011 | 32.61 | 91.63%
[5 empty] | 32.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24786.4236 | 400217.0678 | 32.62 | 91.63%
[5 empty] | 32.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24798.232 | 400407.7345 | 32.63 | 91.63%
[5 empty] | 32.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24810.0405 | 400598.4011 | 32.64 | 91.63%
[5 empty] | 32.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24821.8489 | 400789.0678 | 32.65 | 91.63%
[5 empty] | 32.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24833.6574 | 400979.7345 | 32.66 | 91.63%
[5 empty] | 32.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24845.4658 | 401170.4011 | 32.67 | 91.63%
[5 empty] | 32.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24857.2743 | 401361.0678 | 32.68 | 91.63%
[5 empty] | 32.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24869.0827 | 401551.7345 | 32.69 | 91.63%
[5 empty] | 32.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24880.8912 | 401742.4011 | 32.7 | 91.63%
[5 empty] | 32.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24892.6997 | 401933.0678 | 32.71 | 91.63%
[5 empty] | 32.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24904.5081 | 402123.7345 | 32.72 | 91.63%
[5 empty] | 32.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24916.3166 | 402314.4011 | 32.73 | 91.63%
[5 empty] | 32.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24928.125 | 402505.0678 | 32.74 | 91.63%
[5 empty] | 32.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24939.9335 | 402695.7345 | 32.75 | 91.63%
[5 empty] | 32.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24951.7419 | 402886.4011 | 32.76 | 91.63%
[5 empty] | 32.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24963.5504 | 403077.0678 | 32.77 | 91.63%
[5 empty] | 32.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24975.3588 | 403267.7345 | 32.78 | 91.63%
[5 empty] | 32.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24987.1673 | 403458.4011 | 32.79 | 91.63%
[5 empty] | 32.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 24998.9757 | 403649.0678 | 32.8 | 91.63%
[5 empty] | 32.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25010.7842 | 403839.7345 | 32.81 | 91.63%
[5 empty] | 32.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25022.5926 | 404030.4011 | 32.82 | 91.63%
[5 empty] | 32.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25034.4011 | 404221.0678 | 32.83 | 91.63%
[5 empty] | 32.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25046.2096 | 404411.7345 | 32.84 | 91.63%
[5 empty] | 32.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25058.018 | 404602.4011 | 32.85 | 91.63%
[5 empty] | 32.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25069.8265 | 404793.0678 | 32.86 | 91.63%
[5 empty] | 32.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25081.6349 | 404983.7345 | 32.87 | 91.63%
[5 empty] | 32.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25093.4434 | 405174.4011 | 32.88 | 91.63%
[5 empty] | 32.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25105.2518 | 405365.0678 | 32.89 | 91.63%
[5 empty] | 32.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25117.0603 | 405555.7345 | 32.9 | 91.63%
[5 empty] | 32.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25128.8687 | 405746.4011 | 32.91 | 91.63%
[5 empty] | 32.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25140.6772 | 405937.0678 | 32.92 | 91.63%
[5 empty] | 32.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25152.4856 | 406127.7345 | 32.93 | 91.63%
[5 empty] | 32.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25164.2941 | 406318.4011 | 32.94 | 91.63%
[5 empty] | 32.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25176.1025 | 406509.0678 | 32.95 | 91.63%
[5 empty] | 32.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25187.911 | 406699.7345 | 32.96 | 91.63%
[5 empty] | 32.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25199.7195 | 406890.4011 | 32.97 | 91.63%
[5 empty] | 32.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25211.5279 | 407081.0678 | 32.98 | 91.63%
[5 empty] | 32.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25223.3364 | 407271.7345 | 32.99 | 91.63%
[5 empty] | 33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25235.1448 | 407462.4011 | 33 | 91.63%
[5 empty] | 33.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25246.9533 | 407653.0678 | 33.01 | 91.63%
[5 empty] | 33.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25258.7617 | 407843.7345 | 33.02 | 91.63%
[5 empty] | 33.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25270.5702 | 408034.4011 | 33.03 | 91.63%
[5 empty] | 33.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25282.3786 | 408225.0678 | 33.04 | 91.63%
[5 empty] | 33.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25294.1871 | 408415.7345 | 33.05 | 91.63%
[5 empty] | 33.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25305.9955 | 408606.4011 | 33.06 | 91.63%
[5 empty] | 33.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25317.804 | 408797.0678 | 33.07 | 91.63%
[5 empty] | 33.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25329.6124 | 408987.7345 | 33.08 | 91.63%
[5 empty] | 33.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25341.4209 | 409178.4011 | 33.09 | 91.63%
[5 empty] | 33.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25353.2294 | 409369.0678 | 33.1 | 91.63%
[5 empty] | 33.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25365.0378 | 409559.7345 | 33.11 | 91.63%
[5 empty] | 33.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25376.8463 | 409750.4011 | 33.12 | 91.63%
[5 empty] | 33.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25388.6547 | 409941.0678 | 33.13 | 91.63%
[5 empty] | 33.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25400.4632 | 410131.7345 | 33.14 | 91.63%
[5 empty] | 33.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25412.2716 | 410322.4011 | 33.15 | 91.63%
[5 empty] | 33.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25424.0801 | 410513.0678 | 33.16 | 91.63%
[5 empty] | 33.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25435.8885 | 410703.7345 | 33.17 | 91.63%
[5 empty] | 33.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25447.697 | 410894.4011 | 33.18 | 91.63%
[5 empty] | 33.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25459.5054 | 411085.0678 | 33.19 | 91.63%
[5 empty] | 33.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25471.3139 | 411275.7345 | 33.2 | 91.63%
[5 empty] | 33.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25483.1223 | 411466.4011 | 33.21 | 91.63%
[5 empty] | 33.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25494.9308 | 411657.0678 | 33.22 | 91.63%
[5 empty] | 33.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25506.7393 | 411847.7345 | 33.23 | 91.63%
[5 empty] | 33.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25518.5477 | 412038.4011 | 33.24 | 91.63%
[5 empty] | 33.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25530.3562 | 412229.0678 | 33.25 | 91.63%
[5 empty] | 33.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25542.1646 | 412419.7345 | 33.26 | 91.63%
[5 empty] | 33.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25553.9731 | 412610.4011 | 33.27 | 91.63%
[5 empty] | 33.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25565.7815 | 412801.0678 | 33.28 | 91.63%
[5 empty] | 33.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25577.59 | 412991.7345 | 33.29 | 91.63%
[5 empty] | 33.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25589.3984 | 413182.4011 | 33.3 | 91.63%
[5 empty] | 33.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25601.2069 | 413373.0678 | 33.31 | 91.63%
[5 empty] | 33.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25613.0153 | 413563.7345 | 33.32 | 91.63%
[5 empty] | 33.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25624.8238 | 413754.4011 | 33.33 | 91.63%
[5 empty] | 33.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25636.6322 | 413945.0678 | 33.34 | 91.63%
[5 empty] | 33.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25648.4407 | 414135.7345 | 33.35 | 91.63%
[5 empty] | 33.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25660.2492 | 414326.4011 | 33.36 | 91.63%
[5 empty] | 33.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25672.0576 | 414517.0678 | 33.37 | 91.63%
[5 empty] | 33.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25683.8661 | 414707.7345 | 33.38 | 91.63%
[5 empty] | 33.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25695.6745 | 414898.4011 | 33.39 | 91.63%
[5 empty] | 33.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25707.483 | 415089.0678 | 33.4 | 91.63%
[5 empty] | 33.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25719.2914 | 415279.7345 | 33.41 | 91.63%
[5 empty] | 33.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25731.0999 | 415470.4011 | 33.42 | 91.63%
[5 empty] | 33.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25742.9083 | 415661.0678 | 33.43 | 91.63%
[5 empty] | 33.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25754.7168 | 415851.7345 | 33.44 | 91.63%
[5 empty] | 33.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25766.5252 | 416042.4011 | 33.45 | 91.63%
[5 empty] | 33.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25778.3337 | 416233.0678 | 33.46 | 91.63%
[5 empty] | 33.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25790.1421 | 416423.7345 | 33.47 | 91.63%
[5 empty] | 33.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25801.9506 | 416614.4011 | 33.48 | 91.63%
[5 empty] | 33.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25813.7591 | 416805.0678 | 33.49 | 91.63%
[5 empty] | 33.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25825.5675 | 416995.7345 | 33.5 | 91.63%
[5 empty] | 33.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25837.376 | 417186.4011 | 33.51 | 91.63%
[5 empty] | 33.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25849.1844 | 417377.0678 | 33.52 | 91.63%
[5 empty] | 33.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25860.9929 | 417567.7345 | 33.53 | 91.63%
[5 empty] | 33.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25872.8013 | 417758.4011 | 33.54 | 91.63%
[5 empty] | 33.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25884.6098 | 417949.0678 | 33.55 | 91.63%
[5 empty] | 33.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25896.4182 | 418139.7345 | 33.56 | 91.63%
[5 empty] | 33.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25908.2267 | 418330.4011 | 33.57 | 91.63%
[5 empty] | 33.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25920.0351 | 418521.0678 | 33.58 | 91.63%
[5 empty] | 33.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25931.8436 | 418711.7345 | 33.59 | 91.63%
[5 empty] | 33.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25943.652 | 418902.4011 | 33.6 | 91.63%
[5 empty] | 33.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25955.4605 | 419093.0678 | 33.61 | 91.63%
[5 empty] | 33.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25967.269 | 419283.7345 | 33.62 | 91.63%
[5 empty] | 33.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25979.0774 | 419474.4011 | 33.63 | 91.63%
[5 empty] | 33.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 25990.8859 | 419665.0678 | 33.64 | 91.63%
[5 empty] | 33.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26002.6943 | 419855.7345 | 33.65 | 91.63%
[5 empty] | 33.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26014.5028 | 420046.4011 | 33.66 | 91.63%
[5 empty] | 33.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26026.3112 | 420237.0678 | 33.67 | 91.63%
[5 empty] | 33.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26038.1197 | 420427.7345 | 33.68 | 91.63%
[5 empty] | 33.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26049.9281 | 420618.4011 | 33.69 | 91.63%
[5 empty] | 33.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26061.7366 | 420809.0678 | 33.7 | 91.63%
[5 empty] | 33.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26073.545 | 420999.7345 | 33.71 | 91.63%
[5 empty] | 33.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26085.3535 | 421190.4011 | 33.72 | 91.63%
[5 empty] | 33.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26097.1619 | 421381.0678 | 33.73 | 91.63%
[5 empty] | 33.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26108.9704 | 421571.7345 | 33.74 | 91.63%
[5 empty] | 33.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26120.7789 | 421762.4011 | 33.75 | 91.63%
[5 empty] | 33.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26132.5873 | 421953.0678 | 33.76 | 91.63%
[5 empty] | 33.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26144.3958 | 422143.7345 | 33.77 | 91.63%
[5 empty] | 33.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26156.2042 | 422334.4011 | 33.78 | 91.63%
[5 empty] | 33.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26168.0127 | 422525.0678 | 33.79 | 91.63%
[5 empty] | 33.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26179.8211 | 422715.7345 | 33.8 | 91.63%
[5 empty] | 33.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26191.6296 | 422906.4011 | 33.81 | 91.63%
[5 empty] | 33.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26203.438 | 423097.0678 | 33.82 | 91.63%
[5 empty] | 33.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26215.2465 | 423287.7345 | 33.83 | 91.63%
[5 empty] | 33.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26227.0549 | 423478.4011 | 33.84 | 91.63%
[5 empty] | 33.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26238.8634 | 423669.0678 | 33.85 | 91.63%
[5 empty] | 33.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26250.6718 | 423859.7345 | 33.86 | 91.63%
[5 empty] | 33.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26262.4803 | 424050.4011 | 33.87 | 91.63%
[5 empty] | 33.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26274.2888 | 424241.0678 | 33.88 | 91.63%
[5 empty] | 33.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26286.0972 | 424431.7345 | 33.89 | 91.63%
[5 empty] | 33.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26297.9057 | 424622.4011 | 33.9 | 91.63%
[5 empty] | 33.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26309.7141 | 424813.0678 | 33.91 | 91.63%
[5 empty] | 33.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26321.5226 | 425003.7345 | 33.92 | 91.63%
[5 empty] | 33.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26333.331 | 425194.4011 | 33.93 | 91.63%
[5 empty] | 33.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26345.1395 | 425385.0678 | 33.94 | 91.63%
[5 empty] | 33.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26356.9479 | 425575.7345 | 33.95 | 91.63%
[5 empty] | 33.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26368.7564 | 425766.4011 | 33.96 | 91.63%
[5 empty] | 33.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26380.5648 | 425957.0678 | 33.97 | 91.63%
[5 empty] | 33.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26392.3733 | 426147.7345 | 33.98 | 91.63%
[5 empty] | 33.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26404.1817 | 426338.4011 | 33.99 | 91.63%
[5 empty] | 34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26415.9902 | 426529.0678 | 34 | 91.63%
[5 empty] | 34.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26427.7987 | 426719.7345 | 34.01 | 91.63%
[5 empty] | 34.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26439.6071 | 426910.4011 | 34.02 | 91.63%
[5 empty] | 34.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26451.4156 | 427101.0678 | 34.03 | 91.63%
[5 empty] | 34.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26463.224 | 427291.7345 | 34.04 | 91.63%
[5 empty] | 34.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26475.0325 | 427482.4011 | 34.05 | 91.63%
[5 empty] | 34.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26486.8409 | 427673.0678 | 34.06 | 91.63%
[5 empty] | 34.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26498.6494 | 427863.7345 | 34.07 | 91.63%
[5 empty] | 34.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26510.4578 | 428054.4011 | 34.08 | 91.63%
[5 empty] | 34.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26522.2663 | 428245.0678 | 34.09 | 91.63%
[5 empty] | 34.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26534.0747 | 428435.7345 | 34.1 | 91.63%
[5 empty] | 34.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26545.8832 | 428626.4011 | 34.11 | 91.63%
[5 empty] | 34.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26557.6916 | 428817.0678 | 34.12 | 91.63%
[5 empty] | 34.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26569.5001 | 429007.7345 | 34.13 | 91.63%
[5 empty] | 34.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26581.3086 | 429198.4011 | 34.14 | 91.63%
[5 empty] | 34.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26593.117 | 429389.0678 | 34.15 | 91.63%
[5 empty] | 34.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26604.9255 | 429579.7345 | 34.16 | 91.63%
[5 empty] | 34.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26616.7339 | 429770.4011 | 34.17 | 91.63%
[5 empty] | 34.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26628.5424 | 429961.0678 | 34.18 | 91.63%
[5 empty] | 34.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26640.3508 | 430151.7345 | 34.19 | 91.63%
[5 empty] | 34.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26652.1593 | 430342.4011 | 34.2 | 91.63%
[5 empty] | 34.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26663.9677 | 430533.0678 | 34.21 | 91.63%
[5 empty] | 34.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26675.7762 | 430723.7345 | 34.22 | 91.63%
[5 empty] | 34.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26687.5846 | 430914.4011 | 34.23 | 91.63%
[5 empty] | 34.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26699.3931 | 431105.0678 | 34.24 | 91.63%
[5 empty] | 34.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26711.2015 | 431295.7345 | 34.25 | 91.63%
[5 empty] | 34.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26723.01 | 431486.4011 | 34.26 | 91.63%
[5 empty] | 34.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26734.8185 | 431677.0678 | 34.27 | 91.63%
[5 empty] | 34.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26746.6269 | 431867.7345 | 34.28 | 91.63%
[5 empty] | 34.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26758.4354 | 432058.4011 | 34.29 | 91.63%
[5 empty] | 34.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26770.2438 | 432249.0678 | 34.3 | 91.63%
[5 empty] | 34.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26782.0523 | 432439.7345 | 34.31 | 91.63%
[5 empty] | 34.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26793.8607 | 432630.4011 | 34.32 | 91.63%
[5 empty] | 34.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26805.6692 | 432821.0678 | 34.33 | 91.63%
[5 empty] | 34.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26817.4776 | 433011.7345 | 34.34 | 91.63%
[5 empty] | 34.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26829.2861 | 433202.4011 | 34.35 | 91.63%
[5 empty] | 34.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26841.0945 | 433393.0678 | 34.36 | 91.63%
[5 empty] | 34.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26852.903 | 433583.7345 | 34.37 | 91.63%
[5 empty] | 34.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26864.7114 | 433774.4011 | 34.38 | 91.63%
[5 empty] | 34.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26876.5199 | 433965.0678 | 34.39 | 91.63%
[5 empty] | 34.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26888.3284 | 434155.7345 | 34.4 | 91.63%
[5 empty] | 34.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26900.1368 | 434346.4011 | 34.41 | 91.63%
[5 empty] | 34.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26911.9453 | 434537.0678 | 34.42 | 91.63%
[5 empty] | 34.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26923.7537 | 434727.7345 | 34.43 | 91.63%
[5 empty] | 34.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26935.5622 | 434918.4011 | 34.44 | 91.63%
[5 empty] | 34.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26947.3706 | 435109.0678 | 34.45 | 91.63%
[5 empty] | 34.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26959.1791 | 435299.7345 | 34.46 | 91.63%
[5 empty] | 34.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26970.9875 | 435490.4011 | 34.47 | 91.63%
[5 empty] | 34.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26982.796 | 435681.0678 | 34.48 | 91.63%
[5 empty] | 34.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 26994.6044 | 435871.7345 | 34.49 | 91.63%
[5 empty] | 34.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27006.4129 | 436062.4011 | 34.5 | 91.63%
[5 empty] | 34.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27018.2213 | 436253.0678 | 34.51 | 91.63%
[5 empty] | 34.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27030.0298 | 436443.7345 | 34.52 | 91.63%
[5 empty] | 34.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27041.8383 | 436634.4011 | 34.53 | 91.63%
[5 empty] | 34.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27053.6467 | 436825.0678 | 34.54 | 91.63%
[5 empty] | 34.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27065.4552 | 437015.7345 | 34.55 | 91.63%
[5 empty] | 34.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27077.2636 | 437206.4011 | 34.56 | 91.63%
[5 empty] | 34.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27089.0721 | 437397.0678 | 34.57 | 91.63%
[5 empty] | 34.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27100.8805 | 437587.7345 | 34.58 | 91.63%
[5 empty] | 34.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27112.689 | 437778.4011 | 34.59 | 91.63%
[5 empty] | 34.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27124.4974 | 437969.0678 | 34.6 | 91.63%
[5 empty] | 34.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27136.3059 | 438159.7345 | 34.61 | 91.63%
[5 empty] | 34.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27148.1143 | 438350.4011 | 34.62 | 91.63%
[5 empty] | 34.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27159.9228 | 438541.0678 | 34.63 | 91.63%
[5 empty] | 34.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27171.7312 | 438731.7345 | 34.64 | 91.63%
[5 empty] | 34.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27183.5397 | 438922.4011 | 34.65 | 91.63%
[5 empty] | 34.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27195.3482 | 439113.0678 | 34.66 | 91.63%
[5 empty] | 34.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27207.1566 | 439303.7345 | 34.67 | 91.63%
[5 empty] | 34.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27218.9651 | 439494.4011 | 34.68 | 91.63%
[5 empty] | 34.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27230.7735 | 439685.0678 | 34.69 | 91.63%
[5 empty] | 34.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27242.582 | 439875.7345 | 34.7 | 91.63%
[5 empty] | 34.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27254.3904 | 440066.4011 | 34.71 | 91.63%
[5 empty] | 34.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27266.1989 | 440257.0678 | 34.72 | 91.63%
[5 empty] | 34.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27278.0073 | 440447.7345 | 34.73 | 91.63%
[5 empty] | 34.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27289.8158 | 440638.4011 | 34.74 | 91.63%
[5 empty] | 34.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27301.6242 | 440829.0678 | 34.75 | 91.63%
[5 empty] | 34.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27313.4327 | 441019.7345 | 34.76 | 91.63%
[5 empty] | 34.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27325.2411 | 441210.4011 | 34.77 | 91.63%
[5 empty] | 34.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27337.0496 | 441401.0678 | 34.78 | 91.63%
[5 empty] | 34.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27348.858 | 441591.7345 | 34.79 | 91.63%
[5 empty] | 34.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27360.6665 | 441782.4011 | 34.8 | 91.63%
[5 empty] | 34.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27372.475 | 441973.0678 | 34.81 | 91.63%
[5 empty] | 34.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27384.2834 | 442163.7345 | 34.82 | 91.63%
[5 empty] | 34.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27396.0919 | 442354.4011 | 34.83 | 91.63%
[5 empty] | 34.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27407.9003 | 442545.0678 | 34.84 | 91.63%
[5 empty] | 34.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27419.7088 | 442735.7345 | 34.85 | 91.63%
[5 empty] | 34.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27431.5172 | 442926.4011 | 34.86 | 91.63%
[5 empty] | 34.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27443.3257 | 443117.0678 | 34.87 | 91.63%
[5 empty] | 34.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27455.1341 | 443307.7345 | 34.88 | 91.63%
[5 empty] | 34.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27466.9426 | 443498.4011 | 34.89 | 91.63%
[5 empty] | 34.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27478.751 | 443689.0678 | 34.9 | 91.63%
[5 empty] | 34.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27490.5595 | 443879.7345 | 34.91 | 91.63%
[5 empty] | 34.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27502.3679 | 444070.4011 | 34.92 | 91.63%
[5 empty] | 34.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27514.1764 | 444261.0678 | 34.93 | 91.63%
[5 empty] | 34.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27525.9849 | 444451.7345 | 34.94 | 91.63%
[5 empty] | 34.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27537.7933 | 444642.4011 | 34.95 | 91.63%
[5 empty] | 34.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27549.6018 | 444833.0678 | 34.96 | 91.63%
[5 empty] | 34.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27561.4102 | 445023.7345 | 34.97 | 91.63%
[5 empty] | 34.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27573.2187 | 445214.4011 | 34.98 | 91.63%
[5 empty] | 34.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27585.0271 | 445405.0678 | 34.99 | 91.63%
[5 empty] | 35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27596.8356 | 445595.7345 | 35 | 91.63%
[5 empty] | 35.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27608.644 | 445786.4011 | 35.01 | 91.63%
[5 empty] | 35.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27620.4525 | 445977.0678 | 35.02 | 91.63%
[5 empty] | 35.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27632.2609 | 446167.7345 | 35.03 | 91.63%
[5 empty] | 35.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27644.0694 | 446358.4011 | 35.04 | 91.63%
[5 empty] | 35.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27655.8778 | 446549.0678 | 35.05 | 91.63%
[5 empty] | 35.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27667.6863 | 446739.7345 | 35.06 | 91.63%
[5 empty] | 35.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27679.4948 | 446930.4011 | 35.07 | 91.63%
[5 empty] | 35.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27691.3032 | 447121.0678 | 35.08 | 91.63%
[5 empty] | 35.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27703.1117 | 447311.7345 | 35.09 | 91.63%
[5 empty] | 35.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27714.9201 | 447502.4011 | 35.1 | 91.63%
[5 empty] | 35.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27726.7286 | 447693.0678 | 35.11 | 91.63%
[5 empty] | 35.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27738.537 | 447883.7345 | 35.12 | 91.63%
[5 empty] | 35.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27750.3455 | 448074.4011 | 35.13 | 91.63%
[5 empty] | 35.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27762.1539 | 448265.0678 | 35.14 | 91.63%
[5 empty] | 35.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27773.9624 | 448455.7345 | 35.15 | 91.63%
[5 empty] | 35.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27785.7708 | 448646.4011 | 35.16 | 91.63%
[5 empty] | 35.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27797.5793 | 448837.0678 | 35.17 | 91.63%
[5 empty] | 35.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27809.3877 | 449027.7345 | 35.18 | 91.63%
[5 empty] | 35.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27821.1962 | 449218.4011 | 35.19 | 91.63%
[5 empty] | 35.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27833.0047 | 449409.0678 | 35.2 | 91.63%
[5 empty] | 35.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27844.8131 | 449599.7345 | 35.21 | 91.63%
[5 empty] | 35.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27856.6216 | 449790.4011 | 35.22 | 91.63%
[5 empty] | 35.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27868.43 | 449981.0678 | 35.23 | 91.63%
[5 empty] | 35.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27880.2385 | 450171.7345 | 35.24 | 91.63%
[5 empty] | 35.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27892.0469 | 450362.4011 | 35.25 | 91.63%
[5 empty] | 35.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27903.8554 | 450553.0678 | 35.26 | 91.63%
[5 empty] | 35.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27915.6638 | 450743.7345 | 35.27 | 91.63%
[5 empty] | 35.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27927.4723 | 450934.4011 | 35.28 | 91.63%
[5 empty] | 35.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27939.2807 | 451125.0678 | 35.29 | 91.63%
[5 empty] | 35.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27951.0892 | 451315.7345 | 35.3 | 91.63%
[5 empty] | 35.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27962.8976 | 451506.4011 | 35.31 | 91.63%
[5 empty] | 35.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27974.7061 | 451697.0678 | 35.32 | 91.63%
[5 empty] | 35.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27986.5146 | 451887.7345 | 35.33 | 91.63%
[5 empty] | 35.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 27998.323 | 452078.4011 | 35.34 | 91.63%
[5 empty] | 35.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28010.1315 | 452269.0678 | 35.35 | 91.63%
[5 empty] | 35.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28021.9399 | 452459.7345 | 35.36 | 91.63%
[5 empty] | 35.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28033.7484 | 452650.4011 | 35.37 | 91.63%
[5 empty] | 35.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28045.5568 | 452841.0678 | 35.38 | 91.63%
[5 empty] | 35.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28057.3653 | 453031.7345 | 35.39 | 91.63%
[5 empty] | 35.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28069.1737 | 453222.4011 | 35.4 | 91.63%
[5 empty] | 35.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28080.9822 | 453413.0678 | 35.41 | 91.63%
[5 empty] | 35.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28092.7906 | 453603.7345 | 35.42 | 91.63%
[5 empty] | 35.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28104.5991 | 453794.4011 | 35.43 | 91.63%
[5 empty] | 35.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28116.4075 | 453985.0678 | 35.44 | 91.63%
[5 empty] | 35.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28128.216 | 454175.7345 | 35.45 | 91.63%
[5 empty] | 35.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28140.0245 | 454366.4011 | 35.46 | 91.63%
[5 empty] | 35.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28151.8329 | 454557.0678 | 35.47 | 91.63%
[5 empty] | 35.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28163.6414 | 454747.7345 | 35.48 | 91.63%
[5 empty] | 35.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28175.4498 | 454938.4011 | 35.49 | 91.63%
[5 empty] | 35.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28187.2583 | 455129.0678 | 35.5 | 91.63%
[5 empty] | 35.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28199.0667 | 455319.7345 | 35.51 | 91.63%
[5 empty] | 35.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28210.8752 | 455510.4011 | 35.52 | 91.63%
[5 empty] | 35.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28222.6836 | 455701.0678 | 35.53 | 91.63%
[5 empty] | 35.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28234.4921 | 455891.7345 | 35.54 | 91.63%
[5 empty] | 35.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28246.3005 | 456082.4011 | 35.55 | 91.63%
[5 empty] | 35.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28258.109 | 456273.0678 | 35.56 | 91.63%
[5 empty] | 35.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28269.9174 | 456463.7345 | 35.57 | 91.63%
[5 empty] | 35.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28281.7259 | 456654.4011 | 35.58 | 91.63%
[5 empty] | 35.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28293.5344 | 456845.0678 | 35.59 | 91.63%
[5 empty] | 35.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28305.3428 | 457035.7345 | 35.6 | 91.63%
[5 empty] | 35.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28317.1513 | 457226.4011 | 35.61 | 91.63%
[5 empty] | 35.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28328.9597 | 457417.0678 | 35.62 | 91.63%
[5 empty] | 35.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28340.7682 | 457607.7345 | 35.63 | 91.63%
[5 empty] | 35.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28352.5766 | 457798.4011 | 35.64 | 91.63%
[5 empty] | 35.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28364.3851 | 457989.0678 | 35.65 | 91.63%
[5 empty] | 35.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28376.1935 | 458179.7345 | 35.66 | 91.63%
[5 empty] | 35.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28388.002 | 458370.4011 | 35.67 | 91.63%
[5 empty] | 35.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28399.8104 | 458561.0678 | 35.68 | 91.63%
[5 empty] | 35.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28411.6189 | 458751.7345 | 35.69 | 91.63%
[5 empty] | 35.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28423.4273 | 458942.4011 | 35.7 | 91.63%
[5 empty] | 35.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28435.2358 | 459133.0678 | 35.71 | 91.63%
[5 empty] | 35.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28447.0443 | 459323.7345 | 35.72 | 91.63%
[5 empty] | 35.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28458.8527 | 459514.4011 | 35.73 | 91.63%
[5 empty] | 35.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28470.6612 | 459705.0678 | 35.74 | 91.63%
[5 empty] | 35.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28482.4696 | 459895.7345 | 35.75 | 91.63%
[5 empty] | 35.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28494.2781 | 460086.4011 | 35.76 | 91.63%
[5 empty] | 35.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28506.0865 | 460277.0678 | 35.77 | 91.63%
[5 empty] | 35.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28517.895 | 460467.7345 | 35.78 | 91.63%
[5 empty] | 35.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28529.7034 | 460658.4011 | 35.79 | 91.63%
[5 empty] | 35.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28541.5119 | 460849.0678 | 35.8 | 91.63%
[5 empty] | 35.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28553.3203 | 461039.7345 | 35.81 | 91.63%
[5 empty] | 35.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28565.1288 | 461230.4011 | 35.82 | 91.63%
[5 empty] | 35.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28576.9372 | 461421.0678 | 35.83 | 91.63%
[5 empty] | 35.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28588.7457 | 461611.7345 | 35.84 | 91.63%
[5 empty] | 35.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28600.5542 | 461802.4011 | 35.85 | 91.63%
[5 empty] | 35.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28612.3626 | 461993.0678 | 35.86 | 91.63%
[5 empty] | 35.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28624.1711 | 462183.7345 | 35.87 | 91.63%
[5 empty] | 35.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28635.9795 | 462374.4011 | 35.88 | 91.63%
[5 empty] | 35.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28647.788 | 462565.0678 | 35.89 | 91.63%
[5 empty] | 35.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28659.5964 | 462755.7345 | 35.9 | 91.63%
[5 empty] | 35.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28671.4049 | 462946.4011 | 35.91 | 91.63%
[5 empty] | 35.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28683.2133 | 463137.0678 | 35.92 | 91.63%
[5 empty] | 35.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28695.0218 | 463327.7345 | 35.93 | 91.63%
[5 empty] | 35.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28706.8302 | 463518.4011 | 35.94 | 91.63%
[5 empty] | 35.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28718.6387 | 463709.0678 | 35.95 | 91.63%
[5 empty] | 35.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28730.4471 | 463899.7345 | 35.96 | 91.63%
[5 empty] | 35.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28742.2556 | 464090.4011 | 35.97 | 91.63%
[5 empty] | 35.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28754.0641 | 464281.0678 | 35.98 | 91.63%
[5 empty] | 35.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28765.8725 | 464471.7345 | 35.99 | 91.63%
[5 empty] | 36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28777.681 | 464662.4011 | 36 | 91.63%
[5 empty] | 36.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28789.4894 | 464853.0678 | 36.01 | 91.63%
[5 empty] | 36.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28801.2979 | 465043.7345 | 36.02 | 91.63%
[5 empty] | 36.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28813.1063 | 465234.4011 | 36.03 | 91.63%
[5 empty] | 36.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28824.9148 | 465425.0678 | 36.04 | 91.63%
[5 empty] | 36.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28836.7232 | 465615.7345 | 36.05 | 91.63%
[5 empty] | 36.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28848.5317 | 465806.4011 | 36.06 | 91.63%
[5 empty] | 36.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28860.3401 | 465997.0678 | 36.07 | 91.63%
[5 empty] | 36.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28872.1486 | 466187.7345 | 36.08 | 91.63%
[5 empty] | 36.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28883.957 | 466378.4011 | 36.09 | 91.63%
[5 empty] | 36.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28895.7655 | 466569.0678 | 36.1 | 91.63%
[5 empty] | 36.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28907.574 | 466759.7345 | 36.11 | 91.63%
[5 empty] | 36.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28919.3824 | 466950.4011 | 36.12 | 91.63%
[5 empty] | 36.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28931.1909 | 467141.0678 | 36.13 | 91.63%
[5 empty] | 36.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28942.9993 | 467331.7345 | 36.14 | 91.63%
[5 empty] | 36.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28954.8078 | 467522.4011 | 36.15 | 91.63%
[5 empty] | 36.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28966.6162 | 467713.0678 | 36.16 | 91.63%
[5 empty] | 36.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28978.4247 | 467903.7345 | 36.17 | 91.63%
[5 empty] | 36.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 28990.2331 | 468094.4011 | 36.18 | 91.63%
[5 empty] | 36.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29002.0416 | 468285.0678 | 36.19 | 91.63%
[5 empty] | 36.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29013.85 | 468475.7345 | 36.2 | 91.63%
[5 empty] | 36.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29025.6585 | 468666.4011 | 36.21 | 91.63%
[5 empty] | 36.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29037.4669 | 468857.0678 | 36.22 | 91.63%
[5 empty] | 36.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29049.2754 | 469047.7345 | 36.23 | 91.63%
[5 empty] | 36.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29061.0839 | 469238.4011 | 36.24 | 91.63%
[5 empty] | 36.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29072.8923 | 469429.0678 | 36.25 | 91.63%
[5 empty] | 36.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29084.7008 | 469619.7345 | 36.26 | 91.63%
[5 empty] | 36.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29096.5092 | 469810.4011 | 36.27 | 91.63%
[5 empty] | 36.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29108.3177 | 470001.0678 | 36.28 | 91.63%
[5 empty] | 36.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29120.1261 | 470191.7345 | 36.29 | 91.63%
[5 empty] | 36.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29131.9346 | 470382.4011 | 36.3 | 91.63%
[5 empty] | 36.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29143.743 | 470573.0678 | 36.31 | 91.63%
[5 empty] | 36.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29155.5515 | 470763.7345 | 36.32 | 91.63%
[5 empty] | 36.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29167.3599 | 470954.4011 | 36.33 | 91.63%
[5 empty] | 36.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29179.1684 | 471145.0678 | 36.34 | 91.63%
[5 empty] | 36.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29190.9768 | 471335.7345 | 36.35 | 91.63%
[5 empty] | 36.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29202.7853 | 471526.4011 | 36.36 | 91.63%
[5 empty] | 36.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29214.5938 | 471717.0678 | 36.37 | 91.63%
[5 empty] | 36.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29226.4022 | 471907.7345 | 36.38 | 91.63%
[5 empty] | 36.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29238.2107 | 472098.4011 | 36.39 | 91.63%
[5 empty] | 36.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29250.0191 | 472289.0678 | 36.4 | 91.63%
[5 empty] | 36.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29261.8276 | 472479.7345 | 36.41 | 91.63%
[5 empty] | 36.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29273.636 | 472670.4011 | 36.42 | 91.63%
[5 empty] | 36.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29285.4445 | 472861.0678 | 36.43 | 91.63%
[5 empty] | 36.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29297.2529 | 473051.7345 | 36.44 | 91.63%
[5 empty] | 36.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29309.0614 | 473242.4011 | 36.45 | 91.63%
[5 empty] | 36.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29320.8698 | 473433.0678 | 36.46 | 91.63%
[5 empty] | 36.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29332.6783 | 473623.7345 | 36.47 | 91.63%
[5 empty] | 36.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29344.4867 | 473814.4011 | 36.48 | 91.63%
[5 empty] | 36.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29356.2952 | 474005.0678 | 36.49 | 91.63%
[5 empty] | 36.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29368.1037 | 474195.7345 | 36.5 | 91.63%
[5 empty] | 36.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29379.9121 | 474386.4011 | 36.51 | 91.63%
[5 empty] | 36.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29391.7206 | 474577.0678 | 36.52 | 91.63%
[5 empty] | 36.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29403.529 | 474767.7345 | 36.53 | 91.63%
[5 empty] | 36.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29415.3375 | 474958.4011 | 36.54 | 91.63%
[5 empty] | 36.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29427.1459 | 475149.0678 | 36.55 | 91.63%
[5 empty] | 36.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29438.9544 | 475339.7345 | 36.56 | 91.63%
[5 empty] | 36.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29450.7628 | 475530.4011 | 36.57 | 91.63%
[5 empty] | 36.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29462.5713 | 475721.0678 | 36.58 | 91.63%
[5 empty] | 36.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29474.3797 | 475911.7345 | 36.59 | 91.63%
[5 empty] | 36.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29486.1882 | 476102.4011 | 36.6 | 91.63%
[5 empty] | 36.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29497.9966 | 476293.0678 | 36.61 | 91.63%
[5 empty] | 36.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29509.8051 | 476483.7345 | 36.62 | 91.63%
[5 empty] | 36.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29521.6136 | 476674.4011 | 36.63 | 91.63%
[5 empty] | 36.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29533.422 | 476865.0678 | 36.64 | 91.63%
[5 empty] | 36.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29545.2305 | 477055.7345 | 36.65 | 91.63%
[5 empty] | 36.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29557.0389 | 477246.4011 | 36.66 | 91.63%
[5 empty] | 36.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29568.8474 | 477437.0678 | 36.67 | 91.63%
[5 empty] | 36.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29580.6558 | 477627.7345 | 36.68 | 91.63%
[5 empty] | 36.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29592.4643 | 477818.4011 | 36.69 | 91.63%
[5 empty] | 36.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29604.2727 | 478009.0678 | 36.7 | 91.63%
[5 empty] | 36.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29616.0812 | 478199.7345 | 36.71 | 91.63%
[5 empty] | 36.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29627.8896 | 478390.4011 | 36.72 | 91.63%
[5 empty] | 36.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29639.6981 | 478581.0678 | 36.73 | 91.63%
[5 empty] | 36.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29651.5065 | 478771.7345 | 36.74 | 91.63%
[5 empty] | 36.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29663.315 | 478962.4011 | 36.75 | 91.63%
[5 empty] | 36.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29675.1235 | 479153.0678 | 36.76 | 91.63%
[5 empty] | 36.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29686.9319 | 479343.7345 | 36.77 | 91.63%
[5 empty] | 36.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29698.7404 | 479534.4011 | 36.78 | 91.63%
[5 empty] | 36.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29710.5488 | 479725.0678 | 36.79 | 91.63%
[5 empty] | 36.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29722.3573 | 479915.7345 | 36.8 | 91.63%
[5 empty] | 36.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29734.1657 | 480106.4011 | 36.81 | 91.63%
[5 empty] | 36.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29745.9742 | 480297.0678 | 36.82 | 91.63%
[5 empty] | 36.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29757.7826 | 480487.7345 | 36.83 | 91.63%
[5 empty] | 36.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29769.5911 | 480678.4011 | 36.84 | 91.63%
[5 empty] | 36.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29781.3995 | 480869.0678 | 36.85 | 91.63%
[5 empty] | 36.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29793.208 | 481059.7345 | 36.86 | 91.63%
[5 empty] | 36.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29805.0164 | 481250.4011 | 36.87 | 91.63%
[5 empty] | 36.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29816.8249 | 481441.0678 | 36.88 | 91.63%
[5 empty] | 36.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29828.6334 | 481631.7345 | 36.89 | 91.63%
[5 empty] | 36.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29840.4418 | 481822.4011 | 36.9 | 91.63%
[5 empty] | 36.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29852.2503 | 482013.0678 | 36.91 | 91.63%
[5 empty] | 36.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29864.0587 | 482203.7345 | 36.92 | 91.63%
[5 empty] | 36.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29875.8672 | 482394.4011 | 36.93 | 91.63%
[5 empty] | 36.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29887.6756 | 482585.0678 | 36.94 | 91.63%
[5 empty] | 36.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29899.4841 | 482775.7345 | 36.95 | 91.63%
[5 empty] | 36.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29911.2925 | 482966.4011 | 36.96 | 91.63%
[5 empty] | 36.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29923.101 | 483157.0678 | 36.97 | 91.63%
[5 empty] | 36.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29934.9094 | 483347.7345 | 36.98 | 91.63%
[5 empty] | 36.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29946.7179 | 483538.4011 | 36.99 | 91.63%
[5 empty] | 37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29958.5263 | 483729.0678 | 37 | 91.63%
[5 empty] | 37.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29970.3348 | 483919.7345 | 37.01 | 91.63%
[5 empty] | 37.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29982.1433 | 484110.4011 | 37.02 | 91.63%
[5 empty] | 37.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 29993.9517 | 484301.0678 | 37.03 | 91.63%
[5 empty] | 37.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30005.7602 | 484491.7345 | 37.04 | 91.63%
[5 empty] | 37.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30017.5686 | 484682.4011 | 37.05 | 91.63%
[5 empty] | 37.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30029.3771 | 484873.0678 | 37.06 | 91.63%
[5 empty] | 37.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30041.1855 | 485063.7345 | 37.07 | 91.63%
[5 empty] | 37.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30052.994 | 485254.4011 | 37.08 | 91.63%
[5 empty] | 37.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30064.8024 | 485445.0678 | 37.09 | 91.63%
[5 empty] | 37.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30076.6109 | 485635.7345 | 37.1 | 91.63%
[5 empty] | 37.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30088.4193 | 485826.4011 | 37.11 | 91.63%
[5 empty] | 37.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30100.2278 | 486017.0678 | 37.12 | 91.63%
[5 empty] | 37.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30112.0362 | 486207.7345 | 37.13 | 91.63%
[5 empty] | 37.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30123.8447 | 486398.4011 | 37.14 | 91.63%
[5 empty] | 37.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30135.6531 | 486589.0678 | 37.15 | 91.63%
[5 empty] | 37.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30147.4616 | 486779.7345 | 37.16 | 91.63%
[5 empty] | 37.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30159.2701 | 486970.4011 | 37.17 | 91.63%
[5 empty] | 37.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30171.0785 | 487161.0678 | 37.18 | 91.63%
[5 empty] | 37.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30182.887 | 487351.7345 | 37.19 | 91.63%
[5 empty] | 37.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30194.6954 | 487542.4011 | 37.2 | 91.63%
[5 empty] | 37.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30206.5039 | 487733.0678 | 37.21 | 91.63%
[5 empty] | 37.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30218.3123 | 487923.7345 | 37.22 | 91.63%
[5 empty] | 37.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30230.1208 | 488114.4011 | 37.23 | 91.63%
[5 empty] | 37.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30241.9292 | 488305.0678 | 37.24 | 91.63%
[5 empty] | 37.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30253.7377 | 488495.7345 | 37.25 | 91.63%
[5 empty] | 37.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30265.5461 | 488686.4011 | 37.26 | 91.63%
[5 empty] | 37.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30277.3546 | 488877.0678 | 37.27 | 91.63%
[5 empty] | 37.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30289.163 | 489067.7345 | 37.28 | 91.63%
[5 empty] | 37.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30300.9715 | 489258.4011 | 37.29 | 91.63%
[5 empty] | 37.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30312.78 | 489449.0678 | 37.3 | 91.63%
[5 empty] | 37.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30324.5884 | 489639.7345 | 37.31 | 91.63%
[5 empty] | 37.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30336.3969 | 489830.4011 | 37.32 | 91.63%
[5 empty] | 37.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30348.2053 | 490021.0678 | 37.33 | 91.63%
[5 empty] | 37.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30360.0138 | 490211.7345 | 37.34 | 91.63%
[5 empty] | 37.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30371.8222 | 490402.4011 | 37.35 | 91.63%
[5 empty] | 37.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30383.6307 | 490593.0678 | 37.36 | 91.63%
[5 empty] | 37.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30395.4391 | 490783.7345 | 37.37 | 91.63%
[5 empty] | 37.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30407.2476 | 490974.4011 | 37.38 | 91.63%
[5 empty] | 37.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30419.056 | 491165.0678 | 37.39 | 91.63%
[5 empty] | 37.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30430.8645 | 491355.7345 | 37.4 | 91.63%
[5 empty] | 37.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30442.6729 | 491546.4011 | 37.41 | 91.63%
[5 empty] | 37.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30454.4814 | 491737.0678 | 37.42 | 91.63%
[5 empty] | 37.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30466.2899 | 491927.7345 | 37.43 | 91.63%
[5 empty] | 37.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30478.0983 | 492118.4011 | 37.44 | 91.63%
[5 empty] | 37.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30489.9068 | 492309.0678 | 37.45 | 91.63%
[5 empty] | 37.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30501.7152 | 492499.7345 | 37.46 | 91.63%
[5 empty] | 37.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30513.5237 | 492690.4011 | 37.47 | 91.63%
[5 empty] | 37.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30525.3321 | 492881.0678 | 37.48 | 91.63%
[5 empty] | 37.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30537.1406 | 493071.7345 | 37.49 | 91.63%
[5 empty] | 37.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30548.949 | 493262.4011 | 37.5 | 91.63%
[5 empty] | 37.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30560.7575 | 493453.0678 | 37.51 | 91.63%
[5 empty] | 37.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30572.5659 | 493643.7345 | 37.52 | 91.63%
[5 empty] | 37.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30584.3744 | 493834.4011 | 37.53 | 91.63%
[5 empty] | 37.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30596.1828 | 494025.0678 | 37.54 | 91.63%
[5 empty] | 37.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30607.9913 | 494215.7345 | 37.55 | 91.63%
[5 empty] | 37.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30619.7998 | 494406.4011 | 37.56 | 91.63%
[5 empty] | 37.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30631.6082 | 494597.0678 | 37.57 | 91.63%
[5 empty] | 37.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30643.4167 | 494787.7345 | 37.58 | 91.63%
[5 empty] | 37.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30655.2251 | 494978.4011 | 37.59 | 91.63%
[5 empty] | 37.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30667.0336 | 495169.0678 | 37.6 | 91.63%
[5 empty] | 37.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30678.842 | 495359.7345 | 37.61 | 91.63%
[5 empty] | 37.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30690.6505 | 495550.4011 | 37.62 | 91.63%
[5 empty] | 37.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30702.4589 | 495741.0678 | 37.63 | 91.63%
[5 empty] | 37.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30714.2674 | 495931.7345 | 37.64 | 91.63%
[5 empty] | 37.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30726.0758 | 496122.4011 | 37.65 | 91.63%
[5 empty] | 37.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30737.8843 | 496313.0678 | 37.66 | 91.63%
[5 empty] | 37.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30749.6927 | 496503.7345 | 37.67 | 91.63%
[5 empty] | 37.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30761.5012 | 496694.4011 | 37.68 | 91.63%
[5 empty] | 37.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30773.3097 | 496885.0678 | 37.69 | 91.63%
[5 empty] | 37.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30785.1181 | 497075.7345 | 37.7 | 91.63%
[5 empty] | 37.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30796.9266 | 497266.4011 | 37.71 | 91.63%
[5 empty] | 37.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30808.735 | 497457.0678 | 37.72 | 91.63%
[5 empty] | 37.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30820.5435 | 497647.7345 | 37.73 | 91.63%
[5 empty] | 37.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30832.3519 | 497838.4011 | 37.74 | 91.63%
[5 empty] | 37.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30844.1604 | 498029.0678 | 37.75 | 91.63%
[5 empty] | 37.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30855.9688 | 498219.7345 | 37.76 | 91.63%
[5 empty] | 37.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30867.7773 | 498410.4011 | 37.77 | 91.63%
[5 empty] | 37.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30879.5857 | 498601.0678 | 37.78 | 91.63%
[5 empty] | 37.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30891.3942 | 498791.7345 | 37.79 | 91.63%
[5 empty] | 37.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30903.2026 | 498982.4011 | 37.8 | 91.63%
[5 empty] | 37.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30915.0111 | 499173.0678 | 37.81 | 91.63%
[5 empty] | 37.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30926.8196 | 499363.7345 | 37.82 | 91.63%
[5 empty] | 37.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30938.628 | 499554.4011 | 37.83 | 91.63%
[5 empty] | 37.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30950.4365 | 499745.0678 | 37.84 | 91.63%
[5 empty] | 37.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30962.2449 | 499935.7345 | 37.85 | 91.63%
[5 empty] | 37.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30974.0534 | 500126.4011 | 37.86 | 91.63%
[5 empty] | 37.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30985.8618 | 500317.0678 | 37.87 | 91.63%
[5 empty] | 37.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 30997.6703 | 500507.7345 | 37.88 | 91.63%
[5 empty] | 37.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31009.4787 | 500698.4011 | 37.89 | 91.63%
[5 empty] | 37.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31021.2872 | 500889.0678 | 37.9 | 91.63%
[5 empty] | 37.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31033.0956 | 501079.7345 | 37.91 | 91.63%
[5 empty] | 37.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31044.9041 | 501270.4011 | 37.92 | 91.63%
[5 empty] | 37.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31056.7125 | 501461.0678 | 37.93 | 91.63%
[5 empty] | 37.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31068.521 | 501651.7345 | 37.94 | 91.63%
[5 empty] | 37.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31080.3295 | 501842.4011 | 37.95 | 91.63%
[5 empty] | 37.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31092.1379 | 502033.0678 | 37.96 | 91.63%
[5 empty] | 37.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31103.9464 | 502223.7345 | 37.97 | 91.63%
[5 empty] | 37.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31115.7548 | 502414.4011 | 37.98 | 91.63%
[5 empty] | 37.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31127.5633 | 502605.0678 | 37.99 | 91.63%
[5 empty] | 38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31139.3717 | 502795.7345 | 38 | 91.63%
[5 empty] | 38.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31151.1802 | 502986.4011 | 38.01 | 91.63%
[5 empty] | 38.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31162.9886 | 503177.0678 | 38.02 | 91.63%
[5 empty] | 38.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31174.7971 | 503367.7345 | 38.03 | 91.63%
[5 empty] | 38.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31186.6055 | 503558.4011 | 38.04 | 91.63%
[5 empty] | 38.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31198.414 | 503749.0678 | 38.05 | 91.63%
[5 empty] | 38.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31210.2224 | 503939.7345 | 38.06 | 91.63%
[5 empty] | 38.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31222.0309 | 504130.4011 | 38.07 | 91.63%
[5 empty] | 38.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31233.8394 | 504321.0678 | 38.08 | 91.63%
[5 empty] | 38.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31245.6478 | 504511.7345 | 38.09 | 91.63%
[5 empty] | 38.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31257.4563 | 504702.4011 | 38.1 | 91.63%
[5 empty] | 38.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31269.2647 | 504893.0678 | 38.11 | 91.63%
[5 empty] | 38.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31281.0732 | 505083.7345 | 38.12 | 91.63%
[5 empty] | 38.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31292.8816 | 505274.4011 | 38.13 | 91.63%
[5 empty] | 38.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31304.6901 | 505465.0678 | 38.14 | 91.63%
[5 empty] | 38.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31316.4985 | 505655.7345 | 38.15 | 91.63%
[5 empty] | 38.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31328.307 | 505846.4011 | 38.16 | 91.63%
[5 empty] | 38.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31340.1154 | 506037.0678 | 38.17 | 91.63%
[5 empty] | 38.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31351.9239 | 506227.7345 | 38.18 | 91.63%
[5 empty] | 38.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31363.7323 | 506418.4011 | 38.19 | 91.63%
[5 empty] | 38.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31375.5408 | 506609.0678 | 38.2 | 91.63%
[5 empty] | 38.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31387.3493 | 506799.7345 | 38.21 | 91.63%
[5 empty] | 38.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31399.1577 | 506990.4011 | 38.22 | 91.63%
[5 empty] | 38.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31410.9662 | 507181.0678 | 38.23 | 91.63%
[5 empty] | 38.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31422.7746 | 507371.7345 | 38.24 | 91.63%
[5 empty] | 38.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31434.5831 | 507562.4011 | 38.25 | 91.63%
[5 empty] | 38.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31446.3915 | 507753.0678 | 38.26 | 91.63%
[5 empty] | 38.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31458.2 | 507943.7345 | 38.27 | 91.63%
[5 empty] | 38.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31470.0084 | 508134.4011 | 38.28 | 91.63%
[5 empty] | 38.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31481.8169 | 508325.0678 | 38.29 | 91.63%
[5 empty] | 38.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31493.6253 | 508515.7345 | 38.3 | 91.63%
[5 empty] | 38.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31505.4338 | 508706.4011 | 38.31 | 91.63%
[5 empty] | 38.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31517.2422 | 508897.0678 | 38.32 | 91.63%
[5 empty] | 38.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31529.0507 | 509087.7345 | 38.33 | 91.63%
[5 empty] | 38.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31540.8592 | 509278.4011 | 38.34 | 91.63%
[5 empty] | 38.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31552.6676 | 509469.0678 | 38.35 | 91.63%
[5 empty] | 38.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31564.4761 | 509659.7345 | 38.36 | 91.63%
[5 empty] | 38.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31576.2845 | 509850.4011 | 38.37 | 91.63%
[5 empty] | 38.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31588.093 | 510041.0678 | 38.38 | 91.63%
[5 empty] | 38.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31599.9014 | 510231.7345 | 38.39 | 91.63%
[5 empty] | 38.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31611.7099 | 510422.4011 | 38.4 | 91.63%
[5 empty] | 38.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31623.5183 | 510613.0678 | 38.41 | 91.63%
[5 empty] | 38.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31635.3268 | 510803.7345 | 38.42 | 91.63%
[5 empty] | 38.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31647.1352 | 510994.4011 | 38.43 | 91.63%
[5 empty] | 38.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31658.9437 | 511185.0678 | 38.44 | 91.63%
[5 empty] | 38.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31670.7521 | 511375.7345 | 38.45 | 91.63%
[5 empty] | 38.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31682.5606 | 511566.4011 | 38.46 | 91.63%
[5 empty] | 38.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31694.3691 | 511757.0678 | 38.47 | 91.63%
[5 empty] | 38.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31706.1775 | 511947.7345 | 38.48 | 91.63%
[5 empty] | 38.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31717.986 | 512138.4011 | 38.49 | 91.63%
[5 empty] | 38.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31729.7944 | 512329.0678 | 38.5 | 91.63%
[5 empty] | 38.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31741.6029 | 512519.7345 | 38.51 | 91.63%
[5 empty] | 38.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31753.4113 | 512710.4011 | 38.52 | 91.63%
[5 empty] | 38.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31765.2198 | 512901.0678 | 38.53 | 91.63%
[5 empty] | 38.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31777.0282 | 513091.7345 | 38.54 | 91.63%
[5 empty] | 38.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31788.8367 | 513282.4011 | 38.55 | 91.63%
[5 empty] | 38.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31800.6451 | 513473.0678 | 38.56 | 91.63%
[5 empty] | 38.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31812.4536 | 513663.7345 | 38.57 | 91.63%
[5 empty] | 38.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31824.262 | 513854.4011 | 38.58 | 91.63%
[5 empty] | 38.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31836.0705 | 514045.0678 | 38.59 | 91.63%
[5 empty] | 38.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31847.879 | 514235.7345 | 38.6 | 91.63%
[5 empty] | 38.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31859.6874 | 514426.4011 | 38.61 | 91.63%
[5 empty] | 38.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31871.4959 | 514617.0678 | 38.62 | 91.63%
[5 empty] | 38.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31883.3043 | 514807.7345 | 38.63 | 91.63%
[5 empty] | 38.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31895.1128 | 514998.4011 | 38.64 | 91.63%
[5 empty] | 38.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31906.9212 | 515189.0678 | 38.65 | 91.63%
[5 empty] | 38.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31918.7297 | 515379.7345 | 38.66 | 91.63%
[5 empty] | 38.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31930.5381 | 515570.4011 | 38.67 | 91.63%
[5 empty] | 38.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31942.3466 | 515761.0678 | 38.68 | 91.63%
[5 empty] | 38.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31954.155 | 515951.7345 | 38.69 | 91.63%
[5 empty] | 38.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31965.9635 | 516142.4011 | 38.7 | 91.63%
[5 empty] | 38.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31977.7719 | 516333.0678 | 38.71 | 91.63%
[5 empty] | 38.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 31989.5804 | 516523.7345 | 38.72 | 91.63%
[5 empty] | 38.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32001.3889 | 516714.4011 | 38.73 | 91.63%
[5 empty] | 38.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32013.1973 | 516905.0678 | 38.74 | 91.63%
[5 empty] | 38.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32025.0058 | 517095.7345 | 38.75 | 91.63%
[5 empty] | 38.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32036.8142 | 517286.4011 | 38.76 | 91.63%
[5 empty] | 38.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32048.6227 | 517477.0678 | 38.77 | 91.63%
[5 empty] | 38.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32060.4311 | 517667.7345 | 38.78 | 91.63%
[5 empty] | 38.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32072.2396 | 517858.4011 | 38.79 | 91.63%
[5 empty] | 38.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32084.048 | 518049.0678 | 38.8 | 91.63%
[5 empty] | 38.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32095.8565 | 518239.7345 | 38.81 | 91.63%
[5 empty] | 38.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32107.6649 | 518430.4011 | 38.82 | 91.63%
[5 empty] | 38.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32119.4734 | 518621.0678 | 38.83 | 91.63%
[5 empty] | 38.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32131.2818 | 518811.7345 | 38.84 | 91.63%
[5 empty] | 38.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32143.0903 | 519002.4011 | 38.85 | 91.63%
[5 empty] | 38.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32154.8988 | 519193.0678 | 38.86 | 91.63%
[5 empty] | 38.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32166.7072 | 519383.7345 | 38.87 | 91.63%
[5 empty] | 38.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32178.5157 | 519574.4011 | 38.88 | 91.63%
[5 empty] | 38.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32190.3241 | 519765.0678 | 38.89 | 91.63%
[5 empty] | 38.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32202.1326 | 519955.7345 | 38.9 | 91.63%
[5 empty] | 38.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32213.941 | 520146.4011 | 38.91 | 91.63%
[5 empty] | 38.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32225.7495 | 520337.0678 | 38.92 | 91.63%
[5 empty] | 38.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32237.5579 | 520527.7345 | 38.93 | 91.63%
[5 empty] | 38.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32249.3664 | 520718.4011 | 38.94 | 91.63%
[5 empty] | 38.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32261.1748 | 520909.0678 | 38.95 | 91.63%
[5 empty] | 38.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32272.9833 | 521099.7345 | 38.96 | 91.63%
[5 empty] | 38.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32284.7917 | 521290.4011 | 38.97 | 91.63%
[5 empty] | 38.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32296.6002 | 521481.0678 | 38.98 | 91.63%
[5 empty] | 38.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32308.4087 | 521671.7345 | 38.99 | 91.63%
[5 empty] | 39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32320.2171 | 521862.4011 | 39 | 91.63%
[5 empty] | 39.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32332.0256 | 522053.0678 | 39.01 | 91.63%
[5 empty] | 39.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32343.834 | 522243.7345 | 39.02 | 91.63%
[5 empty] | 39.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32355.6425 | 522434.4011 | 39.03 | 91.63%
[5 empty] | 39.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32367.4509 | 522625.0678 | 39.04 | 91.63%
[5 empty] | 39.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32379.2594 | 522815.7345 | 39.05 | 91.63%
[5 empty] | 39.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32391.0678 | 523006.4011 | 39.06 | 91.63%
[5 empty] | 39.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32402.8763 | 523197.0678 | 39.07 | 91.63%
[5 empty] | 39.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32414.6847 | 523387.7345 | 39.08 | 91.63%
[5 empty] | 39.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32426.4932 | 523578.4011 | 39.09 | 91.63%
[5 empty] | 39.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32438.3016 | 523769.0678 | 39.1 | 91.63%
[5 empty] | 39.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32450.1101 | 523959.7345 | 39.11 | 91.63%
[5 empty] | 39.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32461.9186 | 524150.4011 | 39.12 | 91.63%
[5 empty] | 39.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32473.727 | 524341.0678 | 39.13 | 91.63%
[5 empty] | 39.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32485.5355 | 524531.7345 | 39.14 | 91.63%
[5 empty] | 39.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32497.3439 | 524722.4011 | 39.15 | 91.63%
[5 empty] | 39.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32509.1524 | 524913.0678 | 39.16 | 91.63%
[5 empty] | 39.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32520.9608 | 525103.7345 | 39.17 | 91.63%
[5 empty] | 39.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32532.7693 | 525294.4011 | 39.18 | 91.63%
[5 empty] | 39.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32544.5777 | 525485.0678 | 39.19 | 91.63%
[5 empty] | 39.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32556.3862 | 525675.7345 | 39.2 | 91.63%
[5 empty] | 39.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32568.1946 | 525866.4011 | 39.21 | 91.63%
[5 empty] | 39.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32580.0031 | 526057.0678 | 39.22 | 91.63%
[5 empty] | 39.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32591.8115 | 526247.7345 | 39.23 | 91.63%
[5 empty] | 39.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32603.62 | 526438.4011 | 39.24 | 91.63%
[5 empty] | 39.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32615.4285 | 526629.0678 | 39.25 | 91.63%
[5 empty] | 39.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32627.2369 | 526819.7345 | 39.26 | 91.63%
[5 empty] | 39.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32639.0454 | 527010.4011 | 39.27 | 91.63%
[5 empty] | 39.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32650.8538 | 527201.0678 | 39.28 | 91.63%
[5 empty] | 39.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32662.6623 | 527391.7345 | 39.29 | 91.63%
[5 empty] | 39.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32674.4707 | 527582.4011 | 39.3 | 91.63%
[5 empty] | 39.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32686.2792 | 527773.0678 | 39.31 | 91.63%
[5 empty] | 39.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32698.0876 | 527963.7345 | 39.32 | 91.63%
[5 empty] | 39.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32709.8961 | 528154.4011 | 39.33 | 91.63%
[5 empty] | 39.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32721.7045 | 528345.0678 | 39.34 | 91.63%
[5 empty] | 39.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32733.513 | 528535.7345 | 39.35 | 91.63%
[5 empty] | 39.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32745.3214 | 528726.4011 | 39.36 | 91.63%
[5 empty] | 39.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32757.1299 | 528917.0678 | 39.37 | 91.63%
[5 empty] | 39.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32768.9384 | 529107.7345 | 39.38 | 91.63%
[5 empty] | 39.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32780.7468 | 529298.4011 | 39.39 | 91.63%
[5 empty] | 39.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32792.5553 | 529489.0678 | 39.4 | 91.63%
[5 empty] | 39.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32804.3637 | 529679.7345 | 39.41 | 91.63%
[5 empty] | 39.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32816.1722 | 529870.4011 | 39.42 | 91.63%
[5 empty] | 39.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32827.9806 | 530061.0678 | 39.43 | 91.63%
[5 empty] | 39.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32839.7891 | 530251.7345 | 39.44 | 91.63%
[5 empty] | 39.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32851.5975 | 530442.4011 | 39.45 | 91.63%
[5 empty] | 39.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32863.406 | 530633.0678 | 39.46 | 91.63%
[5 empty] | 39.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32875.2144 | 530823.7345 | 39.47 | 91.63%
[5 empty] | 39.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32887.0229 | 531014.4011 | 39.48 | 91.63%
[5 empty] | 39.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32898.8313 | 531205.0678 | 39.49 | 91.63%
[5 empty] | 39.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32910.6398 | 531395.7345 | 39.5 | 91.63%
[5 empty] | 39.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32922.4483 | 531586.4011 | 39.51 | 91.63%
[5 empty] | 39.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32934.2567 | 531777.0678 | 39.52 | 91.63%
[5 empty] | 39.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32946.0652 | 531967.7345 | 39.53 | 91.63%
[5 empty] | 39.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32957.8736 | 532158.4011 | 39.54 | 91.63%
[5 empty] | 39.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32969.6821 | 532349.0678 | 39.55 | 91.63%
[5 empty] | 39.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32981.4905 | 532539.7345 | 39.56 | 91.63%
[5 empty] | 39.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 32993.299 | 532730.4011 | 39.57 | 91.63%
[5 empty] | 39.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33005.1074 | 532921.0678 | 39.58 | 91.63%
[5 empty] | 39.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33016.9159 | 533111.7345 | 39.59 | 91.63%
[5 empty] | 39.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33028.7243 | 533302.4011 | 39.6 | 91.63%
[5 empty] | 39.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33040.5328 | 533493.0678 | 39.61 | 91.63%
[5 empty] | 39.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33052.3412 | 533683.7345 | 39.62 | 91.63%
[5 empty] | 39.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33064.1497 | 533874.4011 | 39.63 | 91.63%
[5 empty] | 39.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33075.9581 | 534065.0678 | 39.64 | 91.63%
[5 empty] | 39.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33087.7666 | 534255.7345 | 39.65 | 91.63%
[5 empty] | 39.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33099.5751 | 534446.4011 | 39.66 | 91.63%
[5 empty] | 39.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33111.3835 | 534637.0678 | 39.67 | 91.63%
[5 empty] | 39.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33123.192 | 534827.7345 | 39.68 | 91.63%
[5 empty] | 39.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33135.0004 | 535018.4011 | 39.69 | 91.63%
[5 empty] | 39.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33146.8089 | 535209.0678 | 39.7 | 91.63%
[5 empty] | 39.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33158.6173 | 535399.7345 | 39.71 | 91.63%
[5 empty] | 39.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33170.4258 | 535590.4011 | 39.72 | 91.63%
[5 empty] | 39.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33182.2342 | 535781.0678 | 39.73 | 91.63%
[5 empty] | 39.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33194.0427 | 535971.7345 | 39.74 | 91.63%
[5 empty] | 39.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33205.8511 | 536162.4011 | 39.75 | 91.63%
[5 empty] | 39.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33217.6596 | 536353.0678 | 39.76 | 91.63%
[5 empty] | 39.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33229.468 | 536543.7345 | 39.77 | 91.63%
[5 empty] | 39.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33241.2765 | 536734.4011 | 39.78 | 91.63%
[5 empty] | 39.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33253.085 | 536925.0678 | 39.79 | 91.63%
[5 empty] | 39.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33264.8934 | 537115.7345 | 39.8 | 91.63%
[5 empty] | 39.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33276.7019 | 537306.4011 | 39.81 | 91.63%
[5 empty] | 39.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33288.5103 | 537497.0678 | 39.82 | 91.63%
[5 empty] | 39.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33300.3188 | 537687.7345 | 39.83 | 91.63%
[5 empty] | 39.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33312.1272 | 537878.4011 | 39.84 | 91.63%
[5 empty] | 39.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33323.9357 | 538069.0678 | 39.85 | 91.63%
[5 empty] | 39.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33335.7441 | 538259.7345 | 39.86 | 91.63%
[5 empty] | 39.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33347.5526 | 538450.4011 | 39.87 | 91.63%
[5 empty] | 39.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33359.361 | 538641.0678 | 39.88 | 91.63%
[5 empty] | 39.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33371.1695 | 538831.7345 | 39.89 | 91.63%
[5 empty] | 39.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33382.9779 | 539022.4011 | 39.9 | 91.63%
[5 empty] | 39.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33394.7864 | 539213.0678 | 39.91 | 91.63%
[5 empty] | 39.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33406.5949 | 539403.7345 | 39.92 | 91.63%
[5 empty] | 39.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33418.4033 | 539594.4011 | 39.93 | 91.63%
[5 empty] | 39.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33430.2118 | 539785.0678 | 39.94 | 91.63%
[5 empty] | 39.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33442.0202 | 539975.7345 | 39.95 | 91.63%
[5 empty] | 39.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33453.8287 | 540166.4011 | 39.96 | 91.63%
[5 empty] | 39.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33465.6371 | 540357.0678 | 39.97 | 91.63%
[5 empty] | 39.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33477.4456 | 540547.7345 | 39.98 | 91.63%
[5 empty] | 39.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33489.254 | 540738.4011 | 39.99 | 91.63%
[5 empty] | 40 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33501.0625 | 540929.0678 | 40 | 91.63%
[5 empty] | 40.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33512.8709 | 541119.7345 | 40.01 | 91.63%
[5 empty] | 40.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33524.6794 | 541310.4011 | 40.02 | 91.63%
[5 empty] | 40.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33536.4878 | 541501.0678 | 40.03 | 91.63%
[5 empty] | 40.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33548.2963 | 541691.7345 | 40.04 | 91.63%
[5 empty] | 40.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33560.1048 | 541882.4011 | 40.05 | 91.63%
[5 empty] | 40.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33571.9132 | 542073.0678 | 40.06 | 91.63%
[5 empty] | 40.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33583.7217 | 542263.7345 | 40.07 | 91.63%
[5 empty] | 40.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33595.5301 | 542454.4011 | 40.08 | 91.63%
[5 empty] | 40.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33607.3386 | 542645.0678 | 40.09 | 91.63%
[5 empty] | 40.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33619.147 | 542835.7345 | 40.1 | 91.63%
[5 empty] | 40.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33630.9555 | 543026.4011 | 40.11 | 91.63%
[5 empty] | 40.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33642.7639 | 543217.0678 | 40.12 | 91.63%
[5 empty] | 40.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33654.5724 | 543407.7345 | 40.13 | 91.63%
[5 empty] | 40.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33666.3808 | 543598.4011 | 40.14 | 91.63%
[5 empty] | 40.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33678.1893 | 543789.0678 | 40.15 | 91.63%
[5 empty] | 40.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33689.9977 | 543979.7345 | 40.16 | 91.63%
[5 empty] | 40.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33701.8062 | 544170.4011 | 40.17 | 91.63%
[5 empty] | 40.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33713.6147 | 544361.0678 | 40.18 | 91.63%
[5 empty] | 40.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33725.4231 | 544551.7345 | 40.19 | 91.63%
[5 empty] | 40.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33737.2316 | 544742.4011 | 40.2 | 91.63%
[5 empty] | 40.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33749.04 | 544933.0678 | 40.21 | 91.63%
[5 empty] | 40.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33760.8485 | 545123.7345 | 40.22 | 91.63%
[5 empty] | 40.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33772.6569 | 545314.4011 | 40.23 | 91.63%
[5 empty] | 40.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33784.4654 | 545505.0678 | 40.24 | 91.63%
[5 empty] | 40.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33796.2738 | 545695.7345 | 40.25 | 91.63%
[5 empty] | 40.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33808.0823 | 545886.4011 | 40.26 | 91.63%
[5 empty] | 40.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33819.8907 | 546077.0678 | 40.27 | 91.63%
[5 empty] | 40.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33831.6992 | 546267.7345 | 40.28 | 91.63%
[5 empty] | 40.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33843.5076 | 546458.4011 | 40.29 | 91.63%
[5 empty] | 40.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33855.3161 | 546649.0678 | 40.3 | 91.63%
[5 empty] | 40.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33867.1246 | 546839.7345 | 40.31 | 91.63%
[5 empty] | 40.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33878.933 | 547030.4011 | 40.32 | 91.63%
[5 empty] | 40.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33890.7415 | 547221.0678 | 40.33 | 91.63%
[5 empty] | 40.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33902.5499 | 547411.7345 | 40.34 | 91.63%
[5 empty] | 40.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33914.3584 | 547602.4011 | 40.35 | 91.63%
[5 empty] | 40.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33926.1668 | 547793.0678 | 40.36 | 91.63%
[5 empty] | 40.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33937.9753 | 547983.7345 | 40.37 | 91.63%
[5 empty] | 40.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33949.7837 | 548174.4011 | 40.38 | 91.63%
[5 empty] | 40.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33961.5922 | 548365.0678 | 40.39 | 91.63%
[5 empty] | 40.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33973.4006 | 548555.7345 | 40.4 | 91.63%
[5 empty] | 40.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33985.2091 | 548746.4011 | 40.41 | 91.63%
[5 empty] | 40.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 33997.0175 | 548937.0678 | 40.42 | 91.63%
[5 empty] | 40.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34008.826 | 549127.7345 | 40.43 | 91.63%
[5 empty] | 40.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34020.6345 | 549318.4011 | 40.44 | 91.63%
[5 empty] | 40.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34032.4429 | 549509.0678 | 40.45 | 91.63%
[5 empty] | 40.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34044.2514 | 549699.7345 | 40.46 | 91.63%
[5 empty] | 40.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34056.0598 | 549890.4011 | 40.47 | 91.63%
[5 empty] | 40.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34067.8683 | 550081.0678 | 40.48 | 91.63%
[5 empty] | 40.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34079.6767 | 550271.7345 | 40.49 | 91.63%
[5 empty] | 40.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34091.4852 | 550462.4011 | 40.5 | 91.63%
[5 empty] | 40.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34103.2936 | 550653.0678 | 40.51 | 91.63%
[5 empty] | 40.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34115.1021 | 550843.7345 | 40.52 | 91.63%
[5 empty] | 40.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34126.9105 | 551034.4011 | 40.53 | 91.63%
[5 empty] | 40.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34138.719 | 551225.0678 | 40.54 | 91.63%
[5 empty] | 40.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34150.5274 | 551415.7345 | 40.55 | 91.63%
[5 empty] | 40.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34162.3359 | 551606.4011 | 40.56 | 91.63%
[5 empty] | 40.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34174.1444 | 551797.0678 | 40.57 | 91.63%
[5 empty] | 40.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34185.9528 | 551987.7345 | 40.58 | 91.63%
[5 empty] | 40.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34197.7613 | 552178.4011 | 40.59 | 91.63%
[5 empty] | 40.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34209.5697 | 552369.0678 | 40.6 | 91.63%
[5 empty] | 40.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34221.3782 | 552559.7345 | 40.61 | 91.63%
[5 empty] | 40.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34233.1866 | 552750.4011 | 40.62 | 91.63%
[5 empty] | 40.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34244.9951 | 552941.0678 | 40.63 | 91.63%
[5 empty] | 40.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34256.8035 | 553131.7345 | 40.64 | 91.63%
[5 empty] | 40.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34268.612 | 553322.4011 | 40.65 | 91.63%
[5 empty] | 40.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34280.4204 | 553513.0678 | 40.66 | 91.63%
[5 empty] | 40.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34292.2289 | 553703.7345 | 40.67 | 91.63%
[5 empty] | 40.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34304.0373 | 553894.4011 | 40.68 | 91.63%
[5 empty] | 40.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34315.8458 | 554085.0678 | 40.69 | 91.63%
[5 empty] | 40.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34327.6543 | 554275.7345 | 40.7 | 91.63%
[5 empty] | 40.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34339.4627 | 554466.4011 | 40.71 | 91.63%
[5 empty] | 40.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34351.2712 | 554657.0678 | 40.72 | 91.63%
[5 empty] | 40.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34363.0796 | 554847.7345 | 40.73 | 91.63%
[5 empty] | 40.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34374.8881 | 555038.4011 | 40.74 | 91.63%
[5 empty] | 40.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34386.6965 | 555229.0678 | 40.75 | 91.63%
[5 empty] | 40.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34398.505 | 555419.7345 | 40.76 | 91.63%
[5 empty] | 40.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34410.3134 | 555610.4011 | 40.77 | 91.63%
[5 empty] | 40.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34422.1219 | 555801.0678 | 40.78 | 91.63%
[5 empty] | 40.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34433.9303 | 555991.7345 | 40.79 | 91.63%
[5 empty] | 40.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34445.7388 | 556182.4011 | 40.8 | 91.63%
[5 empty] | 40.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34457.5472 | 556373.0678 | 40.81 | 91.63%
[5 empty] | 40.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34469.3557 | 556563.7345 | 40.82 | 91.63%
[5 empty] | 40.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34481.1642 | 556754.4011 | 40.83 | 91.63%
[5 empty] | 40.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34492.9726 | 556945.0678 | 40.84 | 91.63%
[5 empty] | 40.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34504.7811 | 557135.7345 | 40.85 | 91.63%
[5 empty] | 40.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34516.5895 | 557326.4011 | 40.86 | 91.63%
[5 empty] | 40.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34528.398 | 557517.0678 | 40.87 | 91.63%
[5 empty] | 40.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34540.2064 | 557707.7345 | 40.88 | 91.63%
[5 empty] | 40.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34552.0149 | 557898.4011 | 40.89 | 91.63%
[5 empty] | 40.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34563.8233 | 558089.0678 | 40.9 | 91.63%
[5 empty] | 40.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34575.6318 | 558279.7345 | 40.91 | 91.63%
[5 empty] | 40.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34587.4402 | 558470.4011 | 40.92 | 91.63%
[5 empty] | 40.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34599.2487 | 558661.0678 | 40.93 | 91.63%
[5 empty] | 40.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34611.0571 | 558851.7345 | 40.94 | 91.63%
[5 empty] | 40.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34622.8656 | 559042.4011 | 40.95 | 91.63%
[5 empty] | 40.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34634.6741 | 559233.0678 | 40.96 | 91.63%
[5 empty] | 40.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34646.4825 | 559423.7345 | 40.97 | 91.63%
[5 empty] | 40.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34658.291 | 559614.4011 | 40.98 | 91.63%
[5 empty] | 40.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34670.0994 | 559805.0678 | 40.99 | 91.63%
[5 empty] | 41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34681.9079 | 559995.7345 | 41 | 91.63%
[5 empty] | 41.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34693.7163 | 560186.4011 | 41.01 | 91.63%
[5 empty] | 41.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34705.5248 | 560377.0678 | 41.02 | 91.63%
[5 empty] | 41.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34717.3332 | 560567.7345 | 41.03 | 91.63%
[5 empty] | 41.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34729.1417 | 560758.4011 | 41.04 | 91.63%
[5 empty] | 41.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34740.9501 | 560949.0678 | 41.05 | 91.63%
[5 empty] | 41.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34752.7586 | 561139.7345 | 41.06 | 91.63%
[5 empty] | 41.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34764.567 | 561330.4011 | 41.07 | 91.63%
[5 empty] | 41.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34776.3755 | 561521.0678 | 41.08 | 91.63%
[5 empty] | 41.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34788.184 | 561711.7345 | 41.09 | 91.63%
[5 empty] | 41.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34799.9924 | 561902.4011 | 41.1 | 91.63%
[5 empty] | 41.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34811.8009 | 562093.0678 | 41.11 | 91.63%
[5 empty] | 41.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34823.6093 | 562283.7345 | 41.12 | 91.63%
[5 empty] | 41.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34835.4178 | 562474.4011 | 41.13 | 91.63%
[5 empty] | 41.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34847.2262 | 562665.0678 | 41.14 | 91.63%
[5 empty] | 41.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34859.0347 | 562855.7345 | 41.15 | 91.63%
[5 empty] | 41.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34870.8431 | 563046.4011 | 41.16 | 91.63%
[5 empty] | 41.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34882.6516 | 563237.0678 | 41.17 | 91.63%
[5 empty] | 41.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34894.46 | 563427.7345 | 41.18 | 91.63%
[5 empty] | 41.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34906.2685 | 563618.4011 | 41.19 | 91.63%
[5 empty] | 41.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34918.0769 | 563809.0678 | 41.2 | 91.63%
[5 empty] | 41.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34929.8854 | 563999.7345 | 41.21 | 91.63%
[5 empty] | 41.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34941.6939 | 564190.4011 | 41.22 | 91.63%
[5 empty] | 41.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34953.5023 | 564381.0678 | 41.23 | 91.63%
[5 empty] | 41.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34965.3108 | 564571.7345 | 41.24 | 91.63%
[5 empty] | 41.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34977.1192 | 564762.4011 | 41.25 | 91.63%
[5 empty] | 41.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 34988.9277 | 564953.0678 | 41.26 | 91.63%
[5 empty] | 41.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35000.7361 | 565143.7345 | 41.27 | 91.63%
[5 empty] | 41.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35012.5446 | 565334.4011 | 41.28 | 91.63%
[5 empty] | 41.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35024.353 | 565525.0678 | 41.29 | 91.63%
[5 empty] | 41.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35036.1615 | 565715.7345 | 41.3 | 91.63%
[5 empty] | 41.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35047.9699 | 565906.4011 | 41.31 | 91.63%
[5 empty] | 41.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35059.7784 | 566097.0678 | 41.32 | 91.63%
[5 empty] | 41.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35071.5868 | 566287.7345 | 41.33 | 91.63%
[5 empty] | 41.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35083.3953 | 566478.4011 | 41.34 | 91.63%
[5 empty] | 41.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35095.2038 | 566669.0678 | 41.35 | 91.63%
[5 empty] | 41.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35107.0122 | 566859.7345 | 41.36 | 91.63%
[5 empty] | 41.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35118.8207 | 567050.4011 | 41.37 | 91.63%
[5 empty] | 41.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35130.6291 | 567241.0678 | 41.38 | 91.63%
[5 empty] | 41.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35142.4376 | 567431.7345 | 41.39 | 91.63%
[5 empty] | 41.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35154.246 | 567622.4011 | 41.4 | 91.63%
[5 empty] | 41.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35166.0545 | 567813.0678 | 41.41 | 91.63%
[5 empty] | 41.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35177.8629 | 568003.7345 | 41.42 | 91.63%
[5 empty] | 41.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35189.6714 | 568194.4011 | 41.43 | 91.63%
[5 empty] | 41.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35201.4798 | 568385.0678 | 41.44 | 91.63%
[5 empty] | 41.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35213.2883 | 568575.7345 | 41.45 | 91.63%
[5 empty] | 41.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35225.0967 | 568766.4011 | 41.46 | 91.63%
[5 empty] | 41.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35236.9052 | 568957.0678 | 41.47 | 91.63%
[5 empty] | 41.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35248.7137 | 569147.7345 | 41.48 | 91.63%
[5 empty] | 41.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35260.5221 | 569338.4011 | 41.49 | 91.63%
[5 empty] | 41.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35272.3306 | 569529.0678 | 41.5 | 91.63%
[5 empty] | 41.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35284.139 | 569719.7345 | 41.51 | 91.63%
[5 empty] | 41.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35295.9475 | 569910.4011 | 41.52 | 91.63%
[5 empty] | 41.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35307.7559 | 570101.0678 | 41.53 | 91.63%
[5 empty] | 41.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35319.5644 | 570291.7345 | 41.54 | 91.63%
[5 empty] | 41.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35331.3728 | 570482.4011 | 41.55 | 91.63%
[5 empty] | 41.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35343.1813 | 570673.0678 | 41.56 | 91.63%
[5 empty] | 41.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35354.9897 | 570863.7345 | 41.57 | 91.63%
[5 empty] | 41.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35366.7982 | 571054.4011 | 41.58 | 91.63%
[5 empty] | 41.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35378.6066 | 571245.0678 | 41.59 | 91.63%
[5 empty] | 41.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35390.4151 | 571435.7345 | 41.6 | 91.63%
[5 empty] | 41.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35402.2236 | 571626.4011 | 41.61 | 91.63%
[5 empty] | 41.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35414.032 | 571817.0678 | 41.62 | 91.63%
[5 empty] | 41.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35425.8405 | 572007.7345 | 41.63 | 91.63%
[5 empty] | 41.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35437.6489 | 572198.4011 | 41.64 | 91.63%
[5 empty] | 41.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35449.4574 | 572389.0678 | 41.65 | 91.63%
[5 empty] | 41.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35461.2658 | 572579.7345 | 41.66 | 91.63%
[5 empty] | 41.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35473.0743 | 572770.4011 | 41.67 | 91.63%
[5 empty] | 41.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35484.8827 | 572961.0678 | 41.68 | 91.63%
[5 empty] | 41.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35496.6912 | 573151.7345 | 41.69 | 91.63%
[5 empty] | 41.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35508.4996 | 573342.4011 | 41.7 | 91.63%
[5 empty] | 41.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35520.3081 | 573533.0678 | 41.71 | 91.63%
[5 empty] | 41.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35532.1165 | 573723.7345 | 41.72 | 91.63%
[5 empty] | 41.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35543.925 | 573914.4011 | 41.73 | 91.63%
[5 empty] | 41.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35555.7335 | 574105.0678 | 41.74 | 91.63%
[5 empty] | 41.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35567.5419 | 574295.7345 | 41.75 | 91.63%
[5 empty] | 41.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35579.3504 | 574486.4011 | 41.76 | 91.63%
[5 empty] | 41.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35591.1588 | 574677.0678 | 41.77 | 91.63%
[5 empty] | 41.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35602.9673 | 574867.7345 | 41.78 | 91.63%
[5 empty] | 41.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35614.7757 | 575058.4011 | 41.79 | 91.63%
[5 empty] | 41.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35626.5842 | 575249.0678 | 41.8 | 91.63%
[5 empty] | 41.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35638.3926 | 575439.7345 | 41.81 | 91.63%
[5 empty] | 41.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35650.2011 | 575630.4011 | 41.82 | 91.63%
[5 empty] | 41.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35662.0095 | 575821.0678 | 41.83 | 91.63%
[5 empty] | 41.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35673.818 | 576011.7345 | 41.84 | 91.63%
[5 empty] | 41.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35685.6264 | 576202.4011 | 41.85 | 91.63%
[5 empty] | 41.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35697.4349 | 576393.0678 | 41.86 | 91.63%
[5 empty] | 41.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35709.2434 | 576583.7345 | 41.87 | 91.63%
[5 empty] | 41.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35721.0518 | 576774.4011 | 41.88 | 91.63%
[5 empty] | 41.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35732.8603 | 576965.0678 | 41.89 | 91.63%
[5 empty] | 41.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35744.6687 | 577155.7345 | 41.9 | 91.63%
[5 empty] | 41.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35756.4772 | 577346.4011 | 41.91 | 91.63%
[5 empty] | 41.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35768.2856 | 577537.0678 | 41.92 | 91.63%
[5 empty] | 41.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35780.0941 | 577727.7345 | 41.93 | 91.63%
[5 empty] | 41.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35791.9025 | 577918.4011 | 41.94 | 91.63%
[5 empty] | 41.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35803.711 | 578109.0678 | 41.95 | 91.63%
[5 empty] | 41.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35815.5194 | 578299.7345 | 41.96 | 91.63%
[5 empty] | 41.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35827.3279 | 578490.4011 | 41.97 | 91.63%
[5 empty] | 41.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35839.1363 | 578681.0678 | 41.98 | 91.63%
[5 empty] | 41.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35850.9448 | 578871.7345 | 41.99 | 91.63%
[5 empty] | 42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35862.7533 | 579062.4011 | 42 | 91.63%
[5 empty] | 42.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35874.5617 | 579253.0678 | 42.01 | 91.63%
[5 empty] | 42.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35886.3702 | 579443.7345 | 42.02 | 91.63%
[5 empty] | 42.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35898.1786 | 579634.4011 | 42.03 | 91.63%
[5 empty] | 42.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35909.9871 | 579825.0678 | 42.04 | 91.63%
[5 empty] | 42.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35921.7955 | 580015.7345 | 42.05 | 91.63%
[5 empty] | 42.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35933.604 | 580206.4011 | 42.06 | 91.63%
[5 empty] | 42.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35945.4124 | 580397.0678 | 42.07 | 91.63%
[5 empty] | 42.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35957.2209 | 580587.7345 | 42.08 | 91.63%
[5 empty] | 42.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35969.0293 | 580778.4011 | 42.09 | 91.63%
[5 empty] | 42.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35980.8378 | 580969.0678 | 42.1 | 91.63%
[5 empty] | 42.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 35992.6462 | 581159.7345 | 42.11 | 91.63%
[5 empty] | 42.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36004.4547 | 581350.4011 | 42.12 | 91.63%
[5 empty] | 42.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36016.2631 | 581541.0678 | 42.13 | 91.63%
[5 empty] | 42.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36028.0716 | 581731.7345 | 42.14 | 91.63%
[5 empty] | 42.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36039.8801 | 581922.4011 | 42.15 | 91.63%
[5 empty] | 42.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36051.6885 | 582113.0678 | 42.16 | 91.63%
[5 empty] | 42.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36063.497 | 582303.7345 | 42.17 | 91.63%
[5 empty] | 42.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36075.3054 | 582494.4011 | 42.18 | 91.63%
[5 empty] | 42.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36087.1139 | 582685.0678 | 42.19 | 91.63%
[5 empty] | 42.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36098.9223 | 582875.7345 | 42.2 | 91.63%
[5 empty] | 42.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36110.7308 | 583066.4011 | 42.21 | 91.63%
[5 empty] | 42.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36122.5392 | 583257.0678 | 42.22 | 91.63%
[5 empty] | 42.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36134.3477 | 583447.7345 | 42.23 | 91.63%
[5 empty] | 42.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36146.1561 | 583638.4011 | 42.24 | 91.63%
[5 empty] | 42.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36157.9646 | 583829.0678 | 42.25 | 91.63%
[5 empty] | 42.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36169.773 | 584019.7345 | 42.26 | 91.63%
[5 empty] | 42.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36181.5815 | 584210.4011 | 42.27 | 91.63%
[5 empty] | 42.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36193.39 | 584401.0678 | 42.28 | 91.63%
[5 empty] | 42.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36205.1984 | 584591.7345 | 42.29 | 91.63%
[5 empty] | 42.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36217.0069 | 584782.4011 | 42.3 | 91.63%
[5 empty] | 42.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36228.8153 | 584973.0678 | 42.31 | 91.63%
[5 empty] | 42.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36240.6238 | 585163.7345 | 42.32 | 91.63%
[5 empty] | 42.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36252.4322 | 585354.4011 | 42.33 | 91.63%
[5 empty] | 42.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36264.2407 | 585545.0678 | 42.34 | 91.63%
[5 empty] | 42.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36276.0491 | 585735.7345 | 42.35 | 91.63%
[5 empty] | 42.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36287.8576 | 585926.4011 | 42.36 | 91.63%
[5 empty] | 42.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36299.666 | 586117.0678 | 42.37 | 91.63%
[5 empty] | 42.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36311.4745 | 586307.7345 | 42.38 | 91.63%
[5 empty] | 42.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36323.2829 | 586498.4011 | 42.39 | 91.63%
[5 empty] | 42.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36335.0914 | 586689.0678 | 42.4 | 91.63%
[5 empty] | 42.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36346.8999 | 586879.7345 | 42.41 | 91.63%
[5 empty] | 42.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36358.7083 | 587070.4011 | 42.42 | 91.63%
[5 empty] | 42.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36370.5168 | 587261.0678 | 42.43 | 91.63%
[5 empty] | 42.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36382.3252 | 587451.7345 | 42.44 | 91.63%
[5 empty] | 42.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36394.1337 | 587642.4011 | 42.45 | 91.63%
[5 empty] | 42.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36405.9421 | 587833.0678 | 42.46 | 91.63%
[5 empty] | 42.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36417.7506 | 588023.7345 | 42.47 | 91.63%
[5 empty] | 42.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36429.559 | 588214.4011 | 42.48 | 91.63%
[5 empty] | 42.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36441.3675 | 588405.0678 | 42.49 | 91.63%
[5 empty] | 42.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36453.1759 | 588595.7345 | 42.5 | 91.63%
[5 empty] | 42.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36464.9844 | 588786.4011 | 42.51 | 91.63%
[5 empty] | 42.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36476.7928 | 588977.0678 | 42.52 | 91.63%
[5 empty] | 42.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36488.6013 | 589167.7345 | 42.53 | 91.63%
[5 empty] | 42.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36500.4098 | 589358.4011 | 42.54 | 91.63%
[5 empty] | 42.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36512.2182 | 589549.0678 | 42.55 | 91.63%
[5 empty] | 42.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36524.0267 | 589739.7345 | 42.56 | 91.63%
[5 empty] | 42.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36535.8351 | 589930.4011 | 42.57 | 91.63%
[5 empty] | 42.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36547.6436 | 590121.0678 | 42.58 | 91.63%
[5 empty] | 42.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36559.452 | 590311.7345 | 42.59 | 91.63%
[5 empty] | 42.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36571.2605 | 590502.4011 | 42.6 | 91.63%
[5 empty] | 42.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36583.0689 | 590693.0678 | 42.61 | 91.63%
[5 empty] | 42.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36594.8774 | 590883.7345 | 42.62 | 91.63%
[5 empty] | 42.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36606.6858 | 591074.4011 | 42.63 | 91.63%
[5 empty] | 42.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36618.4943 | 591265.0678 | 42.64 | 91.63%
[5 empty] | 42.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36630.3027 | 591455.7345 | 42.65 | 91.63%
[5 empty] | 42.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36642.1112 | 591646.4011 | 42.66 | 91.63%
[5 empty] | 42.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36653.9197 | 591837.0678 | 42.67 | 91.63%
[5 empty] | 42.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36665.7281 | 592027.7345 | 42.68 | 91.63%
[5 empty] | 42.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36677.5366 | 592218.4011 | 42.69 | 91.63%
[5 empty] | 42.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36689.345 | 592409.0678 | 42.7 | 91.63%
[5 empty] | 42.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36701.1535 | 592599.7345 | 42.71 | 91.63%
[5 empty] | 42.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36712.9619 | 592790.4011 | 42.72 | 91.63%
[5 empty] | 42.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36724.7704 | 592981.0678 | 42.73 | 91.63%
[5 empty] | 42.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36736.5788 | 593171.7345 | 42.74 | 91.63%
[5 empty] | 42.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36748.3873 | 593362.4011 | 42.75 | 91.63%
[5 empty] | 42.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36760.1957 | 593553.0678 | 42.76 | 91.63%
[5 empty] | 42.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36772.0042 | 593743.7345 | 42.77 | 91.63%
[5 empty] | 42.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36783.8126 | 593934.4011 | 42.78 | 91.63%
[5 empty] | 42.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36795.6211 | 594125.0678 | 42.79 | 91.63%
[5 empty] | 42.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36807.4296 | 594315.7345 | 42.8 | 91.63%
[5 empty] | 42.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36819.238 | 594506.4011 | 42.81 | 91.63%
[5 empty] | 42.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36831.0465 | 594697.0678 | 42.82 | 91.63%
[5 empty] | 42.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36842.8549 | 594887.7345 | 42.83 | 91.63%
[5 empty] | 42.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36854.6634 | 595078.4011 | 42.84 | 91.63%
[5 empty] | 42.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36866.4718 | 595269.0678 | 42.85 | 91.63%
[5 empty] | 42.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36878.2803 | 595459.7345 | 42.86 | 91.63%
[5 empty] | 42.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36890.0887 | 595650.4011 | 42.87 | 91.63%
[5 empty] | 42.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36901.8972 | 595841.0678 | 42.88 | 91.63%
[5 empty] | 42.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36913.7056 | 596031.7345 | 42.89 | 91.63%
[5 empty] | 42.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36925.5141 | 596222.4011 | 42.9 | 91.63%
[5 empty] | 42.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36937.3225 | 596413.0678 | 42.91 | 91.63%
[5 empty] | 42.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36949.131 | 596603.7345 | 42.92 | 91.63%
[5 empty] | 42.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36960.9395 | 596794.4011 | 42.93 | 91.63%
[5 empty] | 42.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36972.7479 | 596985.0678 | 42.94 | 91.63%
[5 empty] | 42.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36984.5564 | 597175.7345 | 42.95 | 91.63%
[5 empty] | 42.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 36996.3648 | 597366.4011 | 42.96 | 91.63%
[5 empty] | 42.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37008.1733 | 597557.0678 | 42.97 | 91.63%
[5 empty] | 42.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37019.9817 | 597747.7345 | 42.98 | 91.63%
[5 empty] | 42.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37031.7902 | 597938.4011 | 42.99 | 91.63%
[5 empty] | 43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37043.5986 | 598129.0678 | 43 | 91.63%
[5 empty] | 43.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37055.4071 | 598319.7345 | 43.01 | 91.63%
[5 empty] | 43.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37067.2155 | 598510.4011 | 43.02 | 91.63%
[5 empty] | 43.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37079.024 | 598701.0678 | 43.03 | 91.63%
[5 empty] | 43.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37090.8324 | 598891.7345 | 43.04 | 91.63%
[5 empty] | 43.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37102.6409 | 599082.4011 | 43.05 | 91.63%
[5 empty] | 43.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37114.4494 | 599273.0678 | 43.06 | 91.63%
[5 empty] | 43.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37126.2578 | 599463.7345 | 43.07 | 91.63%
[5 empty] | 43.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37138.0663 | 599654.4011 | 43.08 | 91.63%
[5 empty] | 43.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37149.8747 | 599845.0678 | 43.09 | 91.63%
[5 empty] | 43.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37161.6832 | 600035.7345 | 43.1 | 91.63%
[5 empty] | 43.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37173.4916 | 600226.4011 | 43.11 | 91.63%
[5 empty] | 43.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37185.3001 | 600417.0678 | 43.12 | 91.63%
[5 empty] | 43.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37197.1085 | 600607.7345 | 43.13 | 91.63%
[5 empty] | 43.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37208.917 | 600798.4011 | 43.14 | 91.63%
[5 empty] | 43.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37220.7254 | 600989.0678 | 43.15 | 91.63%
[5 empty] | 43.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37232.5339 | 601179.7345 | 43.16 | 91.63%
[5 empty] | 43.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37244.3423 | 601370.4011 | 43.17 | 91.63%
[5 empty] | 43.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37256.1508 | 601561.0678 | 43.18 | 91.63%
[5 empty] | 43.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37267.9593 | 601751.7345 | 43.19 | 91.63%
[5 empty] | 43.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37279.7677 | 601942.4011 | 43.2 | 91.63%
[5 empty] | 43.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37291.5762 | 602133.0678 | 43.21 | 91.63%
[5 empty] | 43.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37303.3846 | 602323.7345 | 43.22 | 91.63%
[5 empty] | 43.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37315.1931 | 602514.4011 | 43.23 | 91.63%
[5 empty] | 43.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37327.0015 | 602705.0678 | 43.24 | 91.63%
[5 empty] | 43.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37338.81 | 602895.7345 | 43.25 | 91.63%
[5 empty] | 43.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37350.6184 | 603086.4011 | 43.26 | 91.63%
[5 empty] | 43.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37362.4269 | 603277.0678 | 43.27 | 91.63%
[5 empty] | 43.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37374.2353 | 603467.7345 | 43.28 | 91.63%
[5 empty] | 43.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37386.0438 | 603658.4011 | 43.29 | 91.63%
[5 empty] | 43.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37397.8522 | 603849.0678 | 43.3 | 91.63%
[5 empty] | 43.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37409.6607 | 604039.7345 | 43.31 | 91.63%
[5 empty] | 43.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37421.4692 | 604230.4011 | 43.32 | 91.63%
[5 empty] | 43.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37433.2776 | 604421.0678 | 43.33 | 91.63%
[5 empty] | 43.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37445.0861 | 604611.7345 | 43.34 | 91.63%
[5 empty] | 43.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37456.8945 | 604802.4011 | 43.35 | 91.63%
[5 empty] | 43.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37468.703 | 604993.0678 | 43.36 | 91.63%
[5 empty] | 43.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37480.5114 | 605183.7345 | 43.37 | 91.63%
[5 empty] | 43.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37492.3199 | 605374.4011 | 43.38 | 91.63%
[5 empty] | 43.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37504.1283 | 605565.0678 | 43.39 | 91.63%
[5 empty] | 43.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37515.9368 | 605755.7345 | 43.4 | 91.63%
[5 empty] | 43.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37527.7452 | 605946.4011 | 43.41 | 91.63%
[5 empty] | 43.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37539.5537 | 606137.0678 | 43.42 | 91.63%
[5 empty] | 43.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37551.3621 | 606327.7345 | 43.43 | 91.63%
[5 empty] | 43.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37563.1706 | 606518.4011 | 43.44 | 91.63%
[5 empty] | 43.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37574.9791 | 606709.0678 | 43.45 | 91.63%
[5 empty] | 43.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37586.7875 | 606899.7345 | 43.46 | 91.63%
[5 empty] | 43.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37598.596 | 607090.4011 | 43.47 | 91.63%
[5 empty] | 43.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37610.4044 | 607281.0678 | 43.48 | 91.63%
[5 empty] | 43.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37622.2129 | 607471.7345 | 43.49 | 91.63%
[5 empty] | 43.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37634.0213 | 607662.4011 | 43.5 | 91.63%
[5 empty] | 43.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37645.8298 | 607853.0678 | 43.51 | 91.63%
[5 empty] | 43.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37657.6382 | 608043.7345 | 43.52 | 91.63%
[5 empty] | 43.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37669.4467 | 608234.4011 | 43.53 | 91.63%
[5 empty] | 43.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37681.2551 | 608425.0678 | 43.54 | 91.63%
[5 empty] | 43.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37693.0636 | 608615.7345 | 43.55 | 91.63%
[5 empty] | 43.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37704.872 | 608806.4011 | 43.56 | 91.63%
[5 empty] | 43.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37716.6805 | 608997.0678 | 43.57 | 91.63%
[5 empty] | 43.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37728.489 | 609187.7345 | 43.58 | 91.63%
[5 empty] | 43.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37740.2974 | 609378.4011 | 43.59 | 91.63%
[5 empty] | 43.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37752.1059 | 609569.0678 | 43.6 | 91.63%
[5 empty] | 43.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37763.9143 | 609759.7345 | 43.61 | 91.63%
[5 empty] | 43.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37775.7228 | 609950.4011 | 43.62 | 91.63%
[5 empty] | 43.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37787.5312 | 610141.0678 | 43.63 | 91.63%
[5 empty] | 43.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37799.3397 | 610331.7345 | 43.64 | 91.63%
[5 empty] | 43.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37811.1481 | 610522.4011 | 43.65 | 91.63%
[5 empty] | 43.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37822.9566 | 610713.0678 | 43.66 | 91.63%
[5 empty] | 43.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37834.765 | 610903.7345 | 43.67 | 91.63%
[5 empty] | 43.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37846.5735 | 611094.4011 | 43.68 | 91.63%
[5 empty] | 43.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37858.3819 | 611285.0678 | 43.69 | 91.63%
[5 empty] | 43.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37870.1904 | 611475.7345 | 43.7 | 91.63%
[5 empty] | 43.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37881.9989 | 611666.4011 | 43.71 | 91.63%
[5 empty] | 43.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37893.8073 | 611857.0678 | 43.72 | 91.63%
[5 empty] | 43.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37905.6158 | 612047.7345 | 43.73 | 91.63%
[5 empty] | 43.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37917.4242 | 612238.4011 | 43.74 | 91.63%
[5 empty] | 43.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37929.2327 | 612429.0678 | 43.75 | 91.63%
[5 empty] | 43.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37941.0411 | 612619.7345 | 43.76 | 91.63%
[5 empty] | 43.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37952.8496 | 612810.4011 | 43.77 | 91.63%
[5 empty] | 43.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37964.658 | 613001.0678 | 43.78 | 91.63%
[5 empty] | 43.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37976.4665 | 613191.7345 | 43.79 | 91.63%
[5 empty] | 43.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 37988.2749 | 613382.4011 | 43.8 | 91.63%
[5 empty] | 43.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38000.0834 | 613573.0678 | 43.81 | 91.63%
[5 empty] | 43.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38011.8918 | 613763.7345 | 43.82 | 91.63%
[5 empty] | 43.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38023.7003 | 613954.4011 | 43.83 | 91.63%
[5 empty] | 43.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38035.5088 | 614145.0678 | 43.84 | 91.63%
[5 empty] | 43.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38047.3172 | 614335.7345 | 43.85 | 91.63%
[5 empty] | 43.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38059.1257 | 614526.4011 | 43.86 | 91.63%
[5 empty] | 43.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38070.9341 | 614717.0678 | 43.87 | 91.63%
[5 empty] | 43.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38082.7426 | 614907.7345 | 43.88 | 91.63%
[5 empty] | 43.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38094.551 | 615098.4011 | 43.89 | 91.63%
[5 empty] | 43.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38106.3595 | 615289.0678 | 43.9 | 91.63%
[5 empty] | 43.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38118.1679 | 615479.7345 | 43.91 | 91.63%
[5 empty] | 43.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38129.9764 | 615670.4011 | 43.92 | 91.63%
[5 empty] | 43.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38141.7848 | 615861.0678 | 43.93 | 91.63%
[5 empty] | 43.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38153.5933 | 616051.7345 | 43.94 | 91.63%
[5 empty] | 43.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38165.4017 | 616242.4011 | 43.95 | 91.63%
[5 empty] | 43.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38177.2102 | 616433.0678 | 43.96 | 91.63%
[5 empty] | 43.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38189.0187 | 616623.7345 | 43.97 | 91.63%
[5 empty] | 43.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38200.8271 | 616814.4011 | 43.98 | 91.63%
[5 empty] | 43.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38212.6356 | 617005.0678 | 43.99 | 91.63%
[5 empty] | 44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38224.444 | 617195.7345 | 44 | 91.63%
[5 empty] | 44.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38236.2525 | 617386.4011 | 44.01 | 91.63%
[5 empty] | 44.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38248.0609 | 617577.0678 | 44.02 | 91.63%
[5 empty] | 44.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38259.8694 | 617767.7345 | 44.03 | 91.63%
[5 empty] | 44.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38271.6778 | 617958.4011 | 44.04 | 91.63%
[5 empty] | 44.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38283.4863 | 618149.0678 | 44.05 | 91.63%
[5 empty] | 44.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38295.2947 | 618339.7345 | 44.06 | 91.63%
[5 empty] | 44.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38307.1032 | 618530.4011 | 44.07 | 91.63%
[5 empty] | 44.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38318.9116 | 618721.0678 | 44.08 | 91.63%
[5 empty] | 44.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38330.7201 | 618911.7345 | 44.09 | 91.63%
[5 empty] | 44.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38342.5286 | 619102.4011 | 44.1 | 91.63%
[5 empty] | 44.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38354.337 | 619293.0678 | 44.11 | 91.63%
[5 empty] | 44.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38366.1455 | 619483.7345 | 44.12 | 91.63%
[5 empty] | 44.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38377.9539 | 619674.4011 | 44.13 | 91.63%
[5 empty] | 44.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38389.7624 | 619865.0678 | 44.14 | 91.63%
[5 empty] | 44.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38401.5708 | 620055.7345 | 44.15 | 91.63%
[5 empty] | 44.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38413.3793 | 620246.4011 | 44.16 | 91.63%
[5 empty] | 44.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38425.1877 | 620437.0678 | 44.17 | 91.63%
[5 empty] | 44.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38436.9962 | 620627.7345 | 44.18 | 91.63%
[5 empty] | 44.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38448.8046 | 620818.4011 | 44.19 | 91.63%
[5 empty] | 44.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38460.6131 | 621009.0678 | 44.2 | 91.63%
[5 empty] | 44.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38472.4215 | 621199.7345 | 44.21 | 91.63%
[5 empty] | 44.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38484.23 | 621390.4011 | 44.22 | 91.63%
[5 empty] | 44.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38496.0385 | 621581.0678 | 44.23 | 91.63%
[5 empty] | 44.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38507.8469 | 621771.7345 | 44.24 | 91.63%
[5 empty] | 44.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38519.6554 | 621962.4011 | 44.25 | 91.63%
[5 empty] | 44.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38531.4638 | 622153.0678 | 44.26 | 91.63%
[5 empty] | 44.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38543.2723 | 622343.7345 | 44.27 | 91.63%
[5 empty] | 44.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38555.0807 | 622534.4011 | 44.28 | 91.63%
[5 empty] | 44.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38566.8892 | 622725.0678 | 44.29 | 91.63%
[5 empty] | 44.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38578.6976 | 622915.7345 | 44.3 | 91.63%
[5 empty] | 44.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38590.5061 | 623106.4011 | 44.31 | 91.63%
[5 empty] | 44.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38602.3145 | 623297.0678 | 44.32 | 91.63%
[5 empty] | 44.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38614.123 | 623487.7345 | 44.33 | 91.63%
[5 empty] | 44.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38625.9314 | 623678.4011 | 44.34 | 91.63%
[5 empty] | 44.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38637.7399 | 623869.0678 | 44.35 | 91.63%
[5 empty] | 44.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38649.5484 | 624059.7345 | 44.36 | 91.63%
[5 empty] | 44.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38661.3568 | 624250.4011 | 44.37 | 91.63%
[5 empty] | 44.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38673.1653 | 624441.0678 | 44.38 | 91.63%
[5 empty] | 44.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38684.9737 | 624631.7345 | 44.39 | 91.63%
[5 empty] | 44.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38696.7822 | 624822.4011 | 44.4 | 91.63%
[5 empty] | 44.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38708.5906 | 625013.0678 | 44.41 | 91.63%
[5 empty] | 44.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38720.3991 | 625203.7345 | 44.42 | 91.63%
[5 empty] | 44.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38732.2075 | 625394.4011 | 44.43 | 91.63%
[5 empty] | 44.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38744.016 | 625585.0678 | 44.44 | 91.63%
[5 empty] | 44.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38755.8244 | 625775.7345 | 44.45 | 91.63%
[5 empty] | 44.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38767.6329 | 625966.4011 | 44.46 | 91.63%
[5 empty] | 44.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38779.4413 | 626157.0678 | 44.47 | 91.63%
[5 empty] | 44.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38791.2498 | 626347.7345 | 44.48 | 91.63%
[5 empty] | 44.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38803.0583 | 626538.4011 | 44.49 | 91.63%
[5 empty] | 44.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38814.8667 | 626729.0678 | 44.5 | 91.63%
[5 empty] | 44.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38826.6752 | 626919.7345 | 44.51 | 91.63%
[5 empty] | 44.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38838.4836 | 627110.4011 | 44.52 | 91.63%
[5 empty] | 44.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38850.2921 | 627301.0678 | 44.53 | 91.63%
[5 empty] | 44.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38862.1005 | 627491.7345 | 44.54 | 91.63%
[5 empty] | 44.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38873.909 | 627682.4011 | 44.55 | 91.63%
[5 empty] | 44.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38885.7174 | 627873.0678 | 44.56 | 91.63%
[5 empty] | 44.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38897.5259 | 628063.7345 | 44.57 | 91.63%
[5 empty] | 44.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38909.3343 | 628254.4011 | 44.58 | 91.63%
[5 empty] | 44.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38921.1428 | 628445.0678 | 44.59 | 91.63%
[5 empty] | 44.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38932.9512 | 628635.7345 | 44.6 | 91.63%
[5 empty] | 44.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38944.7597 | 628826.4011 | 44.61 | 91.63%
[5 empty] | 44.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38956.5681 | 629017.0678 | 44.62 | 91.63%
[5 empty] | 44.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38968.3766 | 629207.7345 | 44.63 | 91.63%
[5 empty] | 44.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38980.1851 | 629398.4011 | 44.64 | 91.63%
[5 empty] | 44.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 38991.9935 | 629589.0678 | 44.65 | 91.63%
[5 empty] | 44.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39003.802 | 629779.7345 | 44.66 | 91.63%
[5 empty] | 44.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39015.6104 | 629970.4011 | 44.67 | 91.63%
[5 empty] | 44.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39027.4189 | 630161.0678 | 44.68 | 91.63%
[5 empty] | 44.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39039.2273 | 630351.7345 | 44.69 | 91.63%
[5 empty] | 44.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39051.0358 | 630542.4011 | 44.7 | 91.63%
[5 empty] | 44.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39062.8442 | 630733.0678 | 44.71 | 91.63%
[5 empty] | 44.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39074.6527 | 630923.7345 | 44.72 | 91.63%
[5 empty] | 44.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39086.4611 | 631114.4011 | 44.73 | 91.63%
[5 empty] | 44.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39098.2696 | 631305.0678 | 44.74 | 91.63%
[5 empty] | 44.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39110.078 | 631495.7345 | 44.75 | 91.63%
[5 empty] | 44.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39121.8865 | 631686.4011 | 44.76 | 91.63%
[5 empty] | 44.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39133.695 | 631877.0678 | 44.77 | 91.63%
[5 empty] | 44.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39145.5034 | 632067.7345 | 44.78 | 91.63%
[5 empty] | 44.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39157.3119 | 632258.4011 | 44.79 | 91.63%
[5 empty] | 44.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39169.1203 | 632449.0678 | 44.8 | 91.63%
[5 empty] | 44.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39180.9288 | 632639.7345 | 44.81 | 91.63%
[5 empty] | 44.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39192.7372 | 632830.4011 | 44.82 | 91.63%
[5 empty] | 44.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39204.5457 | 633021.0678 | 44.83 | 91.63%
[5 empty] | 44.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39216.3541 | 633211.7345 | 44.84 | 91.63%
[5 empty] | 44.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39228.1626 | 633402.4011 | 44.85 | 91.63%
[5 empty] | 44.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39239.971 | 633593.0678 | 44.86 | 91.63%
[5 empty] | 44.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39251.7795 | 633783.7345 | 44.87 | 91.63%
[5 empty] | 44.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39263.5879 | 633974.4011 | 44.88 | 91.63%
[5 empty] | 44.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39275.3964 | 634165.0678 | 44.89 | 91.63%
[5 empty] | 44.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39287.2049 | 634355.7345 | 44.9 | 91.63%
[5 empty] | 44.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39299.0133 | 634546.4011 | 44.91 | 91.63%
[5 empty] | 44.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39310.8218 | 634737.0678 | 44.92 | 91.63%
[5 empty] | 44.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39322.6302 | 634927.7345 | 44.93 | 91.63%
[5 empty] | 44.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39334.4387 | 635118.4011 | 44.94 | 91.63%
[5 empty] | 44.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39346.2471 | 635309.0678 | 44.95 | 91.63%
[5 empty] | 44.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39358.0556 | 635499.7345 | 44.96 | 91.63%
[5 empty] | 44.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39369.864 | 635690.4011 | 44.97 | 91.63%
[5 empty] | 44.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39381.6725 | 635881.0678 | 44.98 | 91.63%
[5 empty] | 44.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39393.4809 | 636071.7345 | 44.99 | 91.63%
[5 empty] | 45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39405.2894 | 636262.4011 | 45 | 91.63%
[5 empty] | 45.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39417.0978 | 636453.0678 | 45.01 | 91.63%
[5 empty] | 45.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39428.9063 | 636643.7345 | 45.02 | 91.63%
[5 empty] | 45.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39440.7148 | 636834.4011 | 45.03 | 91.63%
[5 empty] | 45.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39452.5232 | 637025.0678 | 45.04 | 91.63%
[5 empty] | 45.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39464.3317 | 637215.7345 | 45.05 | 91.63%
[5 empty] | 45.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39476.1401 | 637406.4011 | 45.06 | 91.63%
[5 empty] | 45.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39487.9486 | 637597.0678 | 45.07 | 91.63%
[5 empty] | 45.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39499.757 | 637787.7345 | 45.08 | 91.63%
[5 empty] | 45.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39511.5655 | 637978.4011 | 45.09 | 91.63%
[5 empty] | 45.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39523.3739 | 638169.0678 | 45.1 | 91.63%
[5 empty] | 45.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39535.1824 | 638359.7345 | 45.11 | 91.63%
[5 empty] | 45.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39546.9908 | 638550.4011 | 45.12 | 91.63%
[5 empty] | 45.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39558.7993 | 638741.0678 | 45.13 | 91.63%
[5 empty] | 45.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39570.6077 | 638931.7345 | 45.14 | 91.63%
[5 empty] | 45.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39582.4162 | 639122.4011 | 45.15 | 91.63%
[5 empty] | 45.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39594.2247 | 639313.0678 | 45.16 | 91.63%
[5 empty] | 45.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39606.0331 | 639503.7345 | 45.17 | 91.63%
[5 empty] | 45.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39617.8416 | 639694.4011 | 45.18 | 91.63%
[5 empty] | 45.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39629.65 | 639885.0678 | 45.19 | 91.63%
[5 empty] | 45.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39641.4585 | 640075.7345 | 45.2 | 91.63%
[5 empty] | 45.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39653.2669 | 640266.4011 | 45.21 | 91.63%
[5 empty] | 45.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39665.0754 | 640457.0678 | 45.22 | 91.63%
[5 empty] | 45.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39676.8838 | 640647.7345 | 45.23 | 91.63%
[5 empty] | 45.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39688.6923 | 640838.4011 | 45.24 | 91.63%
[5 empty] | 45.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39700.5007 | 641029.0678 | 45.25 | 91.63%
[5 empty] | 45.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39712.3092 | 641219.7345 | 45.26 | 91.63%
[5 empty] | 45.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39724.1176 | 641410.4011 | 45.27 | 91.63%
[5 empty] | 45.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39735.9261 | 641601.0678 | 45.28 | 91.63%
[5 empty] | 45.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39747.7346 | 641791.7345 | 45.29 | 91.63%
[5 empty] | 45.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39759.543 | 641982.4011 | 45.3 | 91.63%
[5 empty] | 45.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39771.3515 | 642173.0678 | 45.31 | 91.63%
[5 empty] | 45.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39783.1599 | 642363.7345 | 45.32 | 91.63%
[5 empty] | 45.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39794.9684 | 642554.4011 | 45.33 | 91.63%
[5 empty] | 45.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39806.7768 | 642745.0678 | 45.34 | 91.63%
[5 empty] | 45.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39818.5853 | 642935.7345 | 45.35 | 91.63%
[5 empty] | 45.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39830.3937 | 643126.4011 | 45.36 | 91.63%
[5 empty] | 45.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39842.2022 | 643317.0678 | 45.37 | 91.63%
[5 empty] | 45.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39854.0106 | 643507.7345 | 45.38 | 91.63%
[5 empty] | 45.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39865.8191 | 643698.4011 | 45.39 | 91.63%
[5 empty] | 45.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39877.6275 | 643889.0678 | 45.4 | 91.63%
[5 empty] | 45.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39889.436 | 644079.7345 | 45.41 | 91.63%
[5 empty] | 45.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39901.2445 | 644270.4011 | 45.42 | 91.63%
[5 empty] | 45.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39913.0529 | 644461.0678 | 45.43 | 91.63%
[5 empty] | 45.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39924.8614 | 644651.7345 | 45.44 | 91.63%
[5 empty] | 45.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39936.6698 | 644842.4011 | 45.45 | 91.63%
[5 empty] | 45.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39948.4783 | 645033.0678 | 45.46 | 91.63%
[5 empty] | 45.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39960.2867 | 645223.7345 | 45.47 | 91.63%
[5 empty] | 45.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39972.0952 | 645414.4011 | 45.48 | 91.63%
[5 empty] | 45.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39983.9036 | 645605.0678 | 45.49 | 91.63%
[5 empty] | 45.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 39995.7121 | 645795.7345 | 45.5 | 91.63%
[5 empty] | 45.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40007.5205 | 645986.4011 | 45.51 | 91.63%
[5 empty] | 45.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40019.329 | 646177.0678 | 45.52 | 91.63%
[5 empty] | 45.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40031.1374 | 646367.7345 | 45.53 | 91.63%
[5 empty] | 45.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40042.9459 | 646558.4011 | 45.54 | 91.63%
[5 empty] | 45.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40054.7544 | 646749.0678 | 45.55 | 91.63%
[5 empty] | 45.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40066.5628 | 646939.7345 | 45.56 | 91.63%
[5 empty] | 45.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40078.3713 | 647130.4011 | 45.57 | 91.63%
[5 empty] | 45.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40090.1797 | 647321.0678 | 45.58 | 91.63%
[5 empty] | 45.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40101.9882 | 647511.7345 | 45.59 | 91.63%
[5 empty] | 45.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40113.7966 | 647702.4011 | 45.6 | 91.63%
[5 empty] | 45.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40125.6051 | 647893.0678 | 45.61 | 91.63%
[5 empty] | 45.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40137.4135 | 648083.7345 | 45.62 | 91.63%
[5 empty] | 45.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40149.222 | 648274.4011 | 45.63 | 91.63%
[5 empty] | 45.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40161.0304 | 648465.0678 | 45.64 | 91.63%
[5 empty] | 45.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40172.8389 | 648655.7345 | 45.65 | 91.63%
[5 empty] | 45.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40184.6473 | 648846.4011 | 45.66 | 91.63%
[5 empty] | 45.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40196.4558 | 649037.0678 | 45.67 | 91.63%
[5 empty] | 45.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40208.2643 | 649227.7345 | 45.68 | 91.63%
[5 empty] | 45.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40220.0727 | 649418.4011 | 45.69 | 91.63%
[5 empty] | 45.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40231.8812 | 649609.0678 | 45.7 | 91.63%
[5 empty] | 45.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40243.6896 | 649799.7345 | 45.71 | 91.63%
[5 empty] | 45.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40255.4981 | 649990.4011 | 45.72 | 91.63%
[5 empty] | 45.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40267.3065 | 650181.0678 | 45.73 | 91.63%
[5 empty] | 45.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40279.115 | 650371.7345 | 45.74 | 91.63%
[5 empty] | 45.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40290.9234 | 650562.4011 | 45.75 | 91.63%
[5 empty] | 45.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40302.7319 | 650753.0678 | 45.76 | 91.63%
[5 empty] | 45.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40314.5403 | 650943.7345 | 45.77 | 91.63%
[5 empty] | 45.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40326.3488 | 651134.4011 | 45.78 | 91.63%
[5 empty] | 45.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40338.1572 | 651325.0678 | 45.79 | 91.63%
[5 empty] | 45.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40349.9657 | 651515.7345 | 45.8 | 91.63%
[5 empty] | 45.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40361.7742 | 651706.4011 | 45.81 | 91.63%
[5 empty] | 45.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40373.5826 | 651897.0678 | 45.82 | 91.63%
[5 empty] | 45.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40385.3911 | 652087.7345 | 45.83 | 91.63%
[5 empty] | 45.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40397.1995 | 652278.4011 | 45.84 | 91.63%
[5 empty] | 45.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40409.008 | 652469.0678 | 45.85 | 91.63%
[5 empty] | 45.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40420.8164 | 652659.7345 | 45.86 | 91.63%
[5 empty] | 45.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40432.6249 | 652850.4011 | 45.87 | 91.63%
[5 empty] | 45.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40444.4333 | 653041.0678 | 45.88 | 91.63%
[5 empty] | 45.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40456.2418 | 653231.7345 | 45.89 | 91.63%
[5 empty] | 45.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40468.0502 | 653422.4011 | 45.9 | 91.63%
[5 empty] | 45.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40479.8587 | 653613.0678 | 45.91 | 91.63%
[5 empty] | 45.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40491.6671 | 653803.7345 | 45.92 | 91.63%
[5 empty] | 45.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40503.4756 | 653994.4011 | 45.93 | 91.63%
[5 empty] | 45.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40515.2841 | 654185.0678 | 45.94 | 91.63%
[5 empty] | 45.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40527.0925 | 654375.7345 | 45.95 | 91.63%
[5 empty] | 45.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40538.901 | 654566.4011 | 45.96 | 91.63%
[5 empty] | 45.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40550.7094 | 654757.0678 | 45.97 | 91.63%
[5 empty] | 45.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40562.5179 | 654947.7345 | 45.98 | 91.63%
[5 empty] | 45.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40574.3263 | 655138.4011 | 45.99 | 91.63%
[5 empty] | 46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40586.1348 | 655329.0678 | 46 | 91.63%
[5 empty] | 46.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40597.9432 | 655519.7345 | 46.01 | 91.63%
[5 empty] | 46.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40609.7517 | 655710.4011 | 46.02 | 91.63%
[5 empty] | 46.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40621.5601 | 655901.0678 | 46.03 | 91.63%
[5 empty] | 46.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40633.3686 | 656091.7345 | 46.04 | 91.63%
[5 empty] | 46.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40645.177 | 656282.4011 | 46.05 | 91.63%
[5 empty] | 46.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40656.9855 | 656473.0678 | 46.06 | 91.63%
[5 empty] | 46.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40668.794 | 656663.7345 | 46.07 | 91.63%
[5 empty] | 46.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40680.6024 | 656854.4011 | 46.08 | 91.63%
[5 empty] | 46.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40692.4109 | 657045.0678 | 46.09 | 91.63%
[5 empty] | 46.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40704.2193 | 657235.7345 | 46.1 | 91.63%
[5 empty] | 46.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40716.0278 | 657426.4011 | 46.11 | 91.63%
[5 empty] | 46.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40727.8362 | 657617.0678 | 46.12 | 91.63%
[5 empty] | 46.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40739.6447 | 657807.7345 | 46.13 | 91.63%
[5 empty] | 46.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40751.4531 | 657998.4011 | 46.14 | 91.63%
[5 empty] | 46.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40763.2616 | 658189.0678 | 46.15 | 91.63%
[5 empty] | 46.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40775.07 | 658379.7345 | 46.16 | 91.63%
[5 empty] | 46.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40786.8785 | 658570.4011 | 46.17 | 91.63%
[5 empty] | 46.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40798.6869 | 658761.0678 | 46.18 | 91.63%
[5 empty] | 46.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40810.4954 | 658951.7345 | 46.19 | 91.63%
[5 empty] | 46.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40822.3039 | 659142.4011 | 46.2 | 91.63%
[5 empty] | 46.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40834.1123 | 659333.0678 | 46.21 | 91.63%
[5 empty] | 46.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40845.9208 | 659523.7345 | 46.22 | 91.63%
[5 empty] | 46.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40857.7292 | 659714.4011 | 46.23 | 91.63%
[5 empty] | 46.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40869.5377 | 659905.0678 | 46.24 | 91.63%
[5 empty] | 46.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40881.3461 | 660095.7345 | 46.25 | 91.63%
[5 empty] | 46.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40893.1546 | 660286.4011 | 46.26 | 91.63%
[5 empty] | 46.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40904.963 | 660477.0678 | 46.27 | 91.63%
[5 empty] | 46.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40916.7715 | 660667.7345 | 46.28 | 91.63%
[5 empty] | 46.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40928.5799 | 660858.4011 | 46.29 | 91.63%
[5 empty] | 46.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40940.3884 | 661049.0678 | 46.3 | 91.63%
[5 empty] | 46.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40952.1968 | 661239.7345 | 46.31 | 91.63%
[5 empty] | 46.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40964.0053 | 661430.4011 | 46.32 | 91.63%
[5 empty] | 46.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40975.8138 | 661621.0678 | 46.33 | 91.63%
[5 empty] | 46.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40987.6222 | 661811.7345 | 46.34 | 91.63%
[5 empty] | 46.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 40999.4307 | 662002.4011 | 46.35 | 91.63%
[5 empty] | 46.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41011.2391 | 662193.0678 | 46.36 | 91.63%
[5 empty] | 46.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41023.0476 | 662383.7345 | 46.37 | 91.63%
[5 empty] | 46.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41034.856 | 662574.4011 | 46.38 | 91.63%
[5 empty] | 46.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41046.6645 | 662765.0678 | 46.39 | 91.63%
[5 empty] | 46.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41058.4729 | 662955.7345 | 46.4 | 91.63%
[5 empty] | 46.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41070.2814 | 663146.4011 | 46.41 | 91.63%
[5 empty] | 46.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41082.0898 | 663337.0678 | 46.42 | 91.63%
[5 empty] | 46.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41093.8983 | 663527.7345 | 46.43 | 91.63%
[5 empty] | 46.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41105.7067 | 663718.4011 | 46.44 | 91.63%
[5 empty] | 46.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41117.5152 | 663909.0678 | 46.45 | 91.63%
[5 empty] | 46.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41129.3237 | 664099.7345 | 46.46 | 91.63%
[5 empty] | 46.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41141.1321 | 664290.4011 | 46.47 | 91.63%
[5 empty] | 46.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41152.9406 | 664481.0678 | 46.48 | 91.63%
[5 empty] | 46.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41164.749 | 664671.7345 | 46.49 | 91.63%
[5 empty] | 46.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41176.5575 | 664862.4011 | 46.5 | 91.63%
[5 empty] | 46.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41188.3659 | 665053.0678 | 46.51 | 91.63%
[5 empty] | 46.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41200.1744 | 665243.7345 | 46.52 | 91.63%
[5 empty] | 46.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41211.9828 | 665434.4011 | 46.53 | 91.63%
[5 empty] | 46.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41223.7913 | 665625.0678 | 46.54 | 91.63%
[5 empty] | 46.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41235.5997 | 665815.7345 | 46.55 | 91.63%
[5 empty] | 46.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41247.4082 | 666006.4011 | 46.56 | 91.63%
[5 empty] | 46.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41259.2166 | 666197.0678 | 46.57 | 91.63%
[5 empty] | 46.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41271.0251 | 666387.7345 | 46.58 | 91.63%
[5 empty] | 46.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41282.8336 | 666578.4011 | 46.59 | 91.63%
[5 empty] | 46.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41294.642 | 666769.0678 | 46.6 | 91.63%
[5 empty] | 46.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41306.4505 | 666959.7345 | 46.61 | 91.63%
[5 empty] | 46.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41318.2589 | 667150.4011 | 46.62 | 91.63%
[5 empty] | 46.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41330.0674 | 667341.0678 | 46.63 | 91.63%
[5 empty] | 46.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41341.8758 | 667531.7345 | 46.64 | 91.63%
[5 empty] | 46.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41353.6843 | 667722.4011 | 46.65 | 91.63%
[5 empty] | 46.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41365.4927 | 667913.0678 | 46.66 | 91.63%
[5 empty] | 46.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41377.3012 | 668103.7345 | 46.67 | 91.63%
[5 empty] | 46.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41389.1096 | 668294.4011 | 46.68 | 91.63%
[5 empty] | 46.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41400.9181 | 668485.0678 | 46.69 | 91.63%
[5 empty] | 46.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41412.7265 | 668675.7345 | 46.7 | 91.63%
[5 empty] | 46.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41424.535 | 668866.4011 | 46.71 | 91.63%
[5 empty] | 46.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41436.3435 | 669057.0678 | 46.72 | 91.63%
[5 empty] | 46.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41448.1519 | 669247.7345 | 46.73 | 91.63%
[5 empty] | 46.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41459.9604 | 669438.4011 | 46.74 | 91.63%
[5 empty] | 46.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41471.7688 | 669629.0678 | 46.75 | 91.63%
[5 empty] | 46.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41483.5773 | 669819.7345 | 46.76 | 91.63%
[5 empty] | 46.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41495.3857 | 670010.4011 | 46.77 | 91.63%
[5 empty] | 46.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41507.1942 | 670201.0678 | 46.78 | 91.63%
[5 empty] | 46.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41519.0026 | 670391.7345 | 46.79 | 91.63%
[5 empty] | 46.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41530.8111 | 670582.4011 | 46.8 | 91.63%
[5 empty] | 46.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41542.6195 | 670773.0678 | 46.81 | 91.63%
[5 empty] | 46.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41554.428 | 670963.7345 | 46.82 | 91.63%
[5 empty] | 46.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41566.2364 | 671154.4011 | 46.83 | 91.63%
[5 empty] | 46.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41578.0449 | 671345.0678 | 46.84 | 91.63%
[5 empty] | 46.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41589.8534 | 671535.7345 | 46.85 | 91.63%
[5 empty] | 46.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41601.6618 | 671726.4011 | 46.86 | 91.63%
[5 empty] | 46.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41613.4703 | 671917.0678 | 46.87 | 91.63%
[5 empty] | 46.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41625.2787 | 672107.7345 | 46.88 | 91.63%
[5 empty] | 46.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41637.0872 | 672298.4011 | 46.89 | 91.63%
[5 empty] | 46.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41648.8956 | 672489.0678 | 46.9 | 91.63%
[5 empty] | 46.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41660.7041 | 672679.7345 | 46.91 | 91.63%
[5 empty] | 46.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41672.5125 | 672870.4011 | 46.92 | 91.63%
[5 empty] | 46.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41684.321 | 673061.0678 | 46.93 | 91.63%
[5 empty] | 46.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41696.1294 | 673251.7345 | 46.94 | 91.63%
[5 empty] | 46.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41707.9379 | 673442.4011 | 46.95 | 91.63%
[5 empty] | 46.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41719.7463 | 673633.0678 | 46.96 | 91.63%
[5 empty] | 46.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41731.5548 | 673823.7345 | 46.97 | 91.63%
[5 empty] | 46.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41743.3633 | 674014.4011 | 46.98 | 91.63%
[5 empty] | 46.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41755.1717 | 674205.0678 | 46.99 | 91.63%
[5 empty] | 47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41766.9802 | 674395.7345 | 47 | 91.63%
[5 empty] | 47.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41778.7886 | 674586.4011 | 47.01 | 91.63%
[5 empty] | 47.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41790.5971 | 674777.0678 | 47.02 | 91.63%
[5 empty] | 47.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41802.4055 | 674967.7345 | 47.03 | 91.63%
[5 empty] | 47.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41814.214 | 675158.4011 | 47.04 | 91.63%
[5 empty] | 47.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41826.0224 | 675349.0678 | 47.05 | 91.63%
[5 empty] | 47.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41837.8309 | 675539.7345 | 47.06 | 91.63%
[5 empty] | 47.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41849.6393 | 675730.4011 | 47.07 | 91.63%
[5 empty] | 47.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41861.4478 | 675921.0678 | 47.08 | 91.63%
[5 empty] | 47.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41873.2562 | 676111.7345 | 47.09 | 91.63%
[5 empty] | 47.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41885.0647 | 676302.4011 | 47.1 | 91.63%
[5 empty] | 47.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41896.8731 | 676493.0678 | 47.11 | 91.63%
[5 empty] | 47.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41908.6816 | 676683.7345 | 47.12 | 91.63%
[5 empty] | 47.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41920.4901 | 676874.4011 | 47.13 | 91.63%
[5 empty] | 47.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41932.2985 | 677065.0678 | 47.14 | 91.63%
[5 empty] | 47.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41944.107 | 677255.7345 | 47.15 | 91.63%
[5 empty] | 47.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41955.9154 | 677446.4011 | 47.16 | 91.63%
[5 empty] | 47.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41967.7239 | 677637.0678 | 47.17 | 91.63%
[5 empty] | 47.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41979.5323 | 677827.7345 | 47.18 | 91.63%
[5 empty] | 47.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 41991.3408 | 678018.4011 | 47.19 | 91.63%
[5 empty] | 47.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42003.1492 | 678209.0678 | 47.2 | 91.63%
[5 empty] | 47.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42014.9577 | 678399.7345 | 47.21 | 91.63%
[5 empty] | 47.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42026.7661 | 678590.4011 | 47.22 | 91.63%
[5 empty] | 47.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42038.5746 | 678781.0678 | 47.23 | 91.63%
[5 empty] | 47.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42050.383 | 678971.7345 | 47.24 | 91.63%
[5 empty] | 47.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42062.1915 | 679162.4011 | 47.25 | 91.63%
[5 empty] | 47.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42074 | 679353.0678 | 47.26 | 91.63%
[5 empty] | 47.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42085.8084 | 679543.7345 | 47.27 | 91.63%
[5 empty] | 47.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42097.6169 | 679734.4011 | 47.28 | 91.63%
[5 empty] | 47.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42109.4253 | 679925.0678 | 47.29 | 91.63%
[5 empty] | 47.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42121.2338 | 680115.7345 | 47.3 | 91.63%
[5 empty] | 47.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42133.0422 | 680306.4011 | 47.31 | 91.63%
[5 empty] | 47.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42144.8507 | 680497.0678 | 47.32 | 91.63%
[5 empty] | 47.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42156.6591 | 680687.7345 | 47.33 | 91.63%
[5 empty] | 47.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42168.4676 | 680878.4011 | 47.34 | 91.63%
[5 empty] | 47.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42180.276 | 681069.0678 | 47.35 | 91.63%
[5 empty] | 47.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42192.0845 | 681259.7345 | 47.36 | 91.63%
[5 empty] | 47.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42203.8929 | 681450.4011 | 47.37 | 91.63%
[5 empty] | 47.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42215.7014 | 681641.0678 | 47.38 | 91.63%
[5 empty] | 47.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42227.5099 | 681831.7345 | 47.39 | 91.63%
[5 empty] | 47.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42239.3183 | 682022.4011 | 47.4 | 91.63%
[5 empty] | 47.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42251.1268 | 682213.0678 | 47.41 | 91.63%
[5 empty] | 47.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42262.9352 | 682403.7345 | 47.42 | 91.63%
[5 empty] | 47.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42274.7437 | 682594.4011 | 47.43 | 91.63%
[5 empty] | 47.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42286.5521 | 682785.0678 | 47.44 | 91.63%
[5 empty] | 47.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42298.3606 | 682975.7345 | 47.45 | 91.63%
[5 empty] | 47.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42310.169 | 683166.4011 | 47.46 | 91.63%
[5 empty] | 47.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42321.9775 | 683357.0678 | 47.47 | 91.63%
[5 empty] | 47.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42333.7859 | 683547.7345 | 47.48 | 91.63%
[5 empty] | 47.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42345.5944 | 683738.4011 | 47.49 | 91.63%
[5 empty] | 47.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42357.4028 | 683929.0678 | 47.5 | 91.63%
[5 empty] | 47.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42369.2113 | 684119.7345 | 47.51 | 91.63%
[5 empty] | 47.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42381.0198 | 684310.4011 | 47.52 | 91.63%
[5 empty] | 47.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42392.8282 | 684501.0678 | 47.53 | 91.63%
[5 empty] | 47.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42404.6367 | 684691.7345 | 47.54 | 91.63%
[5 empty] | 47.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42416.4451 | 684882.4011 | 47.55 | 91.63%
[5 empty] | 47.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42428.2536 | 685073.0678 | 47.56 | 91.63%
[5 empty] | 47.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42440.062 | 685263.7345 | 47.57 | 91.63%
[5 empty] | 47.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42451.8705 | 685454.4011 | 47.58 | 91.63%
[5 empty] | 47.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42463.6789 | 685645.0678 | 47.59 | 91.63%
[5 empty] | 47.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42475.4874 | 685835.7345 | 47.6 | 91.63%
[5 empty] | 47.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42487.2958 | 686026.4011 | 47.61 | 91.63%
[5 empty] | 47.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42499.1043 | 686217.0678 | 47.62 | 91.63%
[5 empty] | 47.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42510.9127 | 686407.7345 | 47.63 | 91.63%
[5 empty] | 47.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42522.7212 | 686598.4011 | 47.64 | 91.63%
[5 empty] | 47.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42534.5297 | 686789.0678 | 47.65 | 91.63%
[5 empty] | 47.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42546.3381 | 686979.7345 | 47.66 | 91.63%
[5 empty] | 47.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42558.1466 | 687170.4011 | 47.67 | 91.63%
[5 empty] | 47.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42569.955 | 687361.0678 | 47.68 | 91.63%
[5 empty] | 47.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42581.7635 | 687551.7345 | 47.69 | 91.63%
[5 empty] | 47.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42593.5719 | 687742.4011 | 47.7 | 91.63%
[5 empty] | 47.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42605.3804 | 687933.0678 | 47.71 | 91.63%
[5 empty] | 47.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42617.1888 | 688123.7345 | 47.72 | 91.63%
[5 empty] | 47.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42628.9973 | 688314.4011 | 47.73 | 91.63%
[5 empty] | 47.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42640.8057 | 688505.0678 | 47.74 | 91.63%
[5 empty] | 47.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42652.6142 | 688695.7345 | 47.75 | 91.63%
[5 empty] | 47.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42664.4226 | 688886.4011 | 47.76 | 91.63%
[5 empty] | 47.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42676.2311 | 689077.0678 | 47.77 | 91.63%
[5 empty] | 47.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42688.0396 | 689267.7345 | 47.78 | 91.63%
[5 empty] | 47.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42699.848 | 689458.4011 | 47.79 | 91.63%
[5 empty] | 47.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42711.6565 | 689649.0678 | 47.8 | 91.63%
[5 empty] | 47.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42723.4649 | 689839.7345 | 47.81 | 91.63%
[5 empty] | 47.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42735.2734 | 690030.4011 | 47.82 | 91.63%
[5 empty] | 47.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42747.0818 | 690221.0678 | 47.83 | 91.63%
[5 empty] | 47.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42758.8903 | 690411.7345 | 47.84 | 91.63%
[5 empty] | 47.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42770.6987 | 690602.4011 | 47.85 | 91.63%
[5 empty] | 47.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42782.5072 | 690793.0678 | 47.86 | 91.63%
[5 empty] | 47.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42794.3156 | 690983.7345 | 47.87 | 91.63%
[5 empty] | 47.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42806.1241 | 691174.4011 | 47.88 | 91.63%
[5 empty] | 47.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42817.9325 | 691365.0678 | 47.89 | 91.63%
[5 empty] | 47.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42829.741 | 691555.7345 | 47.9 | 91.63%
[5 empty] | 47.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42841.5495 | 691746.4011 | 47.91 | 91.63%
[5 empty] | 47.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42853.3579 | 691937.0678 | 47.92 | 91.63%
[5 empty] | 47.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42865.1664 | 692127.7345 | 47.93 | 91.63%
[5 empty] | 47.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42876.9748 | 692318.4011 | 47.94 | 91.63%
[5 empty] | 47.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42888.7833 | 692509.0678 | 47.95 | 91.63%
[5 empty] | 47.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42900.5917 | 692699.7345 | 47.96 | 91.63%
[5 empty] | 47.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42912.4002 | 692890.4011 | 47.97 | 91.63%
[5 empty] | 47.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42924.2086 | 693081.0678 | 47.98 | 91.63%
[5 empty] | 47.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42936.0171 | 693271.7345 | 47.99 | 91.63%
[5 empty] | 48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42947.8255 | 693462.4011 | 48 | 91.63%
[5 empty] | 48.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42959.634 | 693653.0678 | 48.01 | 91.63%
[5 empty] | 48.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42971.4424 | 693843.7345 | 48.02 | 91.63%
[5 empty] | 48.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42983.2509 | 694034.4011 | 48.03 | 91.63%
[5 empty] | 48.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 42995.0594 | 694225.0678 | 48.04 | 91.63%
[5 empty] | 48.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43006.8678 | 694415.7345 | 48.05 | 91.63%
[5 empty] | 48.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43018.6763 | 694606.4011 | 48.06 | 91.63%
[5 empty] | 48.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43030.4847 | 694797.0678 | 48.07 | 91.63%
[5 empty] | 48.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43042.2932 | 694987.7345 | 48.08 | 91.63%
[5 empty] | 48.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43054.1016 | 695178.4011 | 48.09 | 91.63%
[5 empty] | 48.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43065.9101 | 695369.0678 | 48.1 | 91.63%
[5 empty] | 48.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43077.7185 | 695559.7345 | 48.11 | 91.63%
[5 empty] | 48.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43089.527 | 695750.4011 | 48.12 | 91.63%
[5 empty] | 48.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43101.3354 | 695941.0678 | 48.13 | 91.63%
[5 empty] | 48.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43113.1439 | 696131.7345 | 48.14 | 91.63%
[5 empty] | 48.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43124.9523 | 696322.4011 | 48.15 | 91.63%
[5 empty] | 48.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43136.7608 | 696513.0678 | 48.16 | 91.63%
[5 empty] | 48.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43148.5693 | 696703.7345 | 48.17 | 91.63%
[5 empty] | 48.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43160.3777 | 696894.4011 | 48.18 | 91.63%
[5 empty] | 48.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43172.1862 | 697085.0678 | 48.19 | 91.63%
[5 empty] | 48.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43183.9946 | 697275.7345 | 48.2 | 91.63%
[5 empty] | 48.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43195.8031 | 697466.4011 | 48.21 | 91.63%
[5 empty] | 48.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43207.6115 | 697657.0678 | 48.22 | 91.63%
[5 empty] | 48.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43219.42 | 697847.7345 | 48.23 | 91.63%
[5 empty] | 48.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43231.2284 | 698038.4011 | 48.24 | 91.63%
[5 empty] | 48.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43243.0369 | 698229.0678 | 48.25 | 91.63%
[5 empty] | 48.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43254.8453 | 698419.7345 | 48.26 | 91.63%
[5 empty] | 48.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43266.6538 | 698610.4011 | 48.27 | 91.63%
[5 empty] | 48.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43278.4622 | 698801.0678 | 48.28 | 91.63%
[5 empty] | 48.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43290.2707 | 698991.7345 | 48.29 | 91.63%
[5 empty] | 48.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43302.0792 | 699182.4011 | 48.3 | 91.63%
[5 empty] | 48.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43313.8876 | 699373.0678 | 48.31 | 91.63%
[5 empty] | 48.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43325.6961 | 699563.7345 | 48.32 | 91.63%
[5 empty] | 48.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43337.5045 | 699754.4011 | 48.33 | 91.63%
[5 empty] | 48.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43349.313 | 699945.0678 | 48.34 | 91.63%
[5 empty] | 48.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43361.1214 | 700135.7345 | 48.35 | 91.63%
[5 empty] | 48.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43372.9299 | 700326.4011 | 48.36 | 91.63%
[5 empty] | 48.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43384.7383 | 700517.0678 | 48.37 | 91.63%
[5 empty] | 48.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43396.5468 | 700707.7345 | 48.38 | 91.63%
[5 empty] | 48.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43408.3552 | 700898.4011 | 48.39 | 91.63%
[5 empty] | 48.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43420.1637 | 701089.0678 | 48.4 | 91.63%
[5 empty] | 48.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43431.9721 | 701279.7345 | 48.41 | 91.63%
[5 empty] | 48.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43443.7806 | 701470.4011 | 48.42 | 91.63%
[5 empty] | 48.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43455.5891 | 701661.0678 | 48.43 | 91.63%
[5 empty] | 48.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43467.3975 | 701851.7345 | 48.44 | 91.63%
[5 empty] | 48.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43479.206 | 702042.4011 | 48.45 | 91.63%
[5 empty] | 48.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43491.0144 | 702233.0678 | 48.46 | 91.63%
[5 empty] | 48.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43502.8229 | 702423.7345 | 48.47 | 91.63%
[5 empty] | 48.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43514.6313 | 702614.4011 | 48.48 | 91.63%
[5 empty] | 48.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43526.4398 | 702805.0678 | 48.49 | 91.63%
[5 empty] | 48.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43538.2482 | 702995.7345 | 48.5 | 91.63%
[5 empty] | 48.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43550.0567 | 703186.4011 | 48.51 | 91.63%
[5 empty] | 48.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43561.8651 | 703377.0678 | 48.52 | 91.63%
[5 empty] | 48.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43573.6736 | 703567.7345 | 48.53 | 91.63%
[5 empty] | 48.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43585.482 | 703758.4011 | 48.54 | 91.63%
[5 empty] | 48.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43597.2905 | 703949.0678 | 48.55 | 91.63%
[5 empty] | 48.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43609.099 | 704139.7345 | 48.56 | 91.63%
[5 empty] | 48.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43620.9074 | 704330.4011 | 48.57 | 91.63%
[5 empty] | 48.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43632.7159 | 704521.0678 | 48.58 | 91.63%
[5 empty] | 48.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43644.5243 | 704711.7345 | 48.59 | 91.63%
[5 empty] | 48.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43656.3328 | 704902.4011 | 48.6 | 91.63%
[5 empty] | 48.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43668.1412 | 705093.0678 | 48.61 | 91.63%
[5 empty] | 48.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43679.9497 | 705283.7345 | 48.62 | 91.63%
[5 empty] | 48.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43691.7581 | 705474.4011 | 48.63 | 91.63%
[5 empty] | 48.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43703.5666 | 705665.0678 | 48.64 | 91.63%
[5 empty] | 48.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43715.375 | 705855.7345 | 48.65 | 91.63%
[5 empty] | 48.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43727.1835 | 706046.4011 | 48.66 | 91.63%
[5 empty] | 48.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43738.9919 | 706237.0678 | 48.67 | 91.63%
[5 empty] | 48.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43750.8004 | 706427.7345 | 48.68 | 91.63%
[5 empty] | 48.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43762.6089 | 706618.4011 | 48.69 | 91.63%
[5 empty] | 48.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43774.4173 | 706809.0678 | 48.7 | 91.63%
[5 empty] | 48.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43786.2258 | 706999.7345 | 48.71 | 91.63%
[5 empty] | 48.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43798.0342 | 707190.4011 | 48.72 | 91.63%
[5 empty] | 48.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43809.8427 | 707381.0678 | 48.73 | 91.63%
[5 empty] | 48.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43821.6511 | 707571.7345 | 48.74 | 91.63%
[5 empty] | 48.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43833.4596 | 707762.4011 | 48.75 | 91.63%
[5 empty] | 48.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43845.268 | 707953.0678 | 48.76 | 91.63%
[5 empty] | 48.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43857.0765 | 708143.7345 | 48.77 | 91.63%
[5 empty] | 48.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43868.8849 | 708334.4011 | 48.78 | 91.63%
[5 empty] | 48.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43880.6934 | 708525.0678 | 48.79 | 91.63%
[5 empty] | 48.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43892.5018 | 708715.7345 | 48.8 | 91.63%
[5 empty] | 48.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43904.3103 | 708906.4011 | 48.81 | 91.63%
[5 empty] | 48.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43916.1188 | 709097.0678 | 48.82 | 91.63%
[5 empty] | 48.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43927.9272 | 709287.7345 | 48.83 | 91.63%
[5 empty] | 48.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43939.7357 | 709478.4011 | 48.84 | 91.63%
[5 empty] | 48.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43951.5441 | 709669.0678 | 48.85 | 91.63%
[5 empty] | 48.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43963.3526 | 709859.7345 | 48.86 | 91.63%
[5 empty] | 48.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43975.161 | 710050.4011 | 48.87 | 91.63%
[5 empty] | 48.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43986.9695 | 710241.0678 | 48.88 | 91.63%
[5 empty] | 48.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 43998.7779 | 710431.7345 | 48.89 | 91.63%
[5 empty] | 48.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44010.5864 | 710622.4011 | 48.9 | 91.63%
[5 empty] | 48.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44022.3948 | 710813.0678 | 48.91 | 91.63%
[5 empty] | 48.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44034.2033 | 711003.7345 | 48.92 | 91.63%
[5 empty] | 48.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44046.0117 | 711194.4011 | 48.93 | 91.63%
[5 empty] | 48.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44057.8202 | 711385.0678 | 48.94 | 91.63%
[5 empty] | 48.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44069.6287 | 711575.7345 | 48.95 | 91.63%
[5 empty] | 48.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44081.4371 | 711766.4011 | 48.96 | 91.63%
[5 empty] | 48.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44093.2456 | 711957.0678 | 48.97 | 91.63%
[5 empty] | 48.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44105.054 | 712147.7345 | 48.98 | 91.63%
[5 empty] | 48.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44116.8625 | 712338.4011 | 48.99 | 91.63%
[5 empty] | 49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44128.6709 | 712529.0678 | 49 | 91.63%
[5 empty] | 49.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44140.4794 | 712719.7345 | 49.01 | 91.63%
[5 empty] | 49.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44152.2878 | 712910.4011 | 49.02 | 91.63%
[5 empty] | 49.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44164.0963 | 713101.0678 | 49.03 | 91.63%
[5 empty] | 49.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44175.9047 | 713291.7345 | 49.04 | 91.63%
[5 empty] | 49.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44187.7132 | 713482.4011 | 49.05 | 91.63%
[5 empty] | 49.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44199.5216 | 713673.0678 | 49.06 | 91.63%
[5 empty] | 49.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44211.3301 | 713863.7345 | 49.07 | 91.63%
[5 empty] | 49.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44223.1386 | 714054.4011 | 49.08 | 91.63%
[5 empty] | 49.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44234.947 | 714245.0678 | 49.09 | 91.63%
[5 empty] | 49.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44246.7555 | 714435.7345 | 49.1 | 91.63%
[5 empty] | 49.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44258.5639 | 714626.4011 | 49.11 | 91.63%
[5 empty] | 49.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44270.3724 | 714817.0678 | 49.12 | 91.63%
[5 empty] | 49.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44282.1808 | 715007.7345 | 49.13 | 91.63%
[5 empty] | 49.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44293.9893 | 715198.4011 | 49.14 | 91.63%
[5 empty] | 49.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44305.7977 | 715389.0678 | 49.15 | 91.63%
[5 empty] | 49.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44317.6062 | 715579.7345 | 49.16 | 91.63%
[5 empty] | 49.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44329.4146 | 715770.4011 | 49.17 | 91.63%
[5 empty] | 49.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44341.2231 | 715961.0678 | 49.18 | 91.63%
[5 empty] | 49.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44353.0315 | 716151.7345 | 49.19 | 91.63%
[5 empty] | 49.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44364.84 | 716342.4011 | 49.2 | 91.63%
[5 empty] | 49.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44376.6485 | 716533.0678 | 49.21 | 91.63%
[5 empty] | 49.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44388.4569 | 716723.7345 | 49.22 | 91.63%
[5 empty] | 49.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44400.2654 | 716914.4011 | 49.23 | 91.63%
[5 empty] | 49.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44412.0738 | 717105.0678 | 49.24 | 91.63%
[5 empty] | 49.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44423.8823 | 717295.7345 | 49.25 | 91.63%
[5 empty] | 49.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44435.6907 | 717486.4011 | 49.26 | 91.63%
[5 empty] | 49.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44447.4992 | 717677.0678 | 49.27 | 91.63%
[5 empty] | 49.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44459.3076 | 717867.7345 | 49.28 | 91.63%
[5 empty] | 49.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44471.1161 | 718058.4011 | 49.29 | 91.63%
[5 empty] | 49.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44482.9245 | 718249.0678 | 49.3 | 91.63%
[5 empty] | 49.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44494.733 | 718439.7345 | 49.31 | 91.63%
[5 empty] | 49.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44506.5414 | 718630.4011 | 49.32 | 91.63%
[5 empty] | 49.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44518.3499 | 718821.0678 | 49.33 | 91.63%
[5 empty] | 49.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44530.1584 | 719011.7345 | 49.34 | 91.63%
[5 empty] | 49.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44541.9668 | 719202.4011 | 49.35 | 91.63%
[5 empty] | 49.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44553.7753 | 719393.0678 | 49.36 | 91.63%
[5 empty] | 49.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44565.5837 | 719583.7345 | 49.37 | 91.63%
[5 empty] | 49.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44577.3922 | 719774.4011 | 49.38 | 91.63%
[5 empty] | 49.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44589.2006 | 719965.0678 | 49.39 | 91.63%
[5 empty] | 49.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44601.0091 | 720155.7345 | 49.4 | 91.63%
[5 empty] | 49.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44612.8175 | 720346.4011 | 49.41 | 91.63%
[5 empty] | 49.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44624.626 | 720537.0678 | 49.42 | 91.63%
[5 empty] | 49.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44636.4344 | 720727.7345 | 49.43 | 91.63%
[5 empty] | 49.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44648.2429 | 720918.4011 | 49.44 | 91.63%
[5 empty] | 49.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44660.0513 | 721109.0678 | 49.45 | 91.63%
[5 empty] | 49.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44671.8598 | 721299.7345 | 49.46 | 91.63%
[5 empty] | 49.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44683.6682 | 721490.4011 | 49.47 | 91.63%
[5 empty] | 49.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44695.4767 | 721681.0678 | 49.48 | 91.63%
[5 empty] | 49.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44707.2852 | 721871.7345 | 49.49 | 91.63%
[5 empty] | 49.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44719.0936 | 722062.4011 | 49.5 | 91.63%
[5 empty] | 49.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44730.9021 | 722253.0678 | 49.51 | 91.63%
[5 empty] | 49.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44742.7105 | 722443.7345 | 49.52 | 91.63%
[5 empty] | 49.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44754.519 | 722634.4011 | 49.53 | 91.63%
[5 empty] | 49.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44766.3274 | 722825.0678 | 49.54 | 91.63%
[5 empty] | 49.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44778.1359 | 723015.7345 | 49.55 | 91.63%
[5 empty] | 49.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44789.9443 | 723206.4011 | 49.56 | 91.63%
[5 empty] | 49.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44801.7528 | 723397.0678 | 49.57 | 91.63%
[5 empty] | 49.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44813.5612 | 723587.7345 | 49.58 | 91.63%
[5 empty] | 49.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44825.3697 | 723778.4011 | 49.59 | 91.63%
[5 empty] | 49.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44837.1781 | 723969.0678 | 49.6 | 91.63%
[5 empty] | 49.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44848.9866 | 724159.7345 | 49.61 | 91.63%
[5 empty] | 49.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44860.7951 | 724350.4011 | 49.62 | 91.63%
[5 empty] | 49.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44872.6035 | 724541.0678 | 49.63 | 91.63%
[5 empty] | 49.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44884.412 | 724731.7345 | 49.64 | 91.63%
[5 empty] | 49.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44896.2204 | 724922.4011 | 49.65 | 91.63%
[5 empty] | 49.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44908.0289 | 725113.0678 | 49.66 | 91.63%
[5 empty] | 49.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44919.8373 | 725303.7345 | 49.67 | 91.63%
[5 empty] | 49.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44931.6458 | 725494.4011 | 49.68 | 91.63%
[5 empty] | 49.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44943.4542 | 725685.0678 | 49.69 | 91.63%
[5 empty] | 49.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44955.2627 | 725875.7345 | 49.7 | 91.63%
[5 empty] | 49.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44967.0711 | 726066.4011 | 49.71 | 91.63%
[5 empty] | 49.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44978.8796 | 726257.0678 | 49.72 | 91.63%
[5 empty] | 49.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 44990.688 | 726447.7345 | 49.73 | 91.63%
[5 empty] | 49.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45002.4965 | 726638.4011 | 49.74 | 91.63%
[5 empty] | 49.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45014.305 | 726829.0678 | 49.75 | 91.63%
[5 empty] | 49.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45026.1134 | 727019.7345 | 49.76 | 91.63%
[5 empty] | 49.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45037.9219 | 727210.4011 | 49.77 | 91.63%
[5 empty] | 49.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45049.7303 | 727401.0678 | 49.78 | 91.63%
[5 empty] | 49.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45061.5388 | 727591.7345 | 49.79 | 91.63%
[5 empty] | 49.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45073.3472 | 727782.4011 | 49.8 | 91.63%
[5 empty] | 49.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45085.1557 | 727973.0678 | 49.81 | 91.63%
[5 empty] | 49.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45096.9641 | 728163.7345 | 49.82 | 91.63%
[5 empty] | 49.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45108.7726 | 728354.4011 | 49.83 | 91.63%
[5 empty] | 49.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45120.581 | 728545.0678 | 49.84 | 91.63%
[5 empty] | 49.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45132.3895 | 728735.7345 | 49.85 | 91.63%
[5 empty] | 49.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45144.1979 | 728926.4011 | 49.86 | 91.63%
[5 empty] | 49.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45156.0064 | 729117.0678 | 49.87 | 91.63%
[5 empty] | 49.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45167.8149 | 729307.7345 | 49.88 | 91.63%
[5 empty] | 49.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45179.6233 | 729498.4011 | 49.89 | 91.63%
[5 empty] | 49.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45191.4318 | 729689.0678 | 49.9 | 91.63%
[5 empty] | 49.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45203.2402 | 729879.7345 | 49.91 | 91.63%
[5 empty] | 49.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45215.0487 | 730070.4011 | 49.92 | 91.63%
[5 empty] | 49.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45226.8571 | 730261.0678 | 49.93 | 91.63%
[5 empty] | 49.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45238.6656 | 730451.7345 | 49.94 | 91.63%
[5 empty] | 49.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45250.474 | 730642.4011 | 49.95 | 91.63%
[5 empty] | 49.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45262.2825 | 730833.0678 | 49.96 | 91.63%
[5 empty] | 49.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45274.0909 | 731023.7345 | 49.97 | 91.63%
[5 empty] | 49.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45285.8994 | 731214.4011 | 49.98 | 91.63%
[5 empty] | 49.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45297.7078 | 731405.0678 | 49.99 | 91.63%
[5 empty] | 50 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45309.5163 | 731595.7345 | 50 | 91.63%
[5 empty] | 50.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45321.3248 | 731786.4011 | 50.01 | 91.63%
[5 empty] | 50.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45333.1332 | 731977.0678 | 50.02 | 91.63%
[5 empty] | 50.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45344.9417 | 732167.7345 | 50.03 | 91.63%
[5 empty] | 50.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45356.7501 | 732358.4011 | 50.04 | 91.63%
[5 empty] | 50.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45368.5586 | 732549.0678 | 50.05 | 91.63%
[5 empty] | 50.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45380.367 | 732739.7345 | 50.06 | 91.63%
[5 empty] | 50.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45392.1755 | 732930.4011 | 50.07 | 91.63%
[5 empty] | 50.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45403.9839 | 733121.0678 | 50.08 | 91.63%
[5 empty] | 50.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45415.7924 | 733311.7345 | 50.09 | 91.63%
[5 empty] | 50.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45427.6008 | 733502.4011 | 50.1 | 91.63%
[5 empty] | 50.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45439.4093 | 733693.0678 | 50.11 | 91.63%
[5 empty] | 50.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45451.2177 | 733883.7345 | 50.12 | 91.63%
[5 empty] | 50.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45463.0262 | 734074.4011 | 50.13 | 91.63%
[5 empty] | 50.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45474.8347 | 734265.0678 | 50.14 | 91.63%
[5 empty] | 50.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45486.6431 | 734455.7345 | 50.15 | 91.63%
[5 empty] | 50.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45498.4516 | 734646.4011 | 50.16 | 91.63%
[5 empty] | 50.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45510.26 | 734837.0678 | 50.17 | 91.63%
[5 empty] | 50.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45522.0685 | 735027.7345 | 50.18 | 91.63%
[5 empty] | 50.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45533.8769 | 735218.4011 | 50.19 | 91.63%
[5 empty] | 50.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45545.6854 | 735409.0678 | 50.2 | 91.63%
[5 empty] | 50.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45557.4938 | 735599.7345 | 50.21 | 91.63%
[5 empty] | 50.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45569.3023 | 735790.4011 | 50.22 | 91.63%
[5 empty] | 50.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45581.1107 | 735981.0678 | 50.23 | 91.63%
[5 empty] | 50.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45592.9192 | 736171.7345 | 50.24 | 91.63%
[5 empty] | 50.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45604.7276 | 736362.4011 | 50.25 | 91.63%
[5 empty] | 50.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45616.5361 | 736553.0678 | 50.26 | 91.63%
[5 empty] | 50.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45628.3446 | 736743.7345 | 50.27 | 91.63%
[5 empty] | 50.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45640.153 | 736934.4011 | 50.28 | 91.63%
[5 empty] | 50.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45651.9615 | 737125.0678 | 50.29 | 91.63%
[5 empty] | 50.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45663.7699 | 737315.7345 | 50.3 | 91.63%
[5 empty] | 50.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45675.5784 | 737506.4011 | 50.31 | 91.63%
[5 empty] | 50.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45687.3868 | 737697.0678 | 50.32 | 91.63%
[5 empty] | 50.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45699.1953 | 737887.7345 | 50.33 | 91.63%
[5 empty] | 50.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45711.0037 | 738078.4011 | 50.34 | 91.63%
[5 empty] | 50.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45722.8122 | 738269.0678 | 50.35 | 91.63%
[5 empty] | 50.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45734.6206 | 738459.7345 | 50.36 | 91.63%
[5 empty] | 50.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45746.4291 | 738650.4011 | 50.37 | 91.63%
[5 empty] | 50.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45758.2375 | 738841.0678 | 50.38 | 91.63%
[5 empty] | 50.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45770.046 | 739031.7345 | 50.39 | 91.63%
[5 empty] | 50.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45781.8545 | 739222.4011 | 50.4 | 91.63%
[5 empty] | 50.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45793.6629 | 739413.0678 | 50.41 | 91.63%
[5 empty] | 50.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45805.4714 | 739603.7345 | 50.42 | 91.63%
[5 empty] | 50.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45817.2798 | 739794.4011 | 50.43 | 91.63%
[5 empty] | 50.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45829.0883 | 739985.0678 | 50.44 | 91.63%
[5 empty] | 50.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45840.8967 | 740175.7345 | 50.45 | 91.63%
[5 empty] | 50.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45852.7052 | 740366.4011 | 50.46 | 91.63%
[5 empty] | 50.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45864.5136 | 740557.0678 | 50.47 | 91.63%
[5 empty] | 50.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45876.3221 | 740747.7345 | 50.48 | 91.63%
[5 empty] | 50.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45888.1305 | 740938.4011 | 50.49 | 91.63%
[5 empty] | 50.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45899.939 | 741129.0678 | 50.5 | 91.63%
[5 empty] | 50.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45911.7474 | 741319.7345 | 50.51 | 91.63%
[5 empty] | 50.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45923.5559 | 741510.4011 | 50.52 | 91.63%
[5 empty] | 50.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45935.3644 | 741701.0678 | 50.53 | 91.63%
[5 empty] | 50.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45947.1728 | 741891.7345 | 50.54 | 91.63%
[5 empty] | 50.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45958.9813 | 742082.4011 | 50.55 | 91.63%
[5 empty] | 50.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45970.7897 | 742273.0678 | 50.56 | 91.63%
[5 empty] | 50.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45982.5982 | 742463.7345 | 50.57 | 91.63%
[5 empty] | 50.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 45994.4066 | 742654.4011 | 50.58 | 91.63%
[5 empty] | 50.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46006.2151 | 742845.0678 | 50.59 | 91.63%
[5 empty] | 50.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46018.0235 | 743035.7345 | 50.6 | 91.63%
[5 empty] | 50.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46029.832 | 743226.4011 | 50.61 | 91.63%
[5 empty] | 50.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46041.6404 | 743417.0678 | 50.62 | 91.63%
[5 empty] | 50.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46053.4489 | 743607.7345 | 50.63 | 91.63%
[5 empty] | 50.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46065.2573 | 743798.4011 | 50.64 | 91.63%
[5 empty] | 50.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46077.0658 | 743989.0678 | 50.65 | 91.63%
[5 empty] | 50.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46088.8743 | 744179.7345 | 50.66 | 91.63%
[5 empty] | 50.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46100.6827 | 744370.4011 | 50.67 | 91.63%
[5 empty] | 50.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46112.4912 | 744561.0678 | 50.68 | 91.63%
[5 empty] | 50.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46124.2996 | 744751.7345 | 50.69 | 91.63%
[5 empty] | 50.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46136.1081 | 744942.4011 | 50.7 | 91.63%
[5 empty] | 50.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46147.9165 | 745133.0678 | 50.71 | 91.63%
[5 empty] | 50.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46159.725 | 745323.7345 | 50.72 | 91.63%
[5 empty] | 50.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46171.5334 | 745514.4011 | 50.73 | 91.63%
[5 empty] | 50.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46183.3419 | 745705.0678 | 50.74 | 91.63%
[5 empty] | 50.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46195.1503 | 745895.7345 | 50.75 | 91.63%
[5 empty] | 50.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46206.9588 | 746086.4011 | 50.76 | 91.63%
[5 empty] | 50.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46218.7672 | 746277.0678 | 50.77 | 91.63%
[5 empty] | 50.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46230.5757 | 746467.7345 | 50.78 | 91.63%
[5 empty] | 50.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46242.3842 | 746658.4011 | 50.79 | 91.63%
[5 empty] | 50.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46254.1926 | 746849.0678 | 50.8 | 91.63%
[5 empty] | 50.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46266.0011 | 747039.7345 | 50.81 | 91.63%
[5 empty] | 50.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46277.8095 | 747230.4011 | 50.82 | 91.63%
[5 empty] | 50.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46289.618 | 747421.0678 | 50.83 | 91.63%
[5 empty] | 50.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46301.4264 | 747611.7345 | 50.84 | 91.63%
[5 empty] | 50.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46313.2349 | 747802.4011 | 50.85 | 91.63%
[5 empty] | 50.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46325.0433 | 747993.0678 | 50.86 | 91.63%
[5 empty] | 50.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46336.8518 | 748183.7345 | 50.87 | 91.63%
[5 empty] | 50.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46348.6602 | 748374.4011 | 50.88 | 91.63%
[5 empty] | 50.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46360.4687 | 748565.0678 | 50.89 | 91.63%
[5 empty] | 50.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46372.2771 | 748755.7345 | 50.9 | 91.63%
[5 empty] | 50.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46384.0856 | 748946.4011 | 50.91 | 91.63%
[5 empty] | 50.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46395.8941 | 749137.0678 | 50.92 | 91.63%
[5 empty] | 50.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46407.7025 | 749327.7345 | 50.93 | 91.63%
[5 empty] | 50.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46419.511 | 749518.4011 | 50.94 | 91.63%
[5 empty] | 50.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46431.3194 | 749709.0678 | 50.95 | 91.63%
[5 empty] | 50.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46443.1279 | 749899.7345 | 50.96 | 91.63%
[5 empty] | 50.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46454.9363 | 750090.4011 | 50.97 | 91.63%
[5 empty] | 50.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46466.7448 | 750281.0678 | 50.98 | 91.63%
[5 empty] | 50.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46478.5532 | 750471.7345 | 50.99 | 91.63%
[5 empty] | 51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46490.3617 | 750662.4011 | 51 | 91.63%
[5 empty] | 51.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46502.1701 | 750853.0678 | 51.01 | 91.63%
[5 empty] | 51.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46513.9786 | 751043.7345 | 51.02 | 91.63%
[5 empty] | 51.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46525.787 | 751234.4011 | 51.03 | 91.63%
[5 empty] | 51.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46537.5955 | 751425.0678 | 51.04 | 91.63%
[5 empty] | 51.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46549.404 | 751615.7345 | 51.05 | 91.63%
[5 empty] | 51.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46561.2124 | 751806.4011 | 51.06 | 91.63%
[5 empty] | 51.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46573.0209 | 751997.0678 | 51.07 | 91.63%
[5 empty] | 51.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46584.8293 | 752187.7345 | 51.08 | 91.63%
[5 empty] | 51.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46596.6378 | 752378.4011 | 51.09 | 91.63%
[5 empty] | 51.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46608.4462 | 752569.0678 | 51.1 | 91.63%
[5 empty] | 51.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46620.2547 | 752759.7345 | 51.11 | 91.63%
[5 empty] | 51.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46632.0631 | 752950.4011 | 51.12 | 91.63%
[5 empty] | 51.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46643.8716 | 753141.0678 | 51.13 | 91.63%
[5 empty] | 51.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46655.68 | 753331.7345 | 51.14 | 91.63%
[5 empty] | 51.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46667.4885 | 753522.4011 | 51.15 | 91.63%
[5 empty] | 51.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46679.2969 | 753713.0678 | 51.16 | 91.63%
[5 empty] | 51.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46691.1054 | 753903.7345 | 51.17 | 91.63%
[5 empty] | 51.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46702.9139 | 754094.4011 | 51.18 | 91.63%
[5 empty] | 51.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46714.7223 | 754285.0678 | 51.19 | 91.63%
[5 empty] | 51.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46726.5308 | 754475.7345 | 51.2 | 91.63%
[5 empty] | 51.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46738.3392 | 754666.4011 | 51.21 | 91.63%
[5 empty] | 51.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46750.1477 | 754857.0678 | 51.22 | 91.63%
[5 empty] | 51.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46761.9561 | 755047.7345 | 51.23 | 91.63%
[5 empty] | 51.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46773.7646 | 755238.4011 | 51.24 | 91.63%
[5 empty] | 51.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46785.573 | 755429.0678 | 51.25 | 91.63%
[5 empty] | 51.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46797.3815 | 755619.7345 | 51.26 | 91.63%
[5 empty] | 51.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46809.1899 | 755810.4011 | 51.27 | 91.63%
[5 empty] | 51.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46820.9984 | 756001.0678 | 51.28 | 91.63%
[5 empty] | 51.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46832.8068 | 756191.7345 | 51.29 | 91.63%
[5 empty] | 51.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46844.6153 | 756382.4011 | 51.3 | 91.63%
[5 empty] | 51.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46856.4238 | 756573.0678 | 51.31 | 91.63%
[5 empty] | 51.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46868.2322 | 756763.7345 | 51.32 | 91.63%
[5 empty] | 51.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46880.0407 | 756954.4011 | 51.33 | 91.63%
[5 empty] | 51.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46891.8491 | 757145.0678 | 51.34 | 91.63%
[5 empty] | 51.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46903.6576 | 757335.7345 | 51.35 | 91.63%
[5 empty] | 51.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46915.466 | 757526.4011 | 51.36 | 91.63%
[5 empty] | 51.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46927.2745 | 757717.0678 | 51.37 | 91.63%
[5 empty] | 51.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46939.0829 | 757907.7345 | 51.38 | 91.63%
[5 empty] | 51.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46950.8914 | 758098.4011 | 51.39 | 91.63%
[5 empty] | 51.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46962.6998 | 758289.0678 | 51.4 | 91.63%
[5 empty] | 51.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46974.5083 | 758479.7345 | 51.41 | 91.63%
[5 empty] | 51.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46986.3167 | 758670.4011 | 51.42 | 91.63%
[5 empty] | 51.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 46998.1252 | 758861.0678 | 51.43 | 91.63%
[5 empty] | 51.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47009.9337 | 759051.7345 | 51.44 | 91.63%
[5 empty] | 51.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47021.7421 | 759242.4011 | 51.45 | 91.63%
[5 empty] | 51.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47033.5506 | 759433.0678 | 51.46 | 91.63%
[5 empty] | 51.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47045.359 | 759623.7345 | 51.47 | 91.63%
[5 empty] | 51.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47057.1675 | 759814.4011 | 51.48 | 91.63%
[5 empty] | 51.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47068.9759 | 760005.0678 | 51.49 | 91.63%
[5 empty] | 51.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47080.7844 | 760195.7345 | 51.5 | 91.63%
[5 empty] | 51.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47092.5928 | 760386.4011 | 51.51 | 91.63%
[5 empty] | 51.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47104.4013 | 760577.0678 | 51.52 | 91.63%
[5 empty] | 51.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47116.2097 | 760767.7345 | 51.53 | 91.63%
[5 empty] | 51.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47128.0182 | 760958.4011 | 51.54 | 91.63%
[5 empty] | 51.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47139.8266 | 761149.0678 | 51.55 | 91.63%
[5 empty] | 51.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47151.6351 | 761339.7345 | 51.56 | 91.63%
[5 empty] | 51.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47163.4436 | 761530.4011 | 51.57 | 91.63%
[5 empty] | 51.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47175.252 | 761721.0678 | 51.58 | 91.63%
[5 empty] | 51.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47187.0605 | 761911.7345 | 51.59 | 91.63%
[5 empty] | 51.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47198.8689 | 762102.4011 | 51.6 | 91.63%
[5 empty] | 51.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47210.6774 | 762293.0678 | 51.61 | 91.63%
[5 empty] | 51.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47222.4858 | 762483.7345 | 51.62 | 91.63%
[5 empty] | 51.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47234.2943 | 762674.4011 | 51.63 | 91.63%
[5 empty] | 51.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47246.1027 | 762865.0678 | 51.64 | 91.63%
[5 empty] | 51.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47257.9112 | 763055.7345 | 51.65 | 91.63%
[5 empty] | 51.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47269.7196 | 763246.4011 | 51.66 | 91.63%
[5 empty] | 51.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47281.5281 | 763437.0678 | 51.67 | 91.63%
[5 empty] | 51.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47293.3365 | 763627.7345 | 51.68 | 91.63%
[5 empty] | 51.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47305.145 | 763818.4011 | 51.69 | 91.63%
[5 empty] | 51.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47316.9535 | 764009.0678 | 51.7 | 91.63%
[5 empty] | 51.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47328.7619 | 764199.7345 | 51.71 | 91.63%
[5 empty] | 51.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47340.5704 | 764390.4011 | 51.72 | 91.63%
[5 empty] | 51.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47352.3788 | 764581.0678 | 51.73 | 91.63%
[5 empty] | 51.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47364.1873 | 764771.7345 | 51.74 | 91.63%
[5 empty] | 51.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47375.9957 | 764962.4011 | 51.75 | 91.63%
[5 empty] | 51.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47387.8042 | 765153.0678 | 51.76 | 91.63%
[5 empty] | 51.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47399.6126 | 765343.7345 | 51.77 | 91.63%
[5 empty] | 51.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47411.4211 | 765534.4011 | 51.78 | 91.63%
[5 empty] | 51.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47423.2295 | 765725.0678 | 51.79 | 91.63%
[5 empty] | 51.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47435.038 | 765915.7345 | 51.8 | 91.63%
[5 empty] | 51.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47446.8464 | 766106.4011 | 51.81 | 91.63%
[5 empty] | 51.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47458.6549 | 766297.0678 | 51.82 | 91.63%
[5 empty] | 51.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47470.4634 | 766487.7345 | 51.83 | 91.63%
[5 empty] | 51.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47482.2718 | 766678.4011 | 51.84 | 91.63%
[5 empty] | 51.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47494.0803 | 766869.0678 | 51.85 | 91.63%
[5 empty] | 51.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47505.8887 | 767059.7345 | 51.86 | 91.63%
[5 empty] | 51.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47517.6972 | 767250.4011 | 51.87 | 91.63%
[5 empty] | 51.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47529.5056 | 767441.0678 | 51.88 | 91.63%
[5 empty] | 51.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47541.3141 | 767631.7345 | 51.89 | 91.63%
[5 empty] | 51.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47553.1225 | 767822.4011 | 51.9 | 91.63%
[5 empty] | 51.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47564.931 | 768013.0678 | 51.91 | 91.63%
[5 empty] | 51.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47576.7394 | 768203.7345 | 51.92 | 91.63%
[5 empty] | 51.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47588.5479 | 768394.4011 | 51.93 | 91.63%
[5 empty] | 51.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47600.3563 | 768585.0678 | 51.94 | 91.63%
[5 empty] | 51.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47612.1648 | 768775.7345 | 51.95 | 91.63%
[5 empty] | 51.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47623.9732 | 768966.4011 | 51.96 | 91.63%
[5 empty] | 51.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47635.7817 | 769157.0678 | 51.97 | 91.63%
[5 empty] | 51.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47647.5902 | 769347.7345 | 51.98 | 91.63%
[5 empty] | 51.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47659.3986 | 769538.4011 | 51.99 | 91.63%
[5 empty] | 52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47671.2071 | 769729.0678 | 52 | 91.63%
[5 empty] | 52.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47683.0155 | 769919.7345 | 52.01 | 91.63%
[5 empty] | 52.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47694.824 | 770110.4011 | 52.02 | 91.63%
[5 empty] | 52.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47706.6324 | 770301.0678 | 52.03 | 91.63%
[5 empty] | 52.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47718.4409 | 770491.7345 | 52.04 | 91.63%
[5 empty] | 52.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47730.2493 | 770682.4011 | 52.05 | 91.63%
[5 empty] | 52.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47742.0578 | 770873.0678 | 52.06 | 91.63%
[5 empty] | 52.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47753.8662 | 771063.7345 | 52.07 | 91.63%
[5 empty] | 52.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47765.6747 | 771254.4011 | 52.08 | 91.63%
[5 empty] | 52.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47777.4831 | 771445.0678 | 52.09 | 91.63%
[5 empty] | 52.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47789.2916 | 771635.7345 | 52.1 | 91.63%
[5 empty] | 52.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47801.1001 | 771826.4011 | 52.11 | 91.63%
[5 empty] | 52.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47812.9085 | 772017.0678 | 52.12 | 91.63%
[5 empty] | 52.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47824.717 | 772207.7345 | 52.13 | 91.63%
[5 empty] | 52.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47836.5254 | 772398.4011 | 52.14 | 91.63%
[5 empty] | 52.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47848.3339 | 772589.0678 | 52.15 | 91.63%
[5 empty] | 52.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47860.1423 | 772779.7345 | 52.16 | 91.63%
[5 empty] | 52.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47871.9508 | 772970.4011 | 52.17 | 91.63%
[5 empty] | 52.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47883.7592 | 773161.0678 | 52.18 | 91.63%
[5 empty] | 52.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47895.5677 | 773351.7345 | 52.19 | 91.63%
[5 empty] | 52.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47907.3761 | 773542.4011 | 52.2 | 91.63%
[5 empty] | 52.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47919.1846 | 773733.0678 | 52.21 | 91.63%
[5 empty] | 52.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47930.993 | 773923.7345 | 52.22 | 91.63%
[5 empty] | 52.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47942.8015 | 774114.4011 | 52.23 | 91.63%
[5 empty] | 52.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47954.61 | 774305.0678 | 52.24 | 91.63%
[5 empty] | 52.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47966.4184 | 774495.7345 | 52.25 | 91.63%
[5 empty] | 52.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47978.2269 | 774686.4011 | 52.26 | 91.63%
[5 empty] | 52.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 47990.0353 | 774877.0678 | 52.27 | 91.63%
[5 empty] | 52.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48001.8438 | 775067.7345 | 52.28 | 91.63%
[5 empty] | 52.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48013.6522 | 775258.4011 | 52.29 | 91.63%
[5 empty] | 52.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48025.4607 | 775449.0678 | 52.3 | 91.63%
[5 empty] | 52.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48037.2691 | 775639.7345 | 52.31 | 91.63%
[5 empty] | 52.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48049.0776 | 775830.4011 | 52.32 | 91.63%
[5 empty] | 52.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48060.886 | 776021.0678 | 52.33 | 91.63%
[5 empty] | 52.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48072.6945 | 776211.7345 | 52.34 | 91.63%
[5 empty] | 52.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48084.5029 | 776402.4011 | 52.35 | 91.63%
[5 empty] | 52.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48096.3114 | 776593.0678 | 52.36 | 91.63%
[5 empty] | 52.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48108.1199 | 776783.7345 | 52.37 | 91.63%
[5 empty] | 52.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48119.9283 | 776974.4011 | 52.38 | 91.63%
[5 empty] | 52.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48131.7368 | 777165.0678 | 52.39 | 91.63%
[5 empty] | 52.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48143.5452 | 777355.7345 | 52.4 | 91.63%
[5 empty] | 52.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48155.3537 | 777546.4011 | 52.41 | 91.63%
[5 empty] | 52.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48167.1621 | 777737.0678 | 52.42 | 91.63%
[5 empty] | 52.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48178.9706 | 777927.7345 | 52.43 | 91.63%
[5 empty] | 52.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48190.779 | 778118.4011 | 52.44 | 91.63%
[5 empty] | 52.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48202.5875 | 778309.0678 | 52.45 | 91.63%
[5 empty] | 52.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48214.3959 | 778499.7345 | 52.46 | 91.63%
[5 empty] | 52.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48226.2044 | 778690.4011 | 52.47 | 91.63%
[5 empty] | 52.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48238.0128 | 778881.0678 | 52.48 | 91.63%
[5 empty] | 52.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48249.8213 | 779071.7345 | 52.49 | 91.63%
[5 empty] | 52.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48261.6298 | 779262.4011 | 52.5 | 91.63%
[5 empty] | 52.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48273.4382 | 779453.0678 | 52.51 | 91.63%
[5 empty] | 52.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48285.2467 | 779643.7345 | 52.52 | 91.63%
[5 empty] | 52.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48297.0551 | 779834.4011 | 52.53 | 91.63%
[5 empty] | 52.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48308.8636 | 780025.0678 | 52.54 | 91.63%
[5 empty] | 52.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48320.672 | 780215.7345 | 52.55 | 91.63%
[5 empty] | 52.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48332.4805 | 780406.4011 | 52.56 | 91.63%
[5 empty] | 52.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48344.2889 | 780597.0678 | 52.57 | 91.63%
[5 empty] | 52.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48356.0974 | 780787.7345 | 52.58 | 91.63%
[5 empty] | 52.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48367.9058 | 780978.4011 | 52.59 | 91.63%
[5 empty] | 52.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48379.7143 | 781169.0678 | 52.6 | 91.63%
[5 empty] | 52.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48391.5227 | 781359.7345 | 52.61 | 91.63%
[5 empty] | 52.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48403.3312 | 781550.4011 | 52.62 | 91.63%
[5 empty] | 52.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48415.1397 | 781741.0678 | 52.63 | 91.63%
[5 empty] | 52.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48426.9481 | 781931.7345 | 52.64 | 91.63%
[5 empty] | 52.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48438.7566 | 782122.4011 | 52.65 | 91.63%
[5 empty] | 52.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48450.565 | 782313.0678 | 52.66 | 91.63%
[5 empty] | 52.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48462.3735 | 782503.7345 | 52.67 | 91.63%
[5 empty] | 52.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48474.1819 | 782694.4011 | 52.68 | 91.63%
[5 empty] | 52.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48485.9904 | 782885.0678 | 52.69 | 91.63%
[5 empty] | 52.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48497.7988 | 783075.7345 | 52.7 | 91.63%
[5 empty] | 52.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48509.6073 | 783266.4011 | 52.71 | 91.63%
[5 empty] | 52.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48521.4157 | 783457.0678 | 52.72 | 91.63%
[5 empty] | 52.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48533.2242 | 783647.7345 | 52.73 | 91.63%
[5 empty] | 52.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48545.0326 | 783838.4011 | 52.74 | 91.63%
[5 empty] | 52.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48556.8411 | 784029.0678 | 52.75 | 91.63%
[5 empty] | 52.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48568.6496 | 784219.7345 | 52.76 | 91.63%
[5 empty] | 52.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48580.458 | 784410.4011 | 52.77 | 91.63%
[5 empty] | 52.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48592.2665 | 784601.0678 | 52.78 | 91.63%
[5 empty] | 52.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48604.0749 | 784791.7345 | 52.79 | 91.63%
[5 empty] | 52.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48615.8834 | 784982.4011 | 52.8 | 91.63%
[5 empty] | 52.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48627.6918 | 785173.0678 | 52.81 | 91.63%
[5 empty] | 52.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48639.5003 | 785363.7345 | 52.82 | 91.63%
[5 empty] | 52.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48651.3087 | 785554.4011 | 52.83 | 91.63%
[5 empty] | 52.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48663.1172 | 785745.0678 | 52.84 | 91.63%
[5 empty] | 52.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48674.9256 | 785935.7345 | 52.85 | 91.63%
[5 empty] | 52.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48686.7341 | 786126.4011 | 52.86 | 91.63%
[5 empty] | 52.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48698.5425 | 786317.0678 | 52.87 | 91.63%
[5 empty] | 52.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48710.351 | 786507.7345 | 52.88 | 91.63%
[5 empty] | 52.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48722.1595 | 786698.4011 | 52.89 | 91.63%
[5 empty] | 52.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48733.9679 | 786889.0678 | 52.9 | 91.63%
[5 empty] | 52.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48745.7764 | 787079.7345 | 52.91 | 91.63%
[5 empty] | 52.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48757.5848 | 787270.4011 | 52.92 | 91.63%
[5 empty] | 52.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48769.3933 | 787461.0678 | 52.93 | 91.63%
[5 empty] | 52.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48781.2017 | 787651.7345 | 52.94 | 91.63%
[5 empty] | 52.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48793.0102 | 787842.4011 | 52.95 | 91.63%
[5 empty] | 52.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48804.8186 | 788033.0678 | 52.96 | 91.63%
[5 empty] | 52.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48816.6271 | 788223.7345 | 52.97 | 91.63%
[5 empty] | 52.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48828.4355 | 788414.4011 | 52.98 | 91.63%
[5 empty] | 52.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48840.244 | 788605.0678 | 52.99 | 91.63%
[5 empty] | 53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48852.0524 | 788795.7345 | 53 | 91.63%
[5 empty] | 53.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48863.8609 | 788986.4011 | 53.01 | 91.63%
[5 empty] | 53.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48875.6694 | 789177.0678 | 53.02 | 91.63%
[5 empty] | 53.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48887.4778 | 789367.7345 | 53.03 | 91.63%
[5 empty] | 53.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48899.2863 | 789558.4011 | 53.04 | 91.63%
[5 empty] | 53.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48911.0947 | 789749.0678 | 53.05 | 91.63%
[5 empty] | 53.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48922.9032 | 789939.7345 | 53.06 | 91.63%
[5 empty] | 53.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48934.7116 | 790130.4011 | 53.07 | 91.63%
[5 empty] | 53.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48946.5201 | 790321.0678 | 53.08 | 91.63%
[5 empty] | 53.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48958.3285 | 790511.7345 | 53.09 | 91.63%
[5 empty] | 53.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48970.137 | 790702.4011 | 53.1 | 91.63%
[5 empty] | 53.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48981.9454 | 790893.0678 | 53.11 | 91.63%
[5 empty] | 53.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 48993.7539 | 791083.7345 | 53.12 | 91.63%
[5 empty] | 53.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49005.5623 | 791274.4011 | 53.13 | 91.63%
[5 empty] | 53.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49017.3708 | 791465.0678 | 53.14 | 91.63%
[5 empty] | 53.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49029.1793 | 791655.7345 | 53.15 | 91.63%
[5 empty] | 53.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49040.9877 | 791846.4011 | 53.16 | 91.63%
[5 empty] | 53.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49052.7962 | 792037.0678 | 53.17 | 91.63%
[5 empty] | 53.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49064.6046 | 792227.7345 | 53.18 | 91.63%
[5 empty] | 53.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49076.4131 | 792418.4011 | 53.19 | 91.63%
[5 empty] | 53.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49088.2215 | 792609.0678 | 53.2 | 91.63%
[5 empty] | 53.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49100.03 | 792799.7345 | 53.21 | 91.63%
[5 empty] | 53.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49111.8384 | 792990.4011 | 53.22 | 91.63%
[5 empty] | 53.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49123.6469 | 793181.0678 | 53.23 | 91.63%
[5 empty] | 53.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49135.4553 | 793371.7345 | 53.24 | 91.63%
[5 empty] | 53.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49147.2638 | 793562.4011 | 53.25 | 91.63%
[5 empty] | 53.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49159.0722 | 793753.0678 | 53.26 | 91.63%
[5 empty] | 53.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49170.8807 | 793943.7345 | 53.27 | 91.63%
[5 empty] | 53.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49182.6892 | 794134.4011 | 53.28 | 91.63%
[5 empty] | 53.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49194.4976 | 794325.0678 | 53.29 | 91.63%
[5 empty] | 53.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49206.3061 | 794515.7345 | 53.3 | 91.63%
[5 empty] | 53.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49218.1145 | 794706.4011 | 53.31 | 91.63%
[5 empty] | 53.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49229.923 | 794897.0678 | 53.32 | 91.63%
[5 empty] | 53.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49241.7314 | 795087.7345 | 53.33 | 91.63%
[5 empty] | 53.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49253.5399 | 795278.4011 | 53.34 | 91.63%
[5 empty] | 53.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49265.3483 | 795469.0678 | 53.35 | 91.63%
[5 empty] | 53.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49277.1568 | 795659.7345 | 53.36 | 91.63%
[5 empty] | 53.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49288.9652 | 795850.4011 | 53.37 | 91.63%
[5 empty] | 53.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49300.7737 | 796041.0678 | 53.38 | 91.63%
[5 empty] | 53.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49312.5821 | 796231.7345 | 53.39 | 91.63%
[5 empty] | 53.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49324.3906 | 796422.4011 | 53.4 | 91.63%
[5 empty] | 53.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49336.1991 | 796613.0678 | 53.41 | 91.63%
[5 empty] | 53.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49348.0075 | 796803.7345 | 53.42 | 91.63%
[5 empty] | 53.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49359.816 | 796994.4011 | 53.43 | 91.63%
[5 empty] | 53.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49371.6244 | 797185.0678 | 53.44 | 91.63%
[5 empty] | 53.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49383.4329 | 797375.7345 | 53.45 | 91.63%
[5 empty] | 53.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49395.2413 | 797566.4011 | 53.46 | 91.63%
[5 empty] | 53.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49407.0498 | 797757.0678 | 53.47 | 91.63%
[5 empty] | 53.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49418.8582 | 797947.7345 | 53.48 | 91.63%
[5 empty] | 53.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49430.6667 | 798138.4011 | 53.49 | 91.63%
[5 empty] | 53.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49442.4751 | 798329.0678 | 53.5 | 91.63%
[5 empty] | 53.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49454.2836 | 798519.7345 | 53.51 | 91.63%
[5 empty] | 53.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49466.092 | 798710.4011 | 53.52 | 91.63%
[5 empty] | 53.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49477.9005 | 798901.0678 | 53.53 | 91.63%
[5 empty] | 53.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49489.709 | 799091.7345 | 53.54 | 91.63%
[5 empty] | 53.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49501.5174 | 799282.4011 | 53.55 | 91.63%
[5 empty] | 53.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49513.3259 | 799473.0678 | 53.56 | 91.63%
[5 empty] | 53.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49525.1343 | 799663.7345 | 53.57 | 91.63%
[5 empty] | 53.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49536.9428 | 799854.4011 | 53.58 | 91.63%
[5 empty] | 53.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49548.7512 | 800045.0678 | 53.59 | 91.63%
[5 empty] | 53.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49560.5597 | 800235.7345 | 53.6 | 91.63%
[5 empty] | 53.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49572.3681 | 800426.4011 | 53.61 | 91.63%
[5 empty] | 53.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49584.1766 | 800617.0678 | 53.62 | 91.63%
[5 empty] | 53.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49595.985 | 800807.7345 | 53.63 | 91.63%
[5 empty] | 53.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49607.7935 | 800998.4011 | 53.64 | 91.63%
[5 empty] | 53.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49619.6019 | 801189.0678 | 53.65 | 91.63%
[5 empty] | 53.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49631.4104 | 801379.7345 | 53.66 | 91.63%
[5 empty] | 53.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49643.2189 | 801570.4011 | 53.67 | 91.63%
[5 empty] | 53.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49655.0273 | 801761.0678 | 53.68 | 91.63%
[5 empty] | 53.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49666.8358 | 801951.7345 | 53.69 | 91.63%
[5 empty] | 53.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49678.6442 | 802142.4011 | 53.7 | 91.63%
[5 empty] | 53.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49690.4527 | 802333.0678 | 53.71 | 91.63%
[5 empty] | 53.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49702.2611 | 802523.7345 | 53.72 | 91.63%
[5 empty] | 53.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49714.0696 | 802714.4011 | 53.73 | 91.63%
[5 empty] | 53.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49725.878 | 802905.0678 | 53.74 | 91.63%
[5 empty] | 53.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49737.6865 | 803095.7345 | 53.75 | 91.63%
[5 empty] | 53.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49749.4949 | 803286.4011 | 53.76 | 91.63%
[5 empty] | 53.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49761.3034 | 803477.0678 | 53.77 | 91.63%
[5 empty] | 53.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49773.1118 | 803667.7345 | 53.78 | 91.63%
[5 empty] | 53.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49784.9203 | 803858.4011 | 53.79 | 91.63%
[5 empty] | 53.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49796.7288 | 804049.0678 | 53.8 | 91.63%
[5 empty] | 53.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49808.5372 | 804239.7345 | 53.81 | 91.63%
[5 empty] | 53.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49820.3457 | 804430.4011 | 53.82 | 91.63%
[5 empty] | 53.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49832.1541 | 804621.0678 | 53.83 | 91.63%
[5 empty] | 53.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49843.9626 | 804811.7345 | 53.84 | 91.63%
[5 empty] | 53.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49855.771 | 805002.4011 | 53.85 | 91.63%
[5 empty] | 53.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49867.5795 | 805193.0678 | 53.86 | 91.63%
[5 empty] | 53.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49879.3879 | 805383.7345 | 53.87 | 91.63%
[5 empty] | 53.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49891.1964 | 805574.4011 | 53.88 | 91.63%
[5 empty] | 53.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49903.0048 | 805765.0678 | 53.89 | 91.63%
[5 empty] | 53.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49914.8133 | 805955.7345 | 53.9 | 91.63%
[5 empty] | 53.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49926.6217 | 806146.4011 | 53.91 | 91.63%
[5 empty] | 53.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49938.4302 | 806337.0678 | 53.92 | 91.63%
[5 empty] | 53.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49950.2387 | 806527.7345 | 53.93 | 91.63%
[5 empty] | 53.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49962.0471 | 806718.4011 | 53.94 | 91.63%
[5 empty] | 53.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49973.8556 | 806909.0678 | 53.95 | 91.63%
[5 empty] | 53.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49985.664 | 807099.7345 | 53.96 | 91.63%
[5 empty] | 53.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 49997.4725 | 807290.4011 | 53.97 | 91.63%
[5 empty] | 53.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50009.2809 | 807481.0678 | 53.98 | 91.63%
[5 empty] | 53.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50021.0894 | 807671.7345 | 53.99 | 91.63%
[5 empty] | 54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50032.8978 | 807862.4011 | 54 | 91.63%
[5 empty] | 54.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50044.7063 | 808053.0678 | 54.01 | 91.63%
[5 empty] | 54.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50056.5147 | 808243.7345 | 54.02 | 91.63%
[5 empty] | 54.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50068.3232 | 808434.4011 | 54.03 | 91.63%
[5 empty] | 54.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50080.1316 | 808625.0678 | 54.04 | 91.63%
[5 empty] | 54.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50091.9401 | 808815.7345 | 54.05 | 91.63%
[5 empty] | 54.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50103.7486 | 809006.4011 | 54.06 | 91.63%
[5 empty] | 54.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50115.557 | 809197.0678 | 54.07 | 91.63%
[5 empty] | 54.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50127.3655 | 809387.7345 | 54.08 | 91.63%
[5 empty] | 54.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50139.1739 | 809578.4011 | 54.09 | 91.63%
[5 empty] | 54.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50150.9824 | 809769.0678 | 54.1 | 91.63%
[5 empty] | 54.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50162.7908 | 809959.7345 | 54.11 | 91.63%
[5 empty] | 54.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50174.5993 | 810150.4011 | 54.12 | 91.63%
[5 empty] | 54.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50186.4077 | 810341.0678 | 54.13 | 91.63%
[5 empty] | 54.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50198.2162 | 810531.7345 | 54.14 | 91.63%
[5 empty] | 54.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50210.0246 | 810722.4011 | 54.15 | 91.63%
[5 empty] | 54.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50221.8331 | 810913.0678 | 54.16 | 91.63%
[5 empty] | 54.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50233.6415 | 811103.7345 | 54.17 | 91.63%
[5 empty] | 54.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50245.45 | 811294.4011 | 54.18 | 91.63%
[5 empty] | 54.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50257.2585 | 811485.0678 | 54.19 | 91.63%
[5 empty] | 54.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50269.0669 | 811675.7345 | 54.2 | 91.63%
[5 empty] | 54.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50280.8754 | 811866.4011 | 54.21 | 91.63%
[5 empty] | 54.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50292.6838 | 812057.0678 | 54.22 | 91.63%
[5 empty] | 54.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50304.4923 | 812247.7345 | 54.23 | 91.63%
[5 empty] | 54.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50316.3007 | 812438.4011 | 54.24 | 91.63%
[5 empty] | 54.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50328.1092 | 812629.0678 | 54.25 | 91.63%
[5 empty] | 54.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50339.9176 | 812819.7345 | 54.26 | 91.63%
[5 empty] | 54.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50351.7261 | 813010.4011 | 54.27 | 91.63%
[5 empty] | 54.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50363.5345 | 813201.0678 | 54.28 | 91.63%
[5 empty] | 54.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50375.343 | 813391.7345 | 54.29 | 91.63%
[5 empty] | 54.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50387.1514 | 813582.4011 | 54.3 | 91.63%
[5 empty] | 54.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50398.9599 | 813773.0678 | 54.31 | 91.63%
[5 empty] | 54.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50410.7684 | 813963.7345 | 54.32 | 91.63%
[5 empty] | 54.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50422.5768 | 814154.4011 | 54.33 | 91.63%
[5 empty] | 54.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50434.3853 | 814345.0678 | 54.34 | 91.63%
[5 empty] | 54.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50446.1937 | 814535.7345 | 54.35 | 91.63%
[5 empty] | 54.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50458.0022 | 814726.4011 | 54.36 | 91.63%
[5 empty] | 54.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50469.8106 | 814917.0678 | 54.37 | 91.63%
[5 empty] | 54.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50481.6191 | 815107.7345 | 54.38 | 91.63%
[5 empty] | 54.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50493.4275 | 815298.4011 | 54.39 | 91.63%
[5 empty] | 54.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50505.236 | 815489.0678 | 54.4 | 91.63%
[5 empty] | 54.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50517.0444 | 815679.7345 | 54.41 | 91.63%
[5 empty] | 54.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50528.8529 | 815870.4011 | 54.42 | 91.63%
[5 empty] | 54.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50540.6613 | 816061.0678 | 54.43 | 91.63%
[5 empty] | 54.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50552.4698 | 816251.7345 | 54.44 | 91.63%
[5 empty] | 54.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50564.2782 | 816442.4011 | 54.45 | 91.63%
[5 empty] | 54.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50576.0867 | 816633.0678 | 54.46 | 91.63%
[5 empty] | 54.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50587.8952 | 816823.7345 | 54.47 | 91.63%
[5 empty] | 54.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50599.7036 | 817014.4011 | 54.48 | 91.63%
[5 empty] | 54.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50611.5121 | 817205.0678 | 54.49 | 91.63%
[5 empty] | 54.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50623.3205 | 817395.7345 | 54.5 | 91.63%
[5 empty] | 54.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50635.129 | 817586.4011 | 54.51 | 91.63%
[5 empty] | 54.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50646.9374 | 817777.0678 | 54.52 | 91.63%
[5 empty] | 54.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50658.7459 | 817967.7345 | 54.53 | 91.63%
[5 empty] | 54.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50670.5543 | 818158.4011 | 54.54 | 91.63%
[5 empty] | 54.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50682.3628 | 818349.0678 | 54.55 | 91.63%
[5 empty] | 54.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50694.1712 | 818539.7345 | 54.56 | 91.63%
[5 empty] | 54.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50705.9797 | 818730.4011 | 54.57 | 91.63%
[5 empty] | 54.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50717.7881 | 818921.0678 | 54.58 | 91.63%
[5 empty] | 54.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50729.5966 | 819111.7345 | 54.59 | 91.63%
[5 empty] | 54.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50741.4051 | 819302.4011 | 54.6 | 91.63%
[5 empty] | 54.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50753.2135 | 819493.0678 | 54.61 | 91.63%
[5 empty] | 54.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50765.022 | 819683.7345 | 54.62 | 91.63%
[5 empty] | 54.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50776.8304 | 819874.4011 | 54.63 | 91.63%
[5 empty] | 54.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50788.6389 | 820065.0678 | 54.64 | 91.63%
[5 empty] | 54.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50800.4473 | 820255.7345 | 54.65 | 91.63%
[5 empty] | 54.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50812.2558 | 820446.4011 | 54.66 | 91.63%
[5 empty] | 54.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50824.0642 | 820637.0678 | 54.67 | 91.63%
[5 empty] | 54.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50835.8727 | 820827.7345 | 54.68 | 91.63%
[5 empty] | 54.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50847.6811 | 821018.4011 | 54.69 | 91.63%
[5 empty] | 54.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50859.4896 | 821209.0678 | 54.7 | 91.63%
[5 empty] | 54.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50871.298 | 821399.7345 | 54.71 | 91.63%
[5 empty] | 54.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50883.1065 | 821590.4011 | 54.72 | 91.63%
[5 empty] | 54.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50894.915 | 821781.0678 | 54.73 | 91.63%
[5 empty] | 54.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50906.7234 | 821971.7345 | 54.74 | 91.63%
[5 empty] | 54.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50918.5319 | 822162.4011 | 54.75 | 91.63%
[5 empty] | 54.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50930.3403 | 822353.0678 | 54.76 | 91.63%
[5 empty] | 54.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50942.1488 | 822543.7345 | 54.77 | 91.63%
[5 empty] | 54.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50953.9572 | 822734.4011 | 54.78 | 91.63%
[5 empty] | 54.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50965.7657 | 822925.0678 | 54.79 | 91.63%
[5 empty] | 54.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50977.5741 | 823115.7345 | 54.8 | 91.63%
[5 empty] | 54.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 50989.3826 | 823306.4011 | 54.81 | 91.63%
[5 empty] | 54.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51001.191 | 823497.0678 | 54.82 | 91.63%
[5 empty] | 54.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51012.9995 | 823687.7345 | 54.83 | 91.63%
[5 empty] | 54.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51024.8079 | 823878.4011 | 54.84 | 91.63%
[5 empty] | 54.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51036.6164 | 824069.0678 | 54.85 | 91.63%
[5 empty] | 54.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51048.4249 | 824259.7345 | 54.86 | 91.63%
[5 empty] | 54.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51060.2333 | 824450.4011 | 54.87 | 91.63%
[5 empty] | 54.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51072.0418 | 824641.0678 | 54.88 | 91.63%
[5 empty] | 54.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51083.8502 | 824831.7345 | 54.89 | 91.63%
[5 empty] | 54.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51095.6587 | 825022.4011 | 54.9 | 91.63%
[5 empty] | 54.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51107.4671 | 825213.0678 | 54.91 | 91.63%
[5 empty] | 54.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51119.2756 | 825403.7345 | 54.92 | 91.63%
[5 empty] | 54.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51131.084 | 825594.4011 | 54.93 | 91.63%
[5 empty] | 54.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51142.8925 | 825785.0678 | 54.94 | 91.63%
[5 empty] | 54.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51154.7009 | 825975.7345 | 54.95 | 91.63%
[5 empty] | 54.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51166.5094 | 826166.4011 | 54.96 | 91.63%
[5 empty] | 54.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51178.3178 | 826357.0678 | 54.97 | 91.63%
[5 empty] | 54.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51190.1263 | 826547.7345 | 54.98 | 91.63%
[5 empty] | 54.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51201.9348 | 826738.4011 | 54.99 | 91.63%
[5 empty] | 55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51213.7432 | 826929.0678 | 55 | 91.63%
[5 empty] | 55.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51225.5517 | 827119.7345 | 55.01 | 91.63%
[5 empty] | 55.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51237.3601 | 827310.4011 | 55.02 | 91.63%
[5 empty] | 55.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51249.1686 | 827501.0678 | 55.03 | 91.63%
[5 empty] | 55.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51260.977 | 827691.7345 | 55.04 | 91.63%
[5 empty] | 55.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51272.7855 | 827882.4011 | 55.05 | 91.63%
[5 empty] | 55.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51284.5939 | 828073.0678 | 55.06 | 91.63%
[5 empty] | 55.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51296.4024 | 828263.7345 | 55.07 | 91.63%
[5 empty] | 55.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51308.2108 | 828454.4011 | 55.08 | 91.63%
[5 empty] | 55.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51320.0193 | 828645.0678 | 55.09 | 91.63%
[5 empty] | 55.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51331.8277 | 828835.7345 | 55.1 | 91.63%
[5 empty] | 55.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51343.6362 | 829026.4011 | 55.11 | 91.63%
[5 empty] | 55.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51355.4447 | 829217.0678 | 55.12 | 91.63%
[5 empty] | 55.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51367.2531 | 829407.7345 | 55.13 | 91.63%
[5 empty] | 55.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51379.0616 | 829598.4011 | 55.14 | 91.63%
[5 empty] | 55.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51390.87 | 829789.0678 | 55.15 | 91.63%
[5 empty] | 55.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51402.6785 | 829979.7345 | 55.16 | 91.63%
[5 empty] | 55.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51414.4869 | 830170.4011 | 55.17 | 91.63%
[5 empty] | 55.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51426.2954 | 830361.0678 | 55.18 | 91.63%
[5 empty] | 55.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51438.1038 | 830551.7345 | 55.19 | 91.63%
[5 empty] | 55.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51449.9123 | 830742.4011 | 55.2 | 91.63%
[5 empty] | 55.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51461.7207 | 830933.0678 | 55.21 | 91.63%
[5 empty] | 55.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51473.5292 | 831123.7345 | 55.22 | 91.63%
[5 empty] | 55.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51485.3376 | 831314.4011 | 55.23 | 91.63%
[5 empty] | 55.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51497.1461 | 831505.0678 | 55.24 | 91.63%
[5 empty] | 55.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51508.9546 | 831695.7345 | 55.25 | 91.63%
[5 empty] | 55.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51520.763 | 831886.4011 | 55.26 | 91.63%
[5 empty] | 55.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51532.5715 | 832077.0678 | 55.27 | 91.63%
[5 empty] | 55.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51544.3799 | 832267.7345 | 55.28 | 91.63%
[5 empty] | 55.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51556.1884 | 832458.4011 | 55.29 | 91.63%
[5 empty] | 55.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51567.9968 | 832649.0678 | 55.3 | 91.63%
[5 empty] | 55.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51579.8053 | 832839.7345 | 55.31 | 91.63%
[5 empty] | 55.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51591.6137 | 833030.4011 | 55.32 | 91.63%
[5 empty] | 55.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51603.4222 | 833221.0678 | 55.33 | 91.63%
[5 empty] | 55.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51615.2306 | 833411.7345 | 55.34 | 91.63%
[5 empty] | 55.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51627.0391 | 833602.4011 | 55.35 | 91.63%
[5 empty] | 55.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51638.8475 | 833793.0678 | 55.36 | 91.63%
[5 empty] | 55.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51650.656 | 833983.7345 | 55.37 | 91.63%
[5 empty] | 55.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51662.4645 | 834174.4011 | 55.38 | 91.63%
[5 empty] | 55.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51674.2729 | 834365.0678 | 55.39 | 91.63%
[5 empty] | 55.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51686.0814 | 834555.7345 | 55.4 | 91.63%
[5 empty] | 55.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51697.8898 | 834746.4011 | 55.41 | 91.63%
[5 empty] | 55.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51709.6983 | 834937.0678 | 55.42 | 91.63%
[5 empty] | 55.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51721.5067 | 835127.7345 | 55.43 | 91.63%
[5 empty] | 55.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51733.3152 | 835318.4011 | 55.44 | 91.63%
[5 empty] | 55.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51745.1236 | 835509.0678 | 55.45 | 91.63%
[5 empty] | 55.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51756.9321 | 835699.7345 | 55.46 | 91.63%
[5 empty] | 55.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51768.7405 | 835890.4011 | 55.47 | 91.63%
[5 empty] | 55.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51780.549 | 836081.0678 | 55.48 | 91.63%
[5 empty] | 55.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51792.3574 | 836271.7345 | 55.49 | 91.63%
[5 empty] | 55.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51804.1659 | 836462.4011 | 55.5 | 91.63%
[5 empty] | 55.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51815.9744 | 836653.0678 | 55.51 | 91.63%
[5 empty] | 55.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51827.7828 | 836843.7345 | 55.52 | 91.63%
[5 empty] | 55.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51839.5913 | 837034.4011 | 55.53 | 91.63%
[5 empty] | 55.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51851.3997 | 837225.0678 | 55.54 | 91.63%
[5 empty] | 55.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51863.2082 | 837415.7345 | 55.55 | 91.63%
[5 empty] | 55.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51875.0166 | 837606.4011 | 55.56 | 91.63%
[5 empty] | 55.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51886.8251 | 837797.0678 | 55.57 | 91.63%
[5 empty] | 55.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51898.6335 | 837987.7345 | 55.58 | 91.63%
[5 empty] | 55.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51910.442 | 838178.4011 | 55.59 | 91.63%
[5 empty] | 55.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51922.2504 | 838369.0678 | 55.6 | 91.63%
[5 empty] | 55.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51934.0589 | 838559.7345 | 55.61 | 91.63%
[5 empty] | 55.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51945.8673 | 838750.4011 | 55.62 | 91.63%
[5 empty] | 55.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51957.6758 | 838941.0678 | 55.63 | 91.63%
[5 empty] | 55.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51969.4843 | 839131.7345 | 55.64 | 91.63%
[5 empty] | 55.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51981.2927 | 839322.4011 | 55.65 | 91.63%
[5 empty] | 55.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 51993.1012 | 839513.0678 | 55.66 | 91.63%
[5 empty] | 55.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52004.9096 | 839703.7345 | 55.67 | 91.63%
[5 empty] | 55.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52016.7181 | 839894.4011 | 55.68 | 91.63%
[5 empty] | 55.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52028.5265 | 840085.0678 | 55.69 | 91.63%
[5 empty] | 55.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52040.335 | 840275.7345 | 55.7 | 91.63%
[5 empty] | 55.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52052.1434 | 840466.4011 | 55.71 | 91.63%
[5 empty] | 55.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52063.9519 | 840657.0678 | 55.72 | 91.63%
[5 empty] | 55.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52075.7603 | 840847.7345 | 55.73 | 91.63%
[5 empty] | 55.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52087.5688 | 841038.4011 | 55.74 | 91.63%
[5 empty] | 55.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52099.3772 | 841229.0678 | 55.75 | 91.63%
[5 empty] | 55.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52111.1857 | 841419.7345 | 55.76 | 91.63%
[5 empty] | 55.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52122.9942 | 841610.4011 | 55.77 | 91.63%
[5 empty] | 55.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52134.8026 | 841801.0678 | 55.78 | 91.63%
[5 empty] | 55.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52146.6111 | 841991.7345 | 55.79 | 91.63%
[5 empty] | 55.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52158.4195 | 842182.4011 | 55.8 | 91.63%
[5 empty] | 55.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52170.228 | 842373.0678 | 55.81 | 91.63%
[5 empty] | 55.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52182.0364 | 842563.7345 | 55.82 | 91.63%
[5 empty] | 55.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52193.8449 | 842754.4011 | 55.83 | 91.63%
[5 empty] | 55.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52205.6533 | 842945.0678 | 55.84 | 91.63%
[5 empty] | 55.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52217.4618 | 843135.7345 | 55.85 | 91.63%
[5 empty] | 55.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52229.2702 | 843326.4011 | 55.86 | 91.63%
[5 empty] | 55.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52241.0787 | 843517.0678 | 55.87 | 91.63%
[5 empty] | 55.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52252.8871 | 843707.7345 | 55.88 | 91.63%
[5 empty] | 55.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52264.6956 | 843898.4011 | 55.89 | 91.63%
[5 empty] | 55.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52276.5041 | 844089.0678 | 55.9 | 91.63%
[5 empty] | 55.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52288.3125 | 844279.7345 | 55.91 | 91.63%
[5 empty] | 55.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52300.121 | 844470.4011 | 55.92 | 91.63%
[5 empty] | 55.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52311.9294 | 844661.0678 | 55.93 | 91.63%
[5 empty] | 55.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52323.7379 | 844851.7345 | 55.94 | 91.63%
[5 empty] | 55.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52335.5463 | 845042.4011 | 55.95 | 91.63%
[5 empty] | 55.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52347.3548 | 845233.0678 | 55.96 | 91.63%
[5 empty] | 55.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52359.1632 | 845423.7345 | 55.97 | 91.63%
[5 empty] | 55.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52370.9717 | 845614.4011 | 55.98 | 91.63%
[5 empty] | 55.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52382.7801 | 845805.0678 | 55.99 | 91.63%
[5 empty] | 56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52394.5886 | 845995.7345 | 56 | 91.63%
[5 empty] | 56.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52406.397 | 846186.4011 | 56.01 | 91.63%
[5 empty] | 56.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52418.2055 | 846377.0678 | 56.02 | 91.63%
[5 empty] | 56.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52430.014 | 846567.7345 | 56.03 | 91.63%
[5 empty] | 56.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52441.8224 | 846758.4011 | 56.04 | 91.63%
[5 empty] | 56.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52453.6309 | 846949.0678 | 56.05 | 91.63%
[5 empty] | 56.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52465.4393 | 847139.7345 | 56.06 | 91.63%
[5 empty] | 56.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52477.2478 | 847330.4011 | 56.07 | 91.63%
[5 empty] | 56.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52489.0562 | 847521.0678 | 56.08 | 91.63%
[5 empty] | 56.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52500.8647 | 847711.7345 | 56.09 | 91.63%
[5 empty] | 56.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52512.6731 | 847902.4011 | 56.1 | 91.63%
[5 empty] | 56.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52524.4816 | 848093.0678 | 56.11 | 91.63%
[5 empty] | 56.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52536.29 | 848283.7345 | 56.12 | 91.63%
[5 empty] | 56.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52548.0985 | 848474.4011 | 56.13 | 91.63%
[5 empty] | 56.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52559.9069 | 848665.0678 | 56.14 | 91.63%
[5 empty] | 56.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52571.7154 | 848855.7345 | 56.15 | 91.63%
[5 empty] | 56.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52583.5239 | 849046.4011 | 56.16 | 91.63%
[5 empty] | 56.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52595.3323 | 849237.0678 | 56.17 | 91.63%
[5 empty] | 56.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52607.1408 | 849427.7345 | 56.18 | 91.63%
[5 empty] | 56.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52618.9492 | 849618.4011 | 56.19 | 91.63%
[5 empty] | 56.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52630.7577 | 849809.0678 | 56.2 | 91.63%
[5 empty] | 56.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52642.5661 | 849999.7345 | 56.21 | 91.63%
[5 empty] | 56.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52654.3746 | 850190.4011 | 56.22 | 91.63%
[5 empty] | 56.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52666.183 | 850381.0678 | 56.23 | 91.63%
[5 empty] | 56.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52677.9915 | 850571.7345 | 56.24 | 91.63%
[5 empty] | 56.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52689.7999 | 850762.4011 | 56.25 | 91.63%
[5 empty] | 56.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52701.6084 | 850953.0678 | 56.26 | 91.63%
[5 empty] | 56.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52713.4168 | 851143.7345 | 56.27 | 91.63%
[5 empty] | 56.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52725.2253 | 851334.4011 | 56.28 | 91.63%
[5 empty] | 56.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52737.0338 | 851525.0678 | 56.29 | 91.63%
[5 empty] | 56.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52748.8422 | 851715.7345 | 56.3 | 91.63%
[5 empty] | 56.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52760.6507 | 851906.4011 | 56.31 | 91.63%
[5 empty] | 56.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52772.4591 | 852097.0678 | 56.32 | 91.63%
[5 empty] | 56.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52784.2676 | 852287.7345 | 56.33 | 91.63%
[5 empty] | 56.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52796.076 | 852478.4011 | 56.34 | 91.63%
[5 empty] | 56.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52807.8845 | 852669.0678 | 56.35 | 91.63%
[5 empty] | 56.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52819.6929 | 852859.7345 | 56.36 | 91.63%
[5 empty] | 56.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52831.5014 | 853050.4011 | 56.37 | 91.63%
[5 empty] | 56.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52843.3098 | 853241.0678 | 56.38 | 91.63%
[5 empty] | 56.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52855.1183 | 853431.7345 | 56.39 | 91.63%
[5 empty] | 56.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52866.9267 | 853622.4011 | 56.4 | 91.63%
[5 empty] | 56.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52878.7352 | 853813.0678 | 56.41 | 91.63%
[5 empty] | 56.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52890.5437 | 854003.7345 | 56.42 | 91.63%
[5 empty] | 56.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52902.3521 | 854194.4011 | 56.43 | 91.63%
[5 empty] | 56.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52914.1606 | 854385.0678 | 56.44 | 91.63%
[5 empty] | 56.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52925.969 | 854575.7345 | 56.45 | 91.63%
[5 empty] | 56.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52937.7775 | 854766.4011 | 56.46 | 91.63%
[5 empty] | 56.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52949.5859 | 854957.0678 | 56.47 | 91.63%
[5 empty] | 56.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52961.3944 | 855147.7345 | 56.48 | 91.63%
[5 empty] | 56.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52973.2028 | 855338.4011 | 56.49 | 91.63%
[5 empty] | 56.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52985.0113 | 855529.0678 | 56.5 | 91.63%
[5 empty] | 56.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 52996.8197 | 855719.7345 | 56.51 | 91.63%
[5 empty] | 56.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53008.6282 | 855910.4011 | 56.52 | 91.63%
[5 empty] | 56.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53020.4366 | 856101.0678 | 56.53 | 91.63%
[5 empty] | 56.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53032.2451 | 856291.7345 | 56.54 | 91.63%
[5 empty] | 56.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53044.0536 | 856482.4011 | 56.55 | 91.63%
[5 empty] | 56.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53055.862 | 856673.0678 | 56.56 | 91.63%
[5 empty] | 56.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53067.6705 | 856863.7345 | 56.57 | 91.63%
[5 empty] | 56.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53079.4789 | 857054.4011 | 56.58 | 91.63%
[5 empty] | 56.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53091.2874 | 857245.0678 | 56.59 | 91.63%
[5 empty] | 56.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53103.0958 | 857435.7345 | 56.6 | 91.63%
[5 empty] | 56.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53114.9043 | 857626.4011 | 56.61 | 91.63%
[5 empty] | 56.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53126.7127 | 857817.0678 | 56.62 | 91.63%
[5 empty] | 56.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53138.5212 | 858007.7345 | 56.63 | 91.63%
[5 empty] | 56.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53150.3296 | 858198.4011 | 56.64 | 91.63%
[5 empty] | 56.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53162.1381 | 858389.0678 | 56.65 | 91.63%
[5 empty] | 56.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53173.9465 | 858579.7345 | 56.66 | 91.63%
[5 empty] | 56.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53185.755 | 858770.4011 | 56.67 | 91.63%
[5 empty] | 56.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53197.5635 | 858961.0678 | 56.68 | 91.63%
[5 empty] | 56.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53209.3719 | 859151.7345 | 56.69 | 91.63%
[5 empty] | 56.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53221.1804 | 859342.4011 | 56.7 | 91.63%
[5 empty] | 56.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53232.9888 | 859533.0678 | 56.71 | 91.63%
[5 empty] | 56.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53244.7973 | 859723.7345 | 56.72 | 91.63%
[5 empty] | 56.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53256.6057 | 859914.4011 | 56.73 | 91.63%
[5 empty] | 56.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53268.4142 | 860105.0678 | 56.74 | 91.63%
[5 empty] | 56.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53280.2226 | 860295.7345 | 56.75 | 91.63%
[5 empty] | 56.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53292.0311 | 860486.4011 | 56.76 | 91.63%
[5 empty] | 56.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53303.8395 | 860677.0678 | 56.77 | 91.63%
[5 empty] | 56.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53315.648 | 860867.7345 | 56.78 | 91.63%
[5 empty] | 56.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53327.4564 | 861058.4011 | 56.79 | 91.63%
[5 empty] | 56.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53339.2649 | 861249.0678 | 56.8 | 91.63%
[5 empty] | 56.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53351.0734 | 861439.7345 | 56.81 | 91.63%
[5 empty] | 56.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53362.8818 | 861630.4011 | 56.82 | 91.63%
[5 empty] | 56.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53374.6903 | 861821.0678 | 56.83 | 91.63%
[5 empty] | 56.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53386.4987 | 862011.7345 | 56.84 | 91.63%
[5 empty] | 56.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53398.3072 | 862202.4011 | 56.85 | 91.63%
[5 empty] | 56.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53410.1156 | 862393.0678 | 56.86 | 91.63%
[5 empty] | 56.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53421.9241 | 862583.7345 | 56.87 | 91.63%
[5 empty] | 56.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53433.7325 | 862774.4011 | 56.88 | 91.63%
[5 empty] | 56.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53445.541 | 862965.0678 | 56.89 | 91.63%
[5 empty] | 56.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53457.3494 | 863155.7345 | 56.9 | 91.63%
[5 empty] | 56.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53469.1579 | 863346.4011 | 56.91 | 91.63%
[5 empty] | 56.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53480.9663 | 863537.0678 | 56.92 | 91.63%
[5 empty] | 56.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53492.7748 | 863727.7345 | 56.93 | 91.63%
[5 empty] | 56.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53504.5832 | 863918.4011 | 56.94 | 91.63%
[5 empty] | 56.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53516.3917 | 864109.0678 | 56.95 | 91.63%
[5 empty] | 56.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53528.2002 | 864299.7345 | 56.96 | 91.63%
[5 empty] | 56.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53540.0086 | 864490.4011 | 56.97 | 91.63%
[5 empty] | 56.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53551.8171 | 864681.0678 | 56.98 | 91.63%
[5 empty] | 56.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53563.6255 | 864871.7345 | 56.99 | 91.63%
[5 empty] | 57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53575.434 | 865062.4011 | 57 | 91.63%
[5 empty] | 57.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53587.2424 | 865253.0678 | 57.01 | 91.63%
[5 empty] | 57.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53599.0509 | 865443.7345 | 57.02 | 91.63%
[5 empty] | 57.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53610.8593 | 865634.4011 | 57.03 | 91.63%
[5 empty] | 57.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53622.6678 | 865825.0678 | 57.04 | 91.63%
[5 empty] | 57.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53634.4762 | 866015.7345 | 57.05 | 91.63%
[5 empty] | 57.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53646.2847 | 866206.4011 | 57.06 | 91.63%
[5 empty] | 57.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53658.0931 | 866397.0678 | 57.07 | 91.63%
[5 empty] | 57.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53669.9016 | 866587.7345 | 57.08 | 91.63%
[5 empty] | 57.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53681.7101 | 866778.4011 | 57.09 | 91.63%
[5 empty] | 57.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53693.5185 | 866969.0678 | 57.1 | 91.63%
[5 empty] | 57.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53705.327 | 867159.7345 | 57.11 | 91.63%
[5 empty] | 57.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53717.1354 | 867350.4011 | 57.12 | 91.63%
[5 empty] | 57.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53728.9439 | 867541.0678 | 57.13 | 91.63%
[5 empty] | 57.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53740.7523 | 867731.7345 | 57.14 | 91.63%
[5 empty] | 57.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53752.5608 | 867922.4011 | 57.15 | 91.63%
[5 empty] | 57.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53764.3692 | 868113.0678 | 57.16 | 91.63%
[5 empty] | 57.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53776.1777 | 868303.7345 | 57.17 | 91.63%
[5 empty] | 57.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53787.9861 | 868494.4011 | 57.18 | 91.63%
[5 empty] | 57.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53799.7946 | 868685.0678 | 57.19 | 91.63%
[5 empty] | 57.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53811.603 | 868875.7345 | 57.2 | 91.63%
[5 empty] | 57.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53823.4115 | 869066.4011 | 57.21 | 91.63%
[5 empty] | 57.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53835.22 | 869257.0678 | 57.22 | 91.63%
[5 empty] | 57.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53847.0284 | 869447.7345 | 57.23 | 91.63%
[5 empty] | 57.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53858.8369 | 869638.4011 | 57.24 | 91.63%
[5 empty] | 57.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53870.6453 | 869829.0678 | 57.25 | 91.63%
[5 empty] | 57.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53882.4538 | 870019.7345 | 57.26 | 91.63%
[5 empty] | 57.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53894.2622 | 870210.4011 | 57.27 | 91.63%
[5 empty] | 57.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53906.0707 | 870401.0678 | 57.28 | 91.63%
[5 empty] | 57.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53917.8791 | 870591.7345 | 57.29 | 91.63%
[5 empty] | 57.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53929.6876 | 870782.4011 | 57.3 | 91.63%
[5 empty] | 57.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53941.496 | 870973.0678 | 57.31 | 91.63%
[5 empty] | 57.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53953.3045 | 871163.7345 | 57.32 | 91.63%
[5 empty] | 57.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53965.1129 | 871354.4011 | 57.33 | 91.63%
[5 empty] | 57.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53976.9214 | 871545.0678 | 57.34 | 91.63%
[5 empty] | 57.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 53988.7299 | 871735.7345 | 57.35 | 91.63%
[5 empty] | 57.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54000.5383 | 871926.4011 | 57.36 | 91.63%
[5 empty] | 57.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54012.3468 | 872117.0678 | 57.37 | 91.63%
[5 empty] | 57.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54024.1552 | 872307.7345 | 57.38 | 91.63%
[5 empty] | 57.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54035.9637 | 872498.4011 | 57.39 | 91.63%
[5 empty] | 57.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54047.7721 | 872689.0678 | 57.4 | 91.63%
[5 empty] | 57.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54059.5806 | 872879.7345 | 57.41 | 91.63%
[5 empty] | 57.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54071.389 | 873070.4011 | 57.42 | 91.63%
[5 empty] | 57.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54083.1975 | 873261.0678 | 57.43 | 91.63%
[5 empty] | 57.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54095.0059 | 873451.7345 | 57.44 | 91.63%
[5 empty] | 57.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54106.8144 | 873642.4011 | 57.45 | 91.63%
[5 empty] | 57.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54118.6228 | 873833.0678 | 57.46 | 91.63%
[5 empty] | 57.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54130.4313 | 874023.7345 | 57.47 | 91.63%
[5 empty] | 57.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54142.2398 | 874214.4011 | 57.48 | 91.63%
[5 empty] | 57.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54154.0482 | 874405.0678 | 57.49 | 91.63%
[5 empty] | 57.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54165.8567 | 874595.7345 | 57.5 | 91.63%
[5 empty] | 57.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54177.6651 | 874786.4011 | 57.51 | 91.63%
[5 empty] | 57.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54189.4736 | 874977.0678 | 57.52 | 91.63%
[5 empty] | 57.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54201.282 | 875167.7345 | 57.53 | 91.63%
[5 empty] | 57.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54213.0905 | 875358.4011 | 57.54 | 91.63%
[5 empty] | 57.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54224.8989 | 875549.0678 | 57.55 | 91.63%
[5 empty] | 57.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54236.7074 | 875739.7345 | 57.56 | 91.63%
[5 empty] | 57.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54248.5158 | 875930.4011 | 57.57 | 91.63%
[5 empty] | 57.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54260.3243 | 876121.0678 | 57.58 | 91.63%
[5 empty] | 57.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54272.1327 | 876311.7345 | 57.59 | 91.63%
[5 empty] | 57.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54283.9412 | 876502.4011 | 57.6 | 91.63%
[5 empty] | 57.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54295.7497 | 876693.0678 | 57.61 | 91.63%
[5 empty] | 57.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54307.5581 | 876883.7345 | 57.62 | 91.63%
[5 empty] | 57.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54319.3666 | 877074.4011 | 57.63 | 91.63%
[5 empty] | 57.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54331.175 | 877265.0678 | 57.64 | 91.63%
[5 empty] | 57.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54342.9835 | 877455.7345 | 57.65 | 91.63%
[5 empty] | 57.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54354.7919 | 877646.4011 | 57.66 | 91.63%
[5 empty] | 57.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54366.6004 | 877837.0678 | 57.67 | 91.63%
[5 empty] | 57.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54378.4088 | 878027.7345 | 57.68 | 91.63%
[5 empty] | 57.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54390.2173 | 878218.4011 | 57.69 | 91.63%
[5 empty] | 57.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54402.0257 | 878409.0678 | 57.7 | 91.63%
[5 empty] | 57.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54413.8342 | 878599.7345 | 57.71 | 91.63%
[5 empty] | 57.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54425.6426 | 878790.4011 | 57.72 | 91.63%
[5 empty] | 57.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54437.4511 | 878981.0678 | 57.73 | 91.63%
[5 empty] | 57.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54449.2596 | 879171.7345 | 57.74 | 91.63%
[5 empty] | 57.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54461.068 | 879362.4011 | 57.75 | 91.63%
[5 empty] | 57.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54472.8765 | 879553.0678 | 57.76 | 91.63%
[5 empty] | 57.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54484.6849 | 879743.7345 | 57.77 | 91.63%
[5 empty] | 57.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54496.4934 | 879934.4011 | 57.78 | 91.63%
[5 empty] | 57.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54508.3018 | 880125.0678 | 57.79 | 91.63%
[5 empty] | 57.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54520.1103 | 880315.7345 | 57.8 | 91.63%
[5 empty] | 57.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54531.9187 | 880506.4011 | 57.81 | 91.63%
[5 empty] | 57.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54543.7272 | 880697.0678 | 57.82 | 91.63%
[5 empty] | 57.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54555.5356 | 880887.7345 | 57.83 | 91.63%
[5 empty] | 57.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54567.3441 | 881078.4011 | 57.84 | 91.63%
[5 empty] | 57.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54579.1525 | 881269.0678 | 57.85 | 91.63%
[5 empty] | 57.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54590.961 | 881459.7345 | 57.86 | 91.63%
[5 empty] | 57.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54602.7695 | 881650.4011 | 57.87 | 91.63%
[5 empty] | 57.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54614.5779 | 881841.0678 | 57.88 | 91.63%
[5 empty] | 57.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54626.3864 | 882031.7345 | 57.89 | 91.63%
[5 empty] | 57.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54638.1948 | 882222.4011 | 57.9 | 91.63%
[5 empty] | 57.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54650.0033 | 882413.0678 | 57.91 | 91.63%
[5 empty] | 57.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54661.8117 | 882603.7345 | 57.92 | 91.63%
[5 empty] | 57.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54673.6202 | 882794.4011 | 57.93 | 91.63%
[5 empty] | 57.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54685.4286 | 882985.0678 | 57.94 | 91.63%
[5 empty] | 57.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54697.2371 | 883175.7345 | 57.95 | 91.63%
[5 empty] | 57.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54709.0455 | 883366.4011 | 57.96 | 91.63%
[5 empty] | 57.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54720.854 | 883557.0678 | 57.97 | 91.63%
[5 empty] | 57.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54732.6624 | 883747.7345 | 57.98 | 91.63%
[5 empty] | 57.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54744.4709 | 883938.4011 | 57.99 | 91.63%
[5 empty] | 58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54756.2794 | 884129.0678 | 58 | 91.63%
[5 empty] | 58.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54768.0878 | 884319.7345 | 58.01 | 91.63%
[5 empty] | 58.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54779.8963 | 884510.4011 | 58.02 | 91.63%
[5 empty] | 58.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54791.7047 | 884701.0678 | 58.03 | 91.63%
[5 empty] | 58.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54803.5132 | 884891.7345 | 58.04 | 91.63%
[5 empty] | 58.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54815.3216 | 885082.4011 | 58.05 | 91.63%
[5 empty] | 58.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54827.1301 | 885273.0678 | 58.06 | 91.63%
[5 empty] | 58.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54838.9385 | 885463.7345 | 58.07 | 91.63%
[5 empty] | 58.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54850.747 | 885654.4011 | 58.08 | 91.63%
[5 empty] | 58.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54862.5554 | 885845.0678 | 58.09 | 91.63%
[5 empty] | 58.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54874.3639 | 886035.7345 | 58.1 | 91.63%
[5 empty] | 58.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54886.1723 | 886226.4011 | 58.11 | 91.63%
[5 empty] | 58.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54897.9808 | 886417.0678 | 58.12 | 91.63%
[5 empty] | 58.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54909.7893 | 886607.7345 | 58.13 | 91.63%
[5 empty] | 58.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54921.5977 | 886798.4011 | 58.14 | 91.63%
[5 empty] | 58.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54933.4062 | 886989.0678 | 58.15 | 91.63%
[5 empty] | 58.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54945.2146 | 887179.7345 | 58.16 | 91.63%
[5 empty] | 58.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54957.0231 | 887370.4011 | 58.17 | 91.63%
[5 empty] | 58.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54968.8315 | 887561.0678 | 58.18 | 91.63%
[5 empty] | 58.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54980.64 | 887751.7345 | 58.19 | 91.63%
[5 empty] | 58.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 54992.4484 | 887942.4011 | 58.2 | 91.63%
[5 empty] | 58.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55004.2569 | 888133.0678 | 58.21 | 91.63%
[5 empty] | 58.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55016.0653 | 888323.7345 | 58.22 | 91.63%
[5 empty] | 58.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55027.8738 | 888514.4011 | 58.23 | 91.63%
[5 empty] | 58.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55039.6822 | 888705.0678 | 58.24 | 91.63%
[5 empty] | 58.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55051.4907 | 888895.7345 | 58.25 | 91.63%
[5 empty] | 58.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55063.2992 | 889086.4011 | 58.26 | 91.63%
[5 empty] | 58.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55075.1076 | 889277.0678 | 58.27 | 91.63%
[5 empty] | 58.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55086.9161 | 889467.7345 | 58.28 | 91.63%
[5 empty] | 58.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55098.7245 | 889658.4011 | 58.29 | 91.63%
[5 empty] | 58.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55110.533 | 889849.0678 | 58.3 | 91.63%
[5 empty] | 58.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55122.3414 | 890039.7345 | 58.31 | 91.63%
[5 empty] | 58.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55134.1499 | 890230.4011 | 58.32 | 91.63%
[5 empty] | 58.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55145.9583 | 890421.0678 | 58.33 | 91.63%
[5 empty] | 58.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55157.7668 | 890611.7345 | 58.34 | 91.63%
[5 empty] | 58.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55169.5752 | 890802.4011 | 58.35 | 91.63%
[5 empty] | 58.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55181.3837 | 890993.0678 | 58.36 | 91.63%
[5 empty] | 58.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55193.1921 | 891183.7345 | 58.37 | 91.63%
[5 empty] | 58.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55205.0006 | 891374.4011 | 58.38 | 91.63%
[5 empty] | 58.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55216.8091 | 891565.0678 | 58.39 | 91.63%
[5 empty] | 58.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55228.6175 | 891755.7345 | 58.4 | 91.63%
[5 empty] | 58.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55240.426 | 891946.4011 | 58.41 | 91.63%
[5 empty] | 58.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55252.2344 | 892137.0678 | 58.42 | 91.63%
[5 empty] | 58.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55264.0429 | 892327.7345 | 58.43 | 91.63%
[5 empty] | 58.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55275.8513 | 892518.4011 | 58.44 | 91.63%
[5 empty] | 58.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55287.6598 | 892709.0678 | 58.45 | 91.63%
[5 empty] | 58.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55299.4682 | 892899.7345 | 58.46 | 91.63%
[5 empty] | 58.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55311.2767 | 893090.4011 | 58.47 | 91.63%
[5 empty] | 58.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55323.0851 | 893281.0678 | 58.48 | 91.63%
[5 empty] | 58.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55334.8936 | 893471.7345 | 58.49 | 91.63%
[5 empty] | 58.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55346.702 | 893662.4011 | 58.5 | 91.63%
[5 empty] | 58.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55358.5105 | 893853.0678 | 58.51 | 91.63%
[5 empty] | 58.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55370.319 | 894043.7345 | 58.52 | 91.63%
[5 empty] | 58.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55382.1274 | 894234.4011 | 58.53 | 91.63%
[5 empty] | 58.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55393.9359 | 894425.0678 | 58.54 | 91.63%
[5 empty] | 58.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55405.7443 | 894615.7345 | 58.55 | 91.63%
[5 empty] | 58.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55417.5528 | 894806.4011 | 58.56 | 91.63%
[5 empty] | 58.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55429.3612 | 894997.0678 | 58.57 | 91.63%
[5 empty] | 58.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55441.1697 | 895187.7345 | 58.58 | 91.63%
[5 empty] | 58.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55452.9781 | 895378.4011 | 58.59 | 91.63%
[5 empty] | 58.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55464.7866 | 895569.0678 | 58.6 | 91.63%
[5 empty] | 58.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55476.595 | 895759.7345 | 58.61 | 91.63%
[5 empty] | 58.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55488.4035 | 895950.4011 | 58.62 | 91.63%
[5 empty] | 58.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55500.2119 | 896141.0678 | 58.63 | 91.63%
[5 empty] | 58.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55512.0204 | 896331.7345 | 58.64 | 91.63%
[5 empty] | 58.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55523.8289 | 896522.4011 | 58.65 | 91.63%
[5 empty] | 58.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55535.6373 | 896713.0678 | 58.66 | 91.63%
[5 empty] | 58.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55547.4458 | 896903.7345 | 58.67 | 91.63%
[5 empty] | 58.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55559.2542 | 897094.4011 | 58.68 | 91.63%
[5 empty] | 58.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55571.0627 | 897285.0678 | 58.69 | 91.63%
[5 empty] | 58.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55582.8711 | 897475.7345 | 58.7 | 91.63%
[5 empty] | 58.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55594.6796 | 897666.4011 | 58.71 | 91.63%
[5 empty] | 58.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55606.488 | 897857.0678 | 58.72 | 91.63%
[5 empty] | 58.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55618.2965 | 898047.7345 | 58.73 | 91.63%
[5 empty] | 58.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55630.1049 | 898238.4011 | 58.74 | 91.63%
[5 empty] | 58.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55641.9134 | 898429.0678 | 58.75 | 91.63%
[5 empty] | 58.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55653.7218 | 898619.7345 | 58.76 | 91.63%
[5 empty] | 58.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55665.5303 | 898810.4011 | 58.77 | 91.63%
[5 empty] | 58.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55677.3388 | 899001.0678 | 58.78 | 91.63%
[5 empty] | 58.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55689.1472 | 899191.7345 | 58.79 | 91.63%
[5 empty] | 58.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55700.9557 | 899382.4011 | 58.8 | 91.63%
[5 empty] | 58.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55712.7641 | 899573.0678 | 58.81 | 91.63%
[5 empty] | 58.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55724.5726 | 899763.7345 | 58.82 | 91.63%
[5 empty] | 58.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55736.381 | 899954.4011 | 58.83 | 91.63%
[5 empty] | 58.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55748.1895 | 900145.0678 | 58.84 | 91.63%
[5 empty] | 58.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55759.9979 | 900335.7345 | 58.85 | 91.63%
[5 empty] | 58.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55771.8064 | 900526.4011 | 58.86 | 91.63%
[5 empty] | 58.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55783.6148 | 900717.0678 | 58.87 | 91.63%
[5 empty] | 58.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55795.4233 | 900907.7345 | 58.88 | 91.63%
[5 empty] | 58.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55807.2317 | 901098.4011 | 58.89 | 91.63%
[5 empty] | 58.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55819.0402 | 901289.0678 | 58.9 | 91.63%
[5 empty] | 58.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55830.8487 | 901479.7345 | 58.91 | 91.63%
[5 empty] | 58.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55842.6571 | 901670.4011 | 58.92 | 91.63%
[5 empty] | 58.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55854.4656 | 901861.0678 | 58.93 | 91.63%
[5 empty] | 58.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55866.274 | 902051.7345 | 58.94 | 91.63%
[5 empty] | 58.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55878.0825 | 902242.4011 | 58.95 | 91.63%
[5 empty] | 58.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55889.8909 | 902433.0678 | 58.96 | 91.63%
[5 empty] | 58.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55901.6994 | 902623.7345 | 58.97 | 91.63%
[5 empty] | 58.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55913.5078 | 902814.4011 | 58.98 | 91.63%
[5 empty] | 58.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55925.3163 | 903005.0678 | 58.99 | 91.63%
[5 empty] | 59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55937.1247 | 903195.7345 | 59 | 91.63%
[5 empty] | 59.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55948.9332 | 903386.4011 | 59.01 | 91.63%
[5 empty] | 59.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55960.7416 | 903577.0678 | 59.02 | 91.63%
[5 empty] | 59.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55972.5501 | 903767.7345 | 59.03 | 91.63%
[5 empty] | 59.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55984.3586 | 903958.4011 | 59.04 | 91.63%
[5 empty] | 59.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 55996.167 | 904149.0678 | 59.05 | 91.63%
[5 empty] | 59.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56007.9755 | 904339.7345 | 59.06 | 91.63%
[5 empty] | 59.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56019.7839 | 904530.4011 | 59.07 | 91.63%
[5 empty] | 59.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56031.5924 | 904721.0678 | 59.08 | 91.63%
[5 empty] | 59.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56043.4008 | 904911.7345 | 59.09 | 91.63%
[5 empty] | 59.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56055.2093 | 905102.4011 | 59.1 | 91.63%
[5 empty] | 59.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56067.0177 | 905293.0678 | 59.11 | 91.63%
[5 empty] | 59.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56078.8262 | 905483.7345 | 59.12 | 91.63%
[5 empty] | 59.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56090.6346 | 905674.4011 | 59.13 | 91.63%
[5 empty] | 59.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56102.4431 | 905865.0678 | 59.14 | 91.63%
[5 empty] | 59.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56114.2515 | 906055.7345 | 59.15 | 91.63%
[5 empty] | 59.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56126.06 | 906246.4011 | 59.16 | 91.63%
[5 empty] | 59.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56137.8685 | 906437.0678 | 59.17 | 91.63%
[5 empty] | 59.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56149.6769 | 906627.7345 | 59.18 | 91.63%
[5 empty] | 59.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56161.4854 | 906818.4011 | 59.19 | 91.63%
[5 empty] | 59.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56173.2938 | 907009.0678 | 59.2 | 91.63%
[5 empty] | 59.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56185.1023 | 907199.7345 | 59.21 | 91.63%
[5 empty] | 59.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56196.9107 | 907390.4011 | 59.22 | 91.63%
[5 empty] | 59.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56208.7192 | 907581.0678 | 59.23 | 91.63%
[5 empty] | 59.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56220.5276 | 907771.7345 | 59.24 | 91.63%
[5 empty] | 59.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56232.3361 | 907962.4011 | 59.25 | 91.63%
[5 empty] | 59.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56244.1445 | 908153.0678 | 59.26 | 91.63%
[5 empty] | 59.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56255.953 | 908343.7345 | 59.27 | 91.63%
[5 empty] | 59.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56267.7614 | 908534.4011 | 59.28 | 91.63%
[5 empty] | 59.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56279.5699 | 908725.0678 | 59.29 | 91.63%
[5 empty] | 59.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56291.3784 | 908915.7345 | 59.3 | 91.63%
[5 empty] | 59.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56303.1868 | 909106.4011 | 59.31 | 91.63%
[5 empty] | 59.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56314.9953 | 909297.0678 | 59.32 | 91.63%
[5 empty] | 59.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56326.8037 | 909487.7345 | 59.33 | 91.63%
[5 empty] | 59.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56338.6122 | 909678.4011 | 59.34 | 91.63%
[5 empty] | 59.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56350.4206 | 909869.0678 | 59.35 | 91.63%
[5 empty] | 59.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56362.2291 | 910059.7345 | 59.36 | 91.63%
[5 empty] | 59.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56374.0375 | 910250.4011 | 59.37 | 91.63%
[5 empty] | 59.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56385.846 | 910441.0678 | 59.38 | 91.63%
[5 empty] | 59.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56397.6544 | 910631.7345 | 59.39 | 91.63%
[5 empty] | 59.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56409.4629 | 910822.4011 | 59.4 | 91.63%
[5 empty] | 59.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56421.2713 | 911013.0678 | 59.41 | 91.63%
[5 empty] | 59.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56433.0798 | 911203.7345 | 59.42 | 91.63%
[5 empty] | 59.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56444.8882 | 911394.4011 | 59.43 | 91.63%
[5 empty] | 59.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56456.6967 | 911585.0678 | 59.44 | 91.63%
[5 empty] | 59.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56468.5052 | 911775.7345 | 59.45 | 91.63%
[5 empty] | 59.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56480.3136 | 911966.4011 | 59.46 | 91.63%
[5 empty] | 59.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56492.1221 | 912157.0678 | 59.47 | 91.63%
[5 empty] | 59.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56503.9305 | 912347.7345 | 59.48 | 91.63%
[5 empty] | 59.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56515.739 | 912538.4011 | 59.49 | 91.63%
[5 empty] | 59.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56527.5474 | 912729.0678 | 59.5 | 91.63%
[5 empty] | 59.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56539.3559 | 912919.7345 | 59.51 | 91.63%
[5 empty] | 59.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56551.1643 | 913110.4011 | 59.52 | 91.63%
[5 empty] | 59.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56562.9728 | 913301.0678 | 59.53 | 91.63%
[5 empty] | 59.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56574.7812 | 913491.7345 | 59.54 | 91.63%
[5 empty] | 59.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56586.5897 | 913682.4011 | 59.55 | 91.63%
[5 empty] | 59.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56598.3981 | 913873.0678 | 59.56 | 91.63%
[5 empty] | 59.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56610.2066 | 914063.7345 | 59.57 | 91.63%
[5 empty] | 59.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56622.0151 | 914254.4011 | 59.58 | 91.63%
[5 empty] | 59.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56633.8235 | 914445.0678 | 59.59 | 91.63%
[5 empty] | 59.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56645.632 | 914635.7345 | 59.6 | 91.63%
[5 empty] | 59.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56657.4404 | 914826.4011 | 59.61 | 91.63%
[5 empty] | 59.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56669.2489 | 915017.0678 | 59.62 | 91.63%
[5 empty] | 59.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56681.0573 | 915207.7345 | 59.63 | 91.63%
[5 empty] | 59.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56692.8658 | 915398.4011 | 59.64 | 91.63%
[5 empty] | 59.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56704.6742 | 915589.0678 | 59.65 | 91.63%
[5 empty] | 59.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56716.4827 | 915779.7345 | 59.66 | 91.63%
[5 empty] | 59.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56728.2911 | 915970.4011 | 59.67 | 91.63%
[5 empty] | 59.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56740.0996 | 916161.0678 | 59.68 | 91.63%
[5 empty] | 59.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56751.908 | 916351.7345 | 59.69 | 91.63%
[5 empty] | 59.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56763.7165 | 916542.4011 | 59.7 | 91.63%
[5 empty] | 59.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56775.525 | 916733.0678 | 59.71 | 91.63%
[5 empty] | 59.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56787.3334 | 916923.7345 | 59.72 | 91.63%
[5 empty] | 59.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56799.1419 | 917114.4011 | 59.73 | 91.63%
[5 empty] | 59.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56810.9503 | 917305.0678 | 59.74 | 91.63%
[5 empty] | 59.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56822.7588 | 917495.7345 | 59.75 | 91.63%
[5 empty] | 59.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56834.5672 | 917686.4011 | 59.76 | 91.63%
[5 empty] | 59.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56846.3757 | 917877.0678 | 59.77 | 91.63%
[5 empty] | 59.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56858.1841 | 918067.7345 | 59.78 | 91.63%
[5 empty] | 59.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56869.9926 | 918258.4011 | 59.79 | 91.63%
[5 empty] | 59.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56881.801 | 918449.0678 | 59.8 | 91.63%
[5 empty] | 59.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56893.6095 | 918639.7345 | 59.81 | 91.63%
[5 empty] | 59.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56905.4179 | 918830.4011 | 59.82 | 91.63%
[5 empty] | 59.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56917.2264 | 919021.0678 | 59.83 | 91.63%
[5 empty] | 59.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56929.0349 | 919211.7345 | 59.84 | 91.63%
[5 empty] | 59.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56940.8433 | 919402.4011 | 59.85 | 91.63%
[5 empty] | 59.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56952.6518 | 919593.0678 | 59.86 | 91.63%
[5 empty] | 59.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56964.4602 | 919783.7345 | 59.87 | 91.63%
[5 empty] | 59.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56976.2687 | 919974.4011 | 59.88 | 91.63%
[5 empty] | 59.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56988.0771 | 920165.0678 | 59.89 | 91.63%
[5 empty] | 59.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 56999.8856 | 920355.7345 | 59.9 | 91.63%
[5 empty] | 59.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57011.694 | 920546.4011 | 59.91 | 91.63%
[5 empty] | 59.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57023.5025 | 920737.0678 | 59.92 | 91.63%
[5 empty] | 59.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57035.3109 | 920927.7345 | 59.93 | 91.63%
[5 empty] | 59.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57047.1194 | 921118.4011 | 59.94 | 91.63%
[5 empty] | 59.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57058.9278 | 921309.0678 | 59.95 | 91.63%
[5 empty] | 59.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57070.7363 | 921499.7345 | 59.96 | 91.63%
[5 empty] | 59.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57082.5448 | 921690.4011 | 59.97 | 91.63%
[5 empty] | 59.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57094.3532 | 921881.0678 | 59.98 | 91.63%
[5 empty] | 59.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57106.1617 | 922071.7345 | 59.99 | 91.63%
[5 empty] | 60 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57117.9701 | 922262.4011 | 60 | 91.63%
[5 empty] | 60.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57129.7786 | 922453.0678 | 60.01 | 91.63%
[5 empty] | 60.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57141.587 | 922643.7345 | 60.02 | 91.63%
[5 empty] | 60.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57153.3955 | 922834.4011 | 60.03 | 91.63%
[5 empty] | 60.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57165.2039 | 923025.0678 | 60.04 | 91.63%
[5 empty] | 60.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57177.0124 | 923215.7345 | 60.05 | 91.63%
[5 empty] | 60.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57188.8208 | 923406.4011 | 60.06 | 91.63%
[5 empty] | 60.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57200.6293 | 923597.0678 | 60.07 | 91.63%
[5 empty] | 60.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57212.4377 | 923787.7345 | 60.08 | 91.63%
[5 empty] | 60.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57224.2462 | 923978.4011 | 60.09 | 91.63%
[5 empty] | 60.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57236.0547 | 924169.0678 | 60.1 | 91.63%
[5 empty] | 60.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57247.8631 | 924359.7345 | 60.11 | 91.63%
[5 empty] | 60.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57259.6716 | 924550.4011 | 60.12 | 91.63%
[5 empty] | 60.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57271.48 | 924741.0678 | 60.13 | 91.63%
[5 empty] | 60.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57283.2885 | 924931.7345 | 60.14 | 91.63%
[5 empty] | 60.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57295.0969 | 925122.4011 | 60.15 | 91.63%
[5 empty] | 60.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57306.9054 | 925313.0678 | 60.16 | 91.63%
[5 empty] | 60.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57318.7138 | 925503.7345 | 60.17 | 91.63%
[5 empty] | 60.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57330.5223 | 925694.4011 | 60.18 | 91.63%
[5 empty] | 60.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57342.3307 | 925885.0678 | 60.19 | 91.63%
[5 empty] | 60.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57354.1392 | 926075.7345 | 60.2 | 91.63%
[5 empty] | 60.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57365.9476 | 926266.4011 | 60.21 | 91.63%
[5 empty] | 60.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57377.7561 | 926457.0678 | 60.22 | 91.63%
[5 empty] | 60.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57389.5646 | 926647.7345 | 60.23 | 91.63%
[5 empty] | 60.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57401.373 | 926838.4011 | 60.24 | 91.63%
[5 empty] | 60.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57413.1815 | 927029.0678 | 60.25 | 91.63%
[5 empty] | 60.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57424.9899 | 927219.7345 | 60.26 | 91.63%
[5 empty] | 60.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57436.7984 | 927410.4011 | 60.27 | 91.63%
[5 empty] | 60.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57448.6068 | 927601.0678 | 60.28 | 91.63%
[5 empty] | 60.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57460.4153 | 927791.7345 | 60.29 | 91.63%
[5 empty] | 60.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57472.2237 | 927982.4011 | 60.3 | 91.63%
[5 empty] | 60.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57484.0322 | 928173.0678 | 60.31 | 91.63%
[5 empty] | 60.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57495.8406 | 928363.7345 | 60.32 | 91.63%
[5 empty] | 60.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57507.6491 | 928554.4011 | 60.33 | 91.63%
[5 empty] | 60.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57519.4575 | 928745.0678 | 60.34 | 91.63%
[5 empty] | 60.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57531.266 | 928935.7345 | 60.35 | 91.63%
[5 empty] | 60.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57543.0745 | 929126.4011 | 60.36 | 91.63%
[5 empty] | 60.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57554.8829 | 929317.0678 | 60.37 | 91.63%
[5 empty] | 60.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57566.6914 | 929507.7345 | 60.38 | 91.63%
[5 empty] | 60.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57578.4998 | 929698.4011 | 60.39 | 91.63%
[5 empty] | 60.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57590.3083 | 929889.0678 | 60.4 | 91.63%
[5 empty] | 60.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57602.1167 | 930079.7345 | 60.41 | 91.63%
[5 empty] | 60.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57613.9252 | 930270.4011 | 60.42 | 91.63%
[5 empty] | 60.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57625.7336 | 930461.0678 | 60.43 | 91.63%
[5 empty] | 60.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57637.5421 | 930651.7345 | 60.44 | 91.63%
[5 empty] | 60.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57649.3505 | 930842.4011 | 60.45 | 91.63%
[5 empty] | 60.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57661.159 | 931033.0678 | 60.46 | 91.63%
[5 empty] | 60.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57672.9674 | 931223.7345 | 60.47 | 91.63%
[5 empty] | 60.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57684.7759 | 931414.4011 | 60.48 | 91.63%
[5 empty] | 60.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57696.5844 | 931605.0678 | 60.49 | 91.63%
[5 empty] | 60.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57708.3928 | 931795.7345 | 60.5 | 91.63%
[5 empty] | 60.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57720.2013 | 931986.4011 | 60.51 | 91.63%
[5 empty] | 60.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57732.0097 | 932177.0678 | 60.52 | 91.63%
[5 empty] | 60.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57743.8182 | 932367.7345 | 60.53 | 91.63%
[5 empty] | 60.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57755.6266 | 932558.4011 | 60.54 | 91.63%
[5 empty] | 60.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57767.4351 | 932749.0678 | 60.55 | 91.63%
[5 empty] | 60.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57779.2435 | 932939.7345 | 60.56 | 91.63%
[5 empty] | 60.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57791.052 | 933130.4011 | 60.57 | 91.63%
[5 empty] | 60.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57802.8604 | 933321.0678 | 60.58 | 91.63%
[5 empty] | 60.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57814.6689 | 933511.7345 | 60.59 | 91.63%
[5 empty] | 60.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57826.4773 | 933702.4011 | 60.6 | 91.63%
[5 empty] | 60.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57838.2858 | 933893.0678 | 60.61 | 91.63%
[5 empty] | 60.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57850.0943 | 934083.7345 | 60.62 | 91.63%
[5 empty] | 60.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57861.9027 | 934274.4011 | 60.63 | 91.63%
[5 empty] | 60.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57873.7112 | 934465.0678 | 60.64 | 91.63%
[5 empty] | 60.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57885.5196 | 934655.7345 | 60.65 | 91.63%
[5 empty] | 60.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57897.3281 | 934846.4011 | 60.66 | 91.63%
[5 empty] | 60.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57909.1365 | 935037.0678 | 60.67 | 91.63%
[5 empty] | 60.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57920.945 | 935227.7345 | 60.68 | 91.63%
[5 empty] | 60.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57932.7534 | 935418.4011 | 60.69 | 91.63%
[5 empty] | 60.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57944.5619 | 935609.0678 | 60.7 | 91.63%
[5 empty] | 60.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57956.3703 | 935799.7345 | 60.71 | 91.63%
[5 empty] | 60.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57968.1788 | 935990.4011 | 60.72 | 91.63%
[5 empty] | 60.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57979.9872 | 936181.0678 | 60.73 | 91.63%
[5 empty] | 60.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 57991.7957 | 936371.7345 | 60.74 | 91.63%
[5 empty] | 60.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58003.6042 | 936562.4011 | 60.75 | 91.63%
[5 empty] | 60.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58015.4126 | 936753.0678 | 60.76 | 91.63%
[5 empty] | 60.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58027.2211 | 936943.7345 | 60.77 | 91.63%
[5 empty] | 60.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58039.0295 | 937134.4011 | 60.78 | 91.63%
[5 empty] | 60.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58050.838 | 937325.0678 | 60.79 | 91.63%
[5 empty] | 60.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58062.6464 | 937515.7345 | 60.8 | 91.63%
[5 empty] | 60.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58074.4549 | 937706.4011 | 60.81 | 91.63%
[5 empty] | 60.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58086.2633 | 937897.0678 | 60.82 | 91.63%
[5 empty] | 60.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58098.0718 | 938087.7345 | 60.83 | 91.63%
[5 empty] | 60.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58109.8802 | 938278.4011 | 60.84 | 91.63%
[5 empty] | 60.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58121.6887 | 938469.0678 | 60.85 | 91.63%
[5 empty] | 60.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58133.4971 | 938659.7345 | 60.86 | 91.63%
[5 empty] | 60.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58145.3056 | 938850.4011 | 60.87 | 91.63%
[5 empty] | 60.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58157.1141 | 939041.0678 | 60.88 | 91.63%
[5 empty] | 60.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58168.9225 | 939231.7345 | 60.89 | 91.63%
[5 empty] | 60.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58180.731 | 939422.4011 | 60.9 | 91.63%
[5 empty] | 60.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58192.5394 | 939613.0678 | 60.91 | 91.63%
[5 empty] | 60.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58204.3479 | 939803.7345 | 60.92 | 91.63%
[5 empty] | 60.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58216.1563 | 939994.4011 | 60.93 | 91.63%
[5 empty] | 60.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58227.9648 | 940185.0678 | 60.94 | 91.63%
[5 empty] | 60.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58239.7732 | 940375.7345 | 60.95 | 91.63%
[5 empty] | 60.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58251.5817 | 940566.4011 | 60.96 | 91.63%
[5 empty] | 60.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58263.3901 | 940757.0678 | 60.97 | 91.63%
[5 empty] | 60.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58275.1986 | 940947.7345 | 60.98 | 91.63%
[5 empty] | 60.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58287.007 | 941138.4011 | 60.99 | 91.63%
[5 empty] | 61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58298.8155 | 941329.0678 | 61 | 91.63%
[5 empty] | 61.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58310.624 | 941519.7345 | 61.01 | 91.63%
[5 empty] | 61.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58322.4324 | 941710.4011 | 61.02 | 91.63%
[5 empty] | 61.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58334.2409 | 941901.0678 | 61.03 | 91.63%
[5 empty] | 61.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58346.0493 | 942091.7345 | 61.04 | 91.63%
[5 empty] | 61.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58357.8578 | 942282.4011 | 61.05 | 91.63%
[5 empty] | 61.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58369.6662 | 942473.0678 | 61.06 | 91.63%
[5 empty] | 61.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58381.4747 | 942663.7345 | 61.07 | 91.63%
[5 empty] | 61.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58393.2831 | 942854.4011 | 61.08 | 91.63%
[5 empty] | 61.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58405.0916 | 943045.0678 | 61.09 | 91.63%
[5 empty] | 61.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58416.9 | 943235.7345 | 61.1 | 91.63%
[5 empty] | 61.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58428.7085 | 943426.4011 | 61.11 | 91.63%
[5 empty] | 61.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58440.5169 | 943617.0678 | 61.12 | 91.63%
[5 empty] | 61.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58452.3254 | 943807.7345 | 61.13 | 91.63%
[5 empty] | 61.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58464.1339 | 943998.4011 | 61.14 | 91.63%
[5 empty] | 61.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58475.9423 | 944189.0678 | 61.15 | 91.63%
[5 empty] | 61.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58487.7508 | 944379.7345 | 61.16 | 91.63%
[5 empty] | 61.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58499.5592 | 944570.4011 | 61.17 | 91.63%
[5 empty] | 61.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58511.3677 | 944761.0678 | 61.18 | 91.63%
[5 empty] | 61.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58523.1761 | 944951.7345 | 61.19 | 91.63%
[5 empty] | 61.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58534.9846 | 945142.4011 | 61.2 | 91.63%
[5 empty] | 61.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58546.793 | 945333.0678 | 61.21 | 91.63%
[5 empty] | 61.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58558.6015 | 945523.7345 | 61.22 | 91.63%
[5 empty] | 61.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58570.4099 | 945714.4011 | 61.23 | 91.63%
[5 empty] | 61.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58582.2184 | 945905.0678 | 61.24 | 91.63%
[5 empty] | 61.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58594.0268 | 946095.7345 | 61.25 | 91.63%
[5 empty] | 61.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58605.8353 | 946286.4011 | 61.26 | 91.63%
[5 empty] | 61.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58617.6438 | 946477.0678 | 61.27 | 91.63%
[5 empty] | 61.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58629.4522 | 946667.7345 | 61.28 | 91.63%
[5 empty] | 61.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58641.2607 | 946858.4011 | 61.29 | 91.63%
[5 empty] | 61.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58653.0691 | 947049.0678 | 61.3 | 91.63%
[5 empty] | 61.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58664.8776 | 947239.7345 | 61.31 | 91.63%
[5 empty] | 61.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58676.686 | 947430.4011 | 61.32 | 91.63%
[5 empty] | 61.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58688.4945 | 947621.0678 | 61.33 | 91.63%
[5 empty] | 61.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58700.3029 | 947811.7345 | 61.34 | 91.63%
[5 empty] | 61.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58712.1114 | 948002.4011 | 61.35 | 91.63%
[5 empty] | 61.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58723.9198 | 948193.0678 | 61.36 | 91.63%
[5 empty] | 61.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58735.7283 | 948383.7345 | 61.37 | 91.63%
[5 empty] | 61.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58747.5367 | 948574.4011 | 61.38 | 91.63%
[5 empty] | 61.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58759.3452 | 948765.0678 | 61.39 | 91.63%
[5 empty] | 61.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58771.1537 | 948955.7345 | 61.4 | 91.63%
[5 empty] | 61.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58782.9621 | 949146.4011 | 61.41 | 91.63%
[5 empty] | 61.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58794.7706 | 949337.0678 | 61.42 | 91.63%
[5 empty] | 61.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58806.579 | 949527.7345 | 61.43 | 91.63%
[5 empty] | 61.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58818.3875 | 949718.4011 | 61.44 | 91.63%
[5 empty] | 61.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58830.1959 | 949909.0678 | 61.45 | 91.63%
[5 empty] | 61.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58842.0044 | 950099.7345 | 61.46 | 91.63%
[5 empty] | 61.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58853.8128 | 950290.4011 | 61.47 | 91.63%
[5 empty] | 61.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58865.6213 | 950481.0678 | 61.48 | 91.63%
[5 empty] | 61.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58877.4297 | 950671.7345 | 61.49 | 91.63%
[5 empty] | 61.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58889.2382 | 950862.4011 | 61.5 | 91.63%
[5 empty] | 61.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58901.0466 | 951053.0678 | 61.51 | 91.63%
[5 empty] | 61.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58912.8551 | 951243.7345 | 61.52 | 91.63%
[5 empty] | 61.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58924.6636 | 951434.4011 | 61.53 | 91.63%
[5 empty] | 61.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58936.472 | 951625.0678 | 61.54 | 91.63%
[5 empty] | 61.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58948.2805 | 951815.7345 | 61.55 | 91.63%
[5 empty] | 61.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58960.0889 | 952006.4011 | 61.56 | 91.63%
[5 empty] | 61.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58971.8974 | 952197.0678 | 61.57 | 91.63%
[5 empty] | 61.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58983.7058 | 952387.7345 | 61.58 | 91.63%
[5 empty] | 61.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 58995.5143 | 952578.4011 | 61.59 | 91.63%
[5 empty] | 61.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59007.3227 | 952769.0678 | 61.6 | 91.63%
[5 empty] | 61.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59019.1312 | 952959.7345 | 61.61 | 91.63%
[5 empty] | 61.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59030.9396 | 953150.4011 | 61.62 | 91.63%
[5 empty] | 61.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59042.7481 | 953341.0678 | 61.63 | 91.63%
[5 empty] | 61.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59054.5565 | 953531.7345 | 61.64 | 91.63%
[5 empty] | 61.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59066.365 | 953722.4011 | 61.65 | 91.63%
[5 empty] | 61.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59078.1735 | 953913.0678 | 61.66 | 91.63%
[5 empty] | 61.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59089.9819 | 954103.7345 | 61.67 | 91.63%
[5 empty] | 61.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59101.7904 | 954294.4011 | 61.68 | 91.63%
[5 empty] | 61.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59113.5988 | 954485.0678 | 61.69 | 91.63%
[5 empty] | 61.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59125.4073 | 954675.7345 | 61.7 | 91.63%
[5 empty] | 61.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59137.2157 | 954866.4011 | 61.71 | 91.63%
[5 empty] | 61.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59149.0242 | 955057.0678 | 61.72 | 91.63%
[5 empty] | 61.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59160.8326 | 955247.7345 | 61.73 | 91.63%
[5 empty] | 61.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59172.6411 | 955438.4011 | 61.74 | 91.63%
[5 empty] | 61.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59184.4495 | 955629.0678 | 61.75 | 91.63%
[5 empty] | 61.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59196.258 | 955819.7345 | 61.76 | 91.63%
[5 empty] | 61.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59208.0664 | 956010.4011 | 61.77 | 91.63%
[5 empty] | 61.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59219.8749 | 956201.0678 | 61.78 | 91.63%
[5 empty] | 61.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59231.6833 | 956391.7345 | 61.79 | 91.63%
[5 empty] | 61.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59243.4918 | 956582.4011 | 61.8 | 91.63%
[5 empty] | 61.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59255.3003 | 956773.0678 | 61.81 | 91.63%
[5 empty] | 61.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59267.1087 | 956963.7345 | 61.82 | 91.63%
[5 empty] | 61.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59278.9172 | 957154.4011 | 61.83 | 91.63%
[5 empty] | 61.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59290.7256 | 957345.0678 | 61.84 | 91.63%
[5 empty] | 61.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59302.5341 | 957535.7345 | 61.85 | 91.63%
[5 empty] | 61.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59314.3425 | 957726.4011 | 61.86 | 91.63%
[5 empty] | 61.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59326.151 | 957917.0678 | 61.87 | 91.63%
[5 empty] | 61.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59337.9594 | 958107.7345 | 61.88 | 91.63%
[5 empty] | 61.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59349.7679 | 958298.4011 | 61.89 | 91.63%
[5 empty] | 61.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59361.5763 | 958489.0678 | 61.9 | 91.63%
[5 empty] | 61.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59373.3848 | 958679.7345 | 61.91 | 91.63%
[5 empty] | 61.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59385.1932 | 958870.4011 | 61.92 | 91.63%
[5 empty] | 61.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59397.0017 | 959061.0678 | 61.93 | 91.63%
[5 empty] | 61.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59408.8102 | 959251.7345 | 61.94 | 91.63%
[5 empty] | 61.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59420.6186 | 959442.4011 | 61.95 | 91.63%
[5 empty] | 61.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59432.4271 | 959633.0678 | 61.96 | 91.63%
[5 empty] | 61.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59444.2355 | 959823.7345 | 61.97 | 91.63%
[5 empty] | 61.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59456.044 | 960014.4011 | 61.98 | 91.63%
[5 empty] | 61.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59467.8524 | 960205.0678 | 61.99 | 91.63%
[5 empty] | 62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59479.6609 | 960395.7345 | 62 | 91.63%
[5 empty] | 62.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59491.4693 | 960586.4011 | 62.01 | 91.63%
[5 empty] | 62.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59503.2778 | 960777.0678 | 62.02 | 91.63%
[5 empty] | 62.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59515.0862 | 960967.7345 | 62.03 | 91.63%
[5 empty] | 62.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59526.8947 | 961158.4011 | 62.04 | 91.63%
[5 empty] | 62.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59538.7031 | 961349.0678 | 62.05 | 91.63%
[5 empty] | 62.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59550.5116 | 961539.7345 | 62.06 | 91.63%
[5 empty] | 62.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59562.3201 | 961730.4011 | 62.07 | 91.63%
[5 empty] | 62.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59574.1285 | 961921.0678 | 62.08 | 91.63%
[5 empty] | 62.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59585.937 | 962111.7345 | 62.09 | 91.63%
[5 empty] | 62.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59597.7454 | 962302.4011 | 62.1 | 91.63%
[5 empty] | 62.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59609.5539 | 962493.0678 | 62.11 | 91.63%
[5 empty] | 62.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59621.3623 | 962683.7345 | 62.12 | 91.63%
[5 empty] | 62.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59633.1708 | 962874.4011 | 62.13 | 91.63%
[5 empty] | 62.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59644.9792 | 963065.0678 | 62.14 | 91.63%
[5 empty] | 62.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59656.7877 | 963255.7345 | 62.15 | 91.63%
[5 empty] | 62.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59668.5961 | 963446.4011 | 62.16 | 91.63%
[5 empty] | 62.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59680.4046 | 963637.0678 | 62.17 | 91.63%
[5 empty] | 62.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59692.213 | 963827.7345 | 62.18 | 91.63%
[5 empty] | 62.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59704.0215 | 964018.4011 | 62.19 | 91.63%
[5 empty] | 62.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59715.83 | 964209.0678 | 62.2 | 91.63%
[5 empty] | 62.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59727.6384 | 964399.7345 | 62.21 | 91.63%
[5 empty] | 62.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59739.4469 | 964590.4011 | 62.22 | 91.63%
[5 empty] | 62.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59751.2553 | 964781.0678 | 62.23 | 91.63%
[5 empty] | 62.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59763.0638 | 964971.7345 | 62.24 | 91.63%
[5 empty] | 62.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59774.8722 | 965162.4011 | 62.25 | 91.63%
[5 empty] | 62.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59786.6807 | 965353.0678 | 62.26 | 91.63%
[5 empty] | 62.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59798.4891 | 965543.7345 | 62.27 | 91.63%
[5 empty] | 62.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59810.2976 | 965734.4011 | 62.28 | 91.63%
[5 empty] | 62.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59822.106 | 965925.0678 | 62.29 | 91.63%
[5 empty] | 62.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59833.9145 | 966115.7345 | 62.3 | 91.63%
[5 empty] | 62.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59845.7229 | 966306.4011 | 62.31 | 91.63%
[5 empty] | 62.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59857.5314 | 966497.0678 | 62.32 | 91.63%
[5 empty] | 62.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59869.3399 | 966687.7345 | 62.33 | 91.63%
[5 empty] | 62.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59881.1483 | 966878.4011 | 62.34 | 91.63%
[5 empty] | 62.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59892.9568 | 967069.0678 | 62.35 | 91.63%
[5 empty] | 62.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59904.7652 | 967259.7345 | 62.36 | 91.63%
[5 empty] | 62.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59916.5737 | 967450.4011 | 62.37 | 91.63%
[5 empty] | 62.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59928.3821 | 967641.0678 | 62.38 | 91.63%
[5 empty] | 62.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59940.1906 | 967831.7345 | 62.39 | 91.63%
[5 empty] | 62.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59951.999 | 968022.4011 | 62.4 | 91.63%
[5 empty] | 62.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59963.8075 | 968213.0678 | 62.41 | 91.63%
[5 empty] | 62.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59975.6159 | 968403.7345 | 62.42 | 91.63%
[5 empty] | 62.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59987.4244 | 968594.4011 | 62.43 | 91.63%
[5 empty] | 62.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 59999.2328 | 968785.0678 | 62.44 | 91.63%
[5 empty] | 62.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60011.0413 | 968975.7345 | 62.45 | 91.63%
[5 empty] | 62.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60022.8498 | 969166.4011 | 62.46 | 91.63%
[5 empty] | 62.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60034.6582 | 969357.0678 | 62.47 | 91.63%
[5 empty] | 62.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60046.4667 | 969547.7345 | 62.48 | 91.63%
[5 empty] | 62.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60058.2751 | 969738.4011 | 62.49 | 91.63%
[5 empty] | 62.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60070.0836 | 969929.0678 | 62.5 | 91.63%
[5 empty] | 62.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60081.892 | 970119.7345 | 62.51 | 91.63%
[5 empty] | 62.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60093.7005 | 970310.4011 | 62.52 | 91.63%
[5 empty] | 62.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60105.5089 | 970501.0678 | 62.53 | 91.63%
[5 empty] | 62.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60117.3174 | 970691.7345 | 62.54 | 91.63%
[5 empty] | 62.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60129.1258 | 970882.4011 | 62.55 | 91.63%
[5 empty] | 62.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60140.9343 | 971073.0678 | 62.56 | 91.63%
[5 empty] | 62.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60152.7427 | 971263.7345 | 62.57 | 91.63%
[5 empty] | 62.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60164.5512 | 971454.4011 | 62.58 | 91.63%
[5 empty] | 62.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60176.3597 | 971645.0678 | 62.59 | 91.63%
[5 empty] | 62.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60188.1681 | 971835.7345 | 62.6 | 91.63%
[5 empty] | 62.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60199.9766 | 972026.4011 | 62.61 | 91.63%
[5 empty] | 62.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60211.785 | 972217.0678 | 62.62 | 91.63%
[5 empty] | 62.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60223.5935 | 972407.7345 | 62.63 | 91.63%
[5 empty] | 62.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60235.4019 | 972598.4011 | 62.64 | 91.63%
[5 empty] | 62.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60247.2104 | 972789.0678 | 62.65 | 91.63%
[5 empty] | 62.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60259.0188 | 972979.7345 | 62.66 | 91.63%
[5 empty] | 62.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60270.8273 | 973170.4011 | 62.67 | 91.63%
[5 empty] | 62.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60282.6357 | 973361.0678 | 62.68 | 91.63%
[5 empty] | 62.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60294.4442 | 973551.7345 | 62.69 | 91.63%
[5 empty] | 62.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60306.2526 | 973742.4011 | 62.7 | 91.63%
[5 empty] | 62.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60318.0611 | 973933.0678 | 62.71 | 91.63%
[5 empty] | 62.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60329.8696 | 974123.7345 | 62.72 | 91.63%
[5 empty] | 62.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60341.678 | 974314.4011 | 62.73 | 91.63%
[5 empty] | 62.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60353.4865 | 974505.0678 | 62.74 | 91.63%
[5 empty] | 62.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60365.2949 | 974695.7345 | 62.75 | 91.63%
[5 empty] | 62.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60377.1034 | 974886.4011 | 62.76 | 91.63%
[5 empty] | 62.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60388.9118 | 975077.0678 | 62.77 | 91.63%
[5 empty] | 62.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60400.7203 | 975267.7345 | 62.78 | 91.63%
[5 empty] | 62.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60412.5287 | 975458.4011 | 62.79 | 91.63%
[5 empty] | 62.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60424.3372 | 975649.0678 | 62.8 | 91.63%
[5 empty] | 62.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60436.1456 | 975839.7345 | 62.81 | 91.63%
[5 empty] | 62.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60447.9541 | 976030.4011 | 62.82 | 91.63%
[5 empty] | 62.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60459.7625 | 976221.0678 | 62.83 | 91.63%
[5 empty] | 62.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60471.571 | 976411.7345 | 62.84 | 91.63%
[5 empty] | 62.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60483.3795 | 976602.4011 | 62.85 | 91.63%
[5 empty] | 62.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60495.1879 | 976793.0678 | 62.86 | 91.63%
[5 empty] | 62.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60506.9964 | 976983.7345 | 62.87 | 91.63%
[5 empty] | 62.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60518.8048 | 977174.4011 | 62.88 | 91.63%
[5 empty] | 62.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60530.6133 | 977365.0678 | 62.89 | 91.63%
[5 empty] | 62.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60542.4217 | 977555.7345 | 62.9 | 91.63%
[5 empty] | 62.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60554.2302 | 977746.4011 | 62.91 | 91.63%
[5 empty] | 62.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60566.0386 | 977937.0678 | 62.92 | 91.63%
[5 empty] | 62.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60577.8471 | 978127.7345 | 62.93 | 91.63%
[5 empty] | 62.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60589.6555 | 978318.4011 | 62.94 | 91.63%
[5 empty] | 62.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60601.464 | 978509.0678 | 62.95 | 91.63%
[5 empty] | 62.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60613.2724 | 978699.7345 | 62.96 | 91.63%
[5 empty] | 62.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60625.0809 | 978890.4011 | 62.97 | 91.63%
[5 empty] | 62.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60636.8894 | 979081.0678 | 62.98 | 91.63%
[5 empty] | 62.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60648.6978 | 979271.7345 | 62.99 | 91.63%
[5 empty] | 63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60660.5063 | 979462.4011 | 63 | 91.63%
[5 empty] | 63.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60672.3147 | 979653.0678 | 63.01 | 91.63%
[5 empty] | 63.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60684.1232 | 979843.7345 | 63.02 | 91.63%
[5 empty] | 63.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60695.9316 | 980034.4011 | 63.03 | 91.63%
[5 empty] | 63.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60707.7401 | 980225.0678 | 63.04 | 91.63%
[5 empty] | 63.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60719.5485 | 980415.7345 | 63.05 | 91.63%
[5 empty] | 63.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60731.357 | 980606.4011 | 63.06 | 91.63%
[5 empty] | 63.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60743.1654 | 980797.0678 | 63.07 | 91.63%
[5 empty] | 63.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60754.9739 | 980987.7345 | 63.08 | 91.63%
[5 empty] | 63.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60766.7823 | 981178.4011 | 63.09 | 91.63%
[5 empty] | 63.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60778.5908 | 981369.0678 | 63.1 | 91.63%
[5 empty] | 63.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60790.3993 | 981559.7345 | 63.11 | 91.63%
[5 empty] | 63.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60802.2077 | 981750.4011 | 63.12 | 91.63%
[5 empty] | 63.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60814.0162 | 981941.0678 | 63.13 | 91.63%
[5 empty] | 63.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60825.8246 | 982131.7345 | 63.14 | 91.63%
[5 empty] | 63.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60837.6331 | 982322.4011 | 63.15 | 91.63%
[5 empty] | 63.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60849.4415 | 982513.0678 | 63.16 | 91.63%
[5 empty] | 63.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60861.25 | 982703.7345 | 63.17 | 91.63%
[5 empty] | 63.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60873.0584 | 982894.4011 | 63.18 | 91.63%
[5 empty] | 63.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60884.8669 | 983085.0678 | 63.19 | 91.63%
[5 empty] | 63.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60896.6753 | 983275.7345 | 63.2 | 91.63%
[5 empty] | 63.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60908.4838 | 983466.4011 | 63.21 | 91.63%
[5 empty] | 63.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60920.2922 | 983657.0678 | 63.22 | 91.63%
[5 empty] | 63.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60932.1007 | 983847.7345 | 63.23 | 91.63%
[5 empty] | 63.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60943.9092 | 984038.4011 | 63.24 | 91.63%
[5 empty] | 63.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60955.7176 | 984229.0678 | 63.25 | 91.63%
[5 empty] | 63.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60967.5261 | 984419.7345 | 63.26 | 91.63%
[5 empty] | 63.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60979.3345 | 984610.4011 | 63.27 | 91.63%
[5 empty] | 63.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 60991.143 | 984801.0678 | 63.28 | 91.63%
[5 empty] | 63.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61002.9514 | 984991.7345 | 63.29 | 91.63%
[5 empty] | 63.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61014.7599 | 985182.4011 | 63.3 | 91.63%
[5 empty] | 63.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61026.5683 | 985373.0678 | 63.31 | 91.63%
[5 empty] | 63.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61038.3768 | 985563.7345 | 63.32 | 91.63%
[5 empty] | 63.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61050.1852 | 985754.4011 | 63.33 | 91.63%
[5 empty] | 63.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61061.9937 | 985945.0678 | 63.34 | 91.63%
[5 empty] | 63.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61073.8021 | 986135.7345 | 63.35 | 91.63%
[5 empty] | 63.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61085.6106 | 986326.4011 | 63.36 | 91.63%
[5 empty] | 63.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61097.4191 | 986517.0678 | 63.37 | 91.63%
[5 empty] | 63.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61109.2275 | 986707.7345 | 63.38 | 91.63%
[5 empty] | 63.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61121.036 | 986898.4011 | 63.39 | 91.63%
[5 empty] | 63.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61132.8444 | 987089.0678 | 63.4 | 91.63%
[5 empty] | 63.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61144.6529 | 987279.7345 | 63.41 | 91.63%
[5 empty] | 63.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61156.4613 | 987470.4011 | 63.42 | 91.63%
[5 empty] | 63.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61168.2698 | 987661.0678 | 63.43 | 91.63%
[5 empty] | 63.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61180.0782 | 987851.7345 | 63.44 | 91.63%
[5 empty] | 63.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61191.8867 | 988042.4011 | 63.45 | 91.63%
[5 empty] | 63.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61203.6951 | 988233.0678 | 63.46 | 91.63%
[5 empty] | 63.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61215.5036 | 988423.7345 | 63.47 | 91.63%
[5 empty] | 63.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61227.312 | 988614.4011 | 63.48 | 91.63%
[5 empty] | 63.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61239.1205 | 988805.0678 | 63.49 | 91.63%
[5 empty] | 63.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61250.929 | 988995.7345 | 63.5 | 91.63%
[5 empty] | 63.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61262.7374 | 989186.4011 | 63.51 | 91.63%
[5 empty] | 63.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61274.5459 | 989377.0678 | 63.52 | 91.63%
[5 empty] | 63.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61286.3543 | 989567.7345 | 63.53 | 91.63%
[5 empty] | 63.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61298.1628 | 989758.4011 | 63.54 | 91.63%
[5 empty] | 63.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61309.9712 | 989949.0678 | 63.55 | 91.63%
[5 empty] | 63.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61321.7797 | 990139.7345 | 63.56 | 91.63%
[5 empty] | 63.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61333.5881 | 990330.4011 | 63.57 | 91.63%
[5 empty] | 63.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61345.3966 | 990521.0678 | 63.58 | 91.63%
[5 empty] | 63.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61357.205 | 990711.7345 | 63.59 | 91.63%
[5 empty] | 63.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61369.0135 | 990902.4011 | 63.6 | 91.63%
[5 empty] | 63.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61380.8219 | 991093.0678 | 63.61 | 91.63%
[5 empty] | 63.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61392.6304 | 991283.7345 | 63.62 | 91.63%
[5 empty] | 63.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61404.4389 | 991474.4011 | 63.63 | 91.63%
[5 empty] | 63.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61416.2473 | 991665.0678 | 63.64 | 91.63%
[5 empty] | 63.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61428.0558 | 991855.7345 | 63.65 | 91.63%
[5 empty] | 63.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61439.8642 | 992046.4011 | 63.66 | 91.63%
[5 empty] | 63.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61451.6727 | 992237.0678 | 63.67 | 91.63%
[5 empty] | 63.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61463.4811 | 992427.7345 | 63.68 | 91.63%
[5 empty] | 63.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61475.2896 | 992618.4011 | 63.69 | 91.63%
[5 empty] | 63.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61487.098 | 992809.0678 | 63.7 | 91.63%
[5 empty] | 63.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61498.9065 | 992999.7345 | 63.71 | 91.63%
[5 empty] | 63.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61510.7149 | 993190.4011 | 63.72 | 91.63%
[5 empty] | 63.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61522.5234 | 993381.0678 | 63.73 | 91.63%
[5 empty] | 63.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61534.3318 | 993571.7345 | 63.74 | 91.63%
[5 empty] | 63.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61546.1403 | 993762.4011 | 63.75 | 91.63%
[5 empty] | 63.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61557.9488 | 993953.0678 | 63.76 | 91.63%
[5 empty] | 63.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61569.7572 | 994143.7345 | 63.77 | 91.63%
[5 empty] | 63.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61581.5657 | 994334.4011 | 63.78 | 91.63%
[5 empty] | 63.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61593.3741 | 994525.0678 | 63.79 | 91.63%
[5 empty] | 63.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61605.1826 | 994715.7345 | 63.8 | 91.63%
[5 empty] | 63.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61616.991 | 994906.4011 | 63.81 | 91.63%
[5 empty] | 63.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61628.7995 | 995097.0678 | 63.82 | 91.63%
[5 empty] | 63.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61640.6079 | 995287.7345 | 63.83 | 91.63%
[5 empty] | 63.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61652.4164 | 995478.4011 | 63.84 | 91.63%
[5 empty] | 63.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61664.2248 | 995669.0678 | 63.85 | 91.63%
[5 empty] | 63.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61676.0333 | 995859.7345 | 63.86 | 91.63%
[5 empty] | 63.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61687.8417 | 996050.4011 | 63.87 | 91.63%
[5 empty] | 63.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61699.6502 | 996241.0678 | 63.88 | 91.63%
[5 empty] | 63.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61711.4587 | 996431.7345 | 63.89 | 91.63%
[5 empty] | 63.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61723.2671 | 996622.4011 | 63.9 | 91.63%
[5 empty] | 63.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61735.0756 | 996813.0678 | 63.91 | 91.63%
[5 empty] | 63.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61746.884 | 997003.7345 | 63.92 | 91.63%
[5 empty] | 63.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61758.6925 | 997194.4011 | 63.93 | 91.63%
[5 empty] | 63.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61770.5009 | 997385.0678 | 63.94 | 91.63%
[5 empty] | 63.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61782.3094 | 997575.7345 | 63.95 | 91.63%
[5 empty] | 63.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61794.1178 | 997766.4011 | 63.96 | 91.63%
[5 empty] | 63.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61805.9263 | 997957.0678 | 63.97 | 91.63%
[5 empty] | 63.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61817.7347 | 998147.7345 | 63.98 | 91.63%
[5 empty] | 63.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61829.5432 | 998338.4011 | 63.99 | 91.63%
[5 empty] | 64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61841.3516 | 998529.0678 | 64 | 91.63%
[5 empty] | 64.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61853.1601 | 998719.7345 | 64.01 | 91.63%
[5 empty] | 64.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61864.9686 | 998910.4011 | 64.02 | 91.63%
[5 empty] | 64.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61876.777 | 999101.0678 | 64.03 | 91.63%
[5 empty] | 64.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61888.5855 | 999291.7345 | 64.04 | 91.63%
[5 empty] | 64.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61900.3939 | 999482.4011 | 64.05 | 91.63%
[5 empty] | 64.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61912.2024 | 999673.0678 | 64.06 | 91.63%
[5 empty] | 64.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61924.0108 | 999863.7345 | 64.07 | 91.63%
[5 empty] | 64.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61935.8193 | 1000054.4011 | 64.08 | 91.63%
[5 empty] | 64.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61947.6277 | 1000245.0678 | 64.09 | 91.63%
[5 empty] | 64.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61959.4362 | 1000435.7345 | 64.1 | 91.63%
[5 empty] | 64.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61971.2446 | 1000626.4011 | 64.11 | 91.63%
[5 empty] | 64.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61983.0531 | 1000817.0678 | 64.12 | 91.63%
[5 empty] | 64.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 61994.8615 | 1001007.7345 | 64.13 | 91.63%
[5 empty] | 64.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62006.67 | 1001198.4011 | 64.14 | 91.63%
[5 empty] | 64.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62018.4785 | 1001389.0678 | 64.15 | 91.63%
[5 empty] | 64.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62030.2869 | 1001579.7345 | 64.16 | 91.63%
[5 empty] | 64.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62042.0954 | 1001770.4011 | 64.17 | 91.63%
[5 empty] | 64.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62053.9038 | 1001961.0678 | 64.18 | 91.63%
[5 empty] | 64.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62065.7123 | 1002151.7345 | 64.19 | 91.63%
[5 empty] | 64.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62077.5207 | 1002342.4011 | 64.2 | 91.63%
[5 empty] | 64.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62089.3292 | 1002533.0678 | 64.21 | 91.63%
[5 empty] | 64.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62101.1376 | 1002723.7345 | 64.22 | 91.63%
[5 empty] | 64.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62112.9461 | 1002914.4011 | 64.23 | 91.63%
[5 empty] | 64.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62124.7545 | 1003105.0678 | 64.24 | 91.63%
[5 empty] | 64.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62136.563 | 1003295.7345 | 64.25 | 91.63%
[5 empty] | 64.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62148.3714 | 1003486.4011 | 64.26 | 91.63%
[5 empty] | 64.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62160.1799 | 1003677.0678 | 64.27 | 91.63%
[5 empty] | 64.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62171.9883 | 1003867.7345 | 64.28 | 91.63%
[5 empty] | 64.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62183.7968 | 1004058.4011 | 64.29 | 91.63%
[5 empty] | 64.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62195.6053 | 1004249.0678 | 64.3 | 91.63%
[5 empty] | 64.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62207.4137 | 1004439.7345 | 64.31 | 91.63%
[5 empty] | 64.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62219.2222 | 1004630.4011 | 64.32 | 91.63%
[5 empty] | 64.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62231.0306 | 1004821.0678 | 64.33 | 91.63%
[5 empty] | 64.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62242.8391 | 1005011.7345 | 64.34 | 91.63%
[5 empty] | 64.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62254.6475 | 1005202.4011 | 64.35 | 91.63%
[5 empty] | 64.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62266.456 | 1005393.0678 | 64.36 | 91.63%
[5 empty] | 64.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62278.2644 | 1005583.7345 | 64.37 | 91.63%
[5 empty] | 64.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62290.0729 | 1005774.4011 | 64.38 | 91.63%
[5 empty] | 64.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62301.8813 | 1005965.0678 | 64.39 | 91.63%
[5 empty] | 64.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62313.6898 | 1006155.7345 | 64.4 | 91.63%
[5 empty] | 64.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62325.4982 | 1006346.4011 | 64.41 | 91.63%
[5 empty] | 64.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62337.3067 | 1006537.0678 | 64.42 | 91.63%
[5 empty] | 64.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62349.1152 | 1006727.7345 | 64.43 | 91.63%
[5 empty] | 64.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62360.9236 | 1006918.4011 | 64.44 | 91.63%
[5 empty] | 64.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62372.7321 | 1007109.0678 | 64.45 | 91.63%
[5 empty] | 64.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62384.5405 | 1007299.7345 | 64.46 | 91.63%
[5 empty] | 64.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62396.349 | 1007490.4011 | 64.47 | 91.63%
[5 empty] | 64.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62408.1574 | 1007681.0678 | 64.48 | 91.63%
[5 empty] | 64.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62419.9659 | 1007871.7345 | 64.49 | 91.63%
[5 empty] | 64.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62431.7743 | 1008062.4011 | 64.5 | 91.63%
[5 empty] | 64.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62443.5828 | 1008253.0678 | 64.51 | 91.63%
[5 empty] | 64.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62455.3912 | 1008443.7345 | 64.52 | 91.63%
[5 empty] | 64.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62467.1997 | 1008634.4011 | 64.53 | 91.63%
[5 empty] | 64.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62479.0081 | 1008825.0678 | 64.54 | 91.63%
[5 empty] | 64.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62490.8166 | 1009015.7345 | 64.55 | 91.63%
[5 empty] | 64.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62502.6251 | 1009206.4011 | 64.56 | 91.63%
[5 empty] | 64.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62514.4335 | 1009397.0678 | 64.57 | 91.63%
[5 empty] | 64.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62526.242 | 1009587.7345 | 64.58 | 91.63%
[5 empty] | 64.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62538.0504 | 1009778.4011 | 64.59 | 91.63%
[5 empty] | 64.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62549.8589 | 1009969.0678 | 64.6 | 91.63%
[5 empty] | 64.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62561.6673 | 1010159.7345 | 64.61 | 91.63%
[5 empty] | 64.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62573.4758 | 1010350.4011 | 64.62 | 91.63%
[5 empty] | 64.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62585.2842 | 1010541.0678 | 64.63 | 91.63%
[5 empty] | 64.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62597.0927 | 1010731.7345 | 64.64 | 91.63%
[5 empty] | 64.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62608.9011 | 1010922.4011 | 64.65 | 91.63%
[5 empty] | 64.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62620.7096 | 1011113.0678 | 64.66 | 91.63%
[5 empty] | 64.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62632.518 | 1011303.7345 | 64.67 | 91.63%
[5 empty] | 64.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62644.3265 | 1011494.4011 | 64.68 | 91.63%
[5 empty] | 64.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62656.135 | 1011685.0678 | 64.69 | 91.63%
[5 empty] | 64.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62667.9434 | 1011875.7345 | 64.7 | 91.63%
[5 empty] | 64.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62679.7519 | 1012066.4011 | 64.71 | 91.63%
[5 empty] | 64.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62691.5603 | 1012257.0678 | 64.72 | 91.63%
[5 empty] | 64.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62703.3688 | 1012447.7345 | 64.73 | 91.63%
[5 empty] | 64.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62715.1772 | 1012638.4011 | 64.74 | 91.63%
[5 empty] | 64.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62726.9857 | 1012829.0678 | 64.75 | 91.63%
[5 empty] | 64.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62738.7941 | 1013019.7345 | 64.76 | 91.63%
[5 empty] | 64.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62750.6026 | 1013210.4011 | 64.77 | 91.63%
[5 empty] | 64.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62762.411 | 1013401.0678 | 64.78 | 91.63%
[5 empty] | 64.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62774.2195 | 1013591.7345 | 64.79 | 91.63%
[5 empty] | 64.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62786.0279 | 1013782.4011 | 64.8 | 91.63%
[5 empty] | 64.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62797.8364 | 1013973.0678 | 64.81 | 91.63%
[5 empty] | 64.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62809.6449 | 1014163.7345 | 64.82 | 91.63%
[5 empty] | 64.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62821.4533 | 1014354.4011 | 64.83 | 91.63%
[5 empty] | 64.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62833.2618 | 1014545.0678 | 64.84 | 91.63%
[5 empty] | 64.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62845.0702 | 1014735.7345 | 64.85 | 91.63%
[5 empty] | 64.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62856.8787 | 1014926.4011 | 64.86 | 91.63%
[5 empty] | 64.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62868.6871 | 1015117.0678 | 64.87 | 91.63%
[5 empty] | 64.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62880.4956 | 1015307.7345 | 64.88 | 91.63%
[5 empty] | 64.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62892.304 | 1015498.4011 | 64.89 | 91.63%
[5 empty] | 64.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62904.1125 | 1015689.0678 | 64.9 | 91.63%
[5 empty] | 64.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62915.9209 | 1015879.7345 | 64.91 | 91.63%
[5 empty] | 64.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62927.7294 | 1016070.4011 | 64.92 | 91.63%
[5 empty] | 64.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62939.5378 | 1016261.0678 | 64.93 | 91.63%
[5 empty] | 64.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62951.3463 | 1016451.7345 | 64.94 | 91.63%
[5 empty] | 64.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62963.1548 | 1016642.4011 | 64.95 | 91.63%
[5 empty] | 64.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62974.9632 | 1016833.0678 | 64.96 | 91.63%
[5 empty] | 64.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62986.7717 | 1017023.7345 | 64.97 | 91.63%
[5 empty] | 64.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 62998.5801 | 1017214.4011 | 64.98 | 91.63%
[5 empty] | 64.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63010.3886 | 1017405.0678 | 64.99 | 91.63%
[5 empty] | 65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63022.197 | 1017595.7345 | 65 | 91.63%
[5 empty] | 65.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63034.0055 | 1017786.4011 | 65.01 | 91.63%
[5 empty] | 65.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63045.8139 | 1017977.0678 | 65.02 | 91.63%
[5 empty] | 65.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63057.6224 | 1018167.7345 | 65.03 | 91.63%
[5 empty] | 65.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63069.4308 | 1018358.4011 | 65.04 | 91.63%
[5 empty] | 65.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63081.2393 | 1018549.0678 | 65.05 | 91.63%
[5 empty] | 65.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63093.0477 | 1018739.7345 | 65.06 | 91.63%
[5 empty] | 65.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63104.8562 | 1018930.4011 | 65.07 | 91.63%
[5 empty] | 65.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63116.6647 | 1019121.0678 | 65.08 | 91.63%
[5 empty] | 65.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63128.4731 | 1019311.7345 | 65.09 | 91.63%
[5 empty] | 65.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63140.2816 | 1019502.4011 | 65.1 | 91.63%
[5 empty] | 65.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63152.09 | 1019693.0678 | 65.11 | 91.63%
[5 empty] | 65.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63163.8985 | 1019883.7345 | 65.12 | 91.63%
[5 empty] | 65.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63175.7069 | 1020074.4011 | 65.13 | 91.63%
[5 empty] | 65.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63187.5154 | 1020265.0678 | 65.14 | 91.63%
[5 empty] | 65.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63199.3238 | 1020455.7345 | 65.15 | 91.63%
[5 empty] | 65.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63211.1323 | 1020646.4011 | 65.16 | 91.63%
[5 empty] | 65.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63222.9407 | 1020837.0678 | 65.17 | 91.63%
[5 empty] | 65.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63234.7492 | 1021027.7345 | 65.18 | 91.63%
[5 empty] | 65.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63246.5576 | 1021218.4011 | 65.19 | 91.63%
[5 empty] | 65.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63258.3661 | 1021409.0678 | 65.2 | 91.63%
[5 empty] | 65.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63270.1746 | 1021599.7345 | 65.21 | 91.63%
[5 empty] | 65.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63281.983 | 1021790.4011 | 65.22 | 91.63%
[5 empty] | 65.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63293.7915 | 1021981.0678 | 65.23 | 91.63%
[5 empty] | 65.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63305.5999 | 1022171.7345 | 65.24 | 91.63%
[5 empty] | 65.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63317.4084 | 1022362.4011 | 65.25 | 91.63%
[5 empty] | 65.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63329.2168 | 1022553.0678 | 65.26 | 91.63%
[5 empty] | 65.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63341.0253 | 1022743.7345 | 65.27 | 91.63%
[5 empty] | 65.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63352.8337 | 1022934.4011 | 65.28 | 91.63%
[5 empty] | 65.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63364.6422 | 1023125.0678 | 65.29 | 91.63%
[5 empty] | 65.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63376.4506 | 1023315.7345 | 65.3 | 91.63%
[5 empty] | 65.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63388.2591 | 1023506.4011 | 65.31 | 91.63%
[5 empty] | 65.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63400.0675 | 1023697.0678 | 65.32 | 91.63%
[5 empty] | 65.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63411.876 | 1023887.7345 | 65.33 | 91.63%
[5 empty] | 65.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63423.6845 | 1024078.4011 | 65.34 | 91.63%
[5 empty] | 65.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63435.4929 | 1024269.0678 | 65.35 | 91.63%
[5 empty] | 65.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63447.3014 | 1024459.7345 | 65.36 | 91.63%
[5 empty] | 65.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63459.1098 | 1024650.4011 | 65.37 | 91.63%
[5 empty] | 65.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63470.9183 | 1024841.0678 | 65.38 | 91.63%
[5 empty] | 65.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63482.7267 | 1025031.7345 | 65.39 | 91.63%
[5 empty] | 65.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63494.5352 | 1025222.4011 | 65.4 | 91.63%
[5 empty] | 65.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63506.3436 | 1025413.0678 | 65.41 | 91.63%
[5 empty] | 65.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63518.1521 | 1025603.7345 | 65.42 | 91.63%
[5 empty] | 65.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63529.9605 | 1025794.4011 | 65.43 | 91.63%
[5 empty] | 65.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63541.769 | 1025985.0678 | 65.44 | 91.63%
[5 empty] | 65.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63553.5774 | 1026175.7345 | 65.45 | 91.63%
[5 empty] | 65.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63565.3859 | 1026366.4011 | 65.46 | 91.63%
[5 empty] | 65.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63577.1944 | 1026557.0678 | 65.47 | 91.63%
[5 empty] | 65.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63589.0028 | 1026747.7345 | 65.48 | 91.63%
[5 empty] | 65.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63600.8113 | 1026938.4011 | 65.49 | 91.63%
[5 empty] | 65.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63612.6197 | 1027129.0678 | 65.5 | 91.63%
[5 empty] | 65.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63624.4282 | 1027319.7345 | 65.51 | 91.63%
[5 empty] | 65.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63636.2366 | 1027510.4011 | 65.52 | 91.63%
[5 empty] | 65.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63648.0451 | 1027701.0678 | 65.53 | 91.63%
[5 empty] | 65.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63659.8535 | 1027891.7345 | 65.54 | 91.63%
[5 empty] | 65.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63671.662 | 1028082.4011 | 65.55 | 91.63%
[5 empty] | 65.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63683.4704 | 1028273.0678 | 65.56 | 91.63%
[5 empty] | 65.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63695.2789 | 1028463.7345 | 65.57 | 91.63%
[5 empty] | 65.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63707.0873 | 1028654.4011 | 65.58 | 91.63%
[5 empty] | 65.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63718.8958 | 1028845.0678 | 65.59 | 91.63%
[5 empty] | 65.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63730.7043 | 1029035.7345 | 65.6 | 91.63%
[5 empty] | 65.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63742.5127 | 1029226.4011 | 65.61 | 91.63%
[5 empty] | 65.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63754.3212 | 1029417.0678 | 65.62 | 91.63%
[5 empty] | 65.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63766.1296 | 1029607.7345 | 65.63 | 91.63%
[5 empty] | 65.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63777.9381 | 1029798.4011 | 65.64 | 91.63%
[5 empty] | 65.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63789.7465 | 1029989.0678 | 65.65 | 91.63%
[5 empty] | 65.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63801.555 | 1030179.7345 | 65.66 | 91.63%
[5 empty] | 65.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63813.3634 | 1030370.4011 | 65.67 | 91.63%
[5 empty] | 65.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63825.1719 | 1030561.0678 | 65.68 | 91.63%
[5 empty] | 65.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63836.9803 | 1030751.7345 | 65.69 | 91.63%
[5 empty] | 65.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63848.7888 | 1030942.4011 | 65.7 | 91.63%
[5 empty] | 65.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63860.5972 | 1031133.0678 | 65.71 | 91.63%
[5 empty] | 65.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63872.4057 | 1031323.7345 | 65.72 | 91.63%
[5 empty] | 65.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63884.2142 | 1031514.4011 | 65.73 | 91.63%
[5 empty] | 65.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63896.0226 | 1031705.0678 | 65.74 | 91.63%
[5 empty] | 65.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63907.8311 | 1031895.7345 | 65.75 | 91.63%
[5 empty] | 65.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63919.6395 | 1032086.4011 | 65.76 | 91.63%
[5 empty] | 65.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63931.448 | 1032277.0678 | 65.77 | 91.63%
[5 empty] | 65.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63943.2564 | 1032467.7345 | 65.78 | 91.63%
[5 empty] | 65.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63955.0649 | 1032658.4011 | 65.79 | 91.63%
[5 empty] | 65.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63966.8733 | 1032849.0678 | 65.8 | 91.63%
[5 empty] | 65.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63978.6818 | 1033039.7345 | 65.81 | 91.63%
[5 empty] | 65.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 63990.4902 | 1033230.4011 | 65.82 | 91.63%
[5 empty] | 65.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64002.2987 | 1033421.0678 | 65.83 | 91.63%
[5 empty] | 65.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64014.1071 | 1033611.7345 | 65.84 | 91.63%
[5 empty] | 65.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64025.9156 | 1033802.4011 | 65.85 | 91.63%
[5 empty] | 65.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64037.7241 | 1033993.0678 | 65.86 | 91.63%
[5 empty] | 65.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64049.5325 | 1034183.7345 | 65.87 | 91.63%
[5 empty] | 65.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64061.341 | 1034374.4011 | 65.88 | 91.63%
[5 empty] | 65.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64073.1494 | 1034565.0678 | 65.89 | 91.63%
[5 empty] | 65.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64084.9579 | 1034755.7345 | 65.9 | 91.63%
[5 empty] | 65.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64096.7663 | 1034946.4011 | 65.91 | 91.63%
[5 empty] | 65.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64108.5748 | 1035137.0678 | 65.92 | 91.63%
[5 empty] | 65.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64120.3832 | 1035327.7345 | 65.93 | 91.63%
[5 empty] | 65.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64132.1917 | 1035518.4011 | 65.94 | 91.63%
[5 empty] | 65.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64144.0001 | 1035709.0678 | 65.95 | 91.63%
[5 empty] | 65.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64155.8086 | 1035899.7345 | 65.96 | 91.63%
[5 empty] | 65.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64167.617 | 1036090.4011 | 65.97 | 91.63%
[5 empty] | 65.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64179.4255 | 1036281.0678 | 65.98 | 91.63%
[5 empty] | 65.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64191.234 | 1036471.7345 | 65.99 | 91.63%
[5 empty] | 66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64203.0424 | 1036662.4011 | 66 | 91.63%
[5 empty] | 66.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64214.8509 | 1036853.0678 | 66.01 | 91.63%
[5 empty] | 66.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64226.6593 | 1037043.7345 | 66.02 | 91.63%
[5 empty] | 66.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64238.4678 | 1037234.4011 | 66.03 | 91.63%
[5 empty] | 66.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64250.2762 | 1037425.0678 | 66.04 | 91.63%
[5 empty] | 66.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64262.0847 | 1037615.7345 | 66.05 | 91.63%
[5 empty] | 66.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64273.8931 | 1037806.4011 | 66.06 | 91.63%
[5 empty] | 66.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64285.7016 | 1037997.0678 | 66.07 | 91.63%
[5 empty] | 66.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64297.51 | 1038187.7345 | 66.08 | 91.63%
[5 empty] | 66.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64309.3185 | 1038378.4011 | 66.09 | 91.63%
[5 empty] | 66.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64321.1269 | 1038569.0678 | 66.1 | 91.63%
[5 empty] | 66.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64332.9354 | 1038759.7345 | 66.11 | 91.63%
[5 empty] | 66.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64344.7439 | 1038950.4011 | 66.12 | 91.63%
[5 empty] | 66.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64356.5523 | 1039141.0678 | 66.13 | 91.63%
[5 empty] | 66.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64368.3608 | 1039331.7345 | 66.14 | 91.63%
[5 empty] | 66.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64380.1692 | 1039522.4011 | 66.15 | 91.63%
[5 empty] | 66.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64391.9777 | 1039713.0678 | 66.16 | 91.63%
[5 empty] | 66.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64403.7861 | 1039903.7345 | 66.17 | 91.63%
[5 empty] | 66.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64415.5946 | 1040094.4011 | 66.18 | 91.63%
[5 empty] | 66.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64427.403 | 1040285.0678 | 66.19 | 91.63%
[5 empty] | 66.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64439.2115 | 1040475.7345 | 66.2 | 91.63%
[5 empty] | 66.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64451.0199 | 1040666.4011 | 66.21 | 91.63%
[5 empty] | 66.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64462.8284 | 1040857.0678 | 66.22 | 91.63%
[5 empty] | 66.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64474.6368 | 1041047.7345 | 66.23 | 91.63%
[5 empty] | 66.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64486.4453 | 1041238.4011 | 66.24 | 91.63%
[5 empty] | 66.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64498.2538 | 1041429.0678 | 66.25 | 91.63%
[5 empty] | 66.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64510.0622 | 1041619.7345 | 66.26 | 91.63%
[5 empty] | 66.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64521.8707 | 1041810.4011 | 66.27 | 91.63%
[5 empty] | 66.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64533.6791 | 1042001.0678 | 66.28 | 91.63%
[5 empty] | 66.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64545.4876 | 1042191.7345 | 66.29 | 91.63%
[5 empty] | 66.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64557.296 | 1042382.4011 | 66.3 | 91.63%
[5 empty] | 66.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64569.1045 | 1042573.0678 | 66.31 | 91.63%
[5 empty] | 66.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64580.9129 | 1042763.7345 | 66.32 | 91.63%
[5 empty] | 66.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64592.7214 | 1042954.4011 | 66.33 | 91.63%
[5 empty] | 66.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64604.5298 | 1043145.0678 | 66.34 | 91.63%
[5 empty] | 66.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64616.3383 | 1043335.7345 | 66.35 | 91.63%
[5 empty] | 66.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64628.1467 | 1043526.4011 | 66.36 | 91.63%
[5 empty] | 66.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64639.9552 | 1043717.0678 | 66.37 | 91.63%
[5 empty] | 66.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64651.7637 | 1043907.7345 | 66.38 | 91.63%
[5 empty] | 66.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64663.5721 | 1044098.4011 | 66.39 | 91.63%
[5 empty] | 66.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64675.3806 | 1044289.0678 | 66.4 | 91.63%
[5 empty] | 66.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64687.189 | 1044479.7345 | 66.41 | 91.63%
[5 empty] | 66.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64698.9975 | 1044670.4011 | 66.42 | 91.63%
[5 empty] | 66.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64710.8059 | 1044861.0678 | 66.43 | 91.63%
[5 empty] | 66.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64722.6144 | 1045051.7345 | 66.44 | 91.63%
[5 empty] | 66.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64734.4228 | 1045242.4011 | 66.45 | 91.63%
[5 empty] | 66.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64746.2313 | 1045433.0678 | 66.46 | 91.63%
[5 empty] | 66.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64758.0397 | 1045623.7345 | 66.47 | 91.63%
[5 empty] | 66.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64769.8482 | 1045814.4011 | 66.48 | 91.63%
[5 empty] | 66.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64781.6566 | 1046005.0678 | 66.49 | 91.63%
[5 empty] | 66.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64793.4651 | 1046195.7345 | 66.5 | 91.63%
[5 empty] | 66.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64805.2736 | 1046386.4011 | 66.51 | 91.63%
[5 empty] | 66.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64817.082 | 1046577.0678 | 66.52 | 91.63%
[5 empty] | 66.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64828.8905 | 1046767.7345 | 66.53 | 91.63%
[5 empty] | 66.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64840.6989 | 1046958.4011 | 66.54 | 91.63%
[5 empty] | 66.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64852.5074 | 1047149.0678 | 66.55 | 91.63%
[5 empty] | 66.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64864.3158 | 1047339.7345 | 66.56 | 91.63%
[5 empty] | 66.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64876.1243 | 1047530.4011 | 66.57 | 91.63%
[5 empty] | 66.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64887.9327 | 1047721.0678 | 66.58 | 91.63%
[5 empty] | 66.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64899.7412 | 1047911.7345 | 66.59 | 91.63%
[5 empty] | 66.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64911.5496 | 1048102.4011 | 66.6 | 91.63%
[5 empty] | 66.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64923.3581 | 1048293.0678 | 66.61 | 91.63%
[5 empty] | 66.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64935.1665 | 1048483.7345 | 66.62 | 91.63%
[5 empty] | 66.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64946.975 | 1048674.4011 | 66.63 | 91.63%
[5 empty] | 66.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64958.7835 | 1048865.0678 | 66.64 | 91.63%
[5 empty] | 66.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64970.5919 | 1049055.7345 | 66.65 | 91.63%
[5 empty] | 66.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64982.4004 | 1049246.4011 | 66.66 | 91.63%
[5 empty] | 66.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 64994.2088 | 1049437.0678 | 66.67 | 91.63%
[5 empty] | 66.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65006.0173 | 1049627.7345 | 66.68 | 91.63%
[5 empty] | 66.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65017.8257 | 1049818.4011 | 66.69 | 91.63%
[5 empty] | 66.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65029.6342 | 1050009.0678 | 66.7 | 91.63%
[5 empty] | 66.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65041.4426 | 1050199.7345 | 66.71 | 91.63%
[5 empty] | 66.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65053.2511 | 1050390.4011 | 66.72 | 91.63%
[5 empty] | 66.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65065.0595 | 1050581.0678 | 66.73 | 91.63%
[5 empty] | 66.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65076.868 | 1050771.7345 | 66.74 | 91.63%
[5 empty] | 66.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65088.6764 | 1050962.4011 | 66.75 | 91.63%
[5 empty] | 66.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65100.4849 | 1051153.0678 | 66.76 | 91.63%
[5 empty] | 66.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65112.2933 | 1051343.7345 | 66.77 | 91.63%
[5 empty] | 66.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65124.1018 | 1051534.4011 | 66.78 | 91.63%
[5 empty] | 66.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65135.9103 | 1051725.0678 | 66.79 | 91.63%
[5 empty] | 66.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65147.7187 | 1051915.7345 | 66.8 | 91.63%
[5 empty] | 66.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65159.5272 | 1052106.4011 | 66.81 | 91.63%
[5 empty] | 66.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65171.3356 | 1052297.0678 | 66.82 | 91.63%
[5 empty] | 66.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65183.1441 | 1052487.7345 | 66.83 | 91.63%
[5 empty] | 66.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65194.9525 | 1052678.4011 | 66.84 | 91.63%
[5 empty] | 66.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65206.761 | 1052869.0678 | 66.85 | 91.63%
[5 empty] | 66.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65218.5694 | 1053059.7345 | 66.86 | 91.63%
[5 empty] | 66.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65230.3779 | 1053250.4011 | 66.87 | 91.63%
[5 empty] | 66.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65242.1863 | 1053441.0678 | 66.88 | 91.63%
[5 empty] | 66.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65253.9948 | 1053631.7345 | 66.89 | 91.63%
[5 empty] | 66.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65265.8032 | 1053822.4011 | 66.9 | 91.63%
[5 empty] | 66.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65277.6117 | 1054013.0678 | 66.91 | 91.63%
[5 empty] | 66.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65289.4202 | 1054203.7345 | 66.92 | 91.63%
[5 empty] | 66.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65301.2286 | 1054394.4011 | 66.93 | 91.63%
[5 empty] | 66.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65313.0371 | 1054585.0678 | 66.94 | 91.63%
[5 empty] | 66.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65324.8455 | 1054775.7345 | 66.95 | 91.63%
[5 empty] | 66.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65336.654 | 1054966.4011 | 66.96 | 91.63%
[5 empty] | 66.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65348.4624 | 1055157.0678 | 66.97 | 91.63%
[5 empty] | 66.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65360.2709 | 1055347.7345 | 66.98 | 91.63%
[5 empty] | 66.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65372.0793 | 1055538.4011 | 66.99 | 91.63%
[5 empty] | 67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65383.8878 | 1055729.0678 | 67 | 91.63%
[5 empty] | 67.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65395.6962 | 1055919.7345 | 67.01 | 91.63%
[5 empty] | 67.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65407.5047 | 1056110.4011 | 67.02 | 91.63%
[5 empty] | 67.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65419.3131 | 1056301.0678 | 67.03 | 91.63%
[5 empty] | 67.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65431.1216 | 1056491.7345 | 67.04 | 91.63%
[5 empty] | 67.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65442.9301 | 1056682.4011 | 67.05 | 91.63%
[5 empty] | 67.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65454.7385 | 1056873.0678 | 67.06 | 91.63%
[5 empty] | 67.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65466.547 | 1057063.7345 | 67.07 | 91.63%
[5 empty] | 67.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65478.3554 | 1057254.4011 | 67.08 | 91.63%
[5 empty] | 67.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65490.1639 | 1057445.0678 | 67.09 | 91.63%
[5 empty] | 67.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65501.9723 | 1057635.7345 | 67.1 | 91.63%
[5 empty] | 67.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65513.7808 | 1057826.4011 | 67.11 | 91.63%
[5 empty] | 67.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65525.5892 | 1058017.0678 | 67.12 | 91.63%
[5 empty] | 67.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65537.3977 | 1058207.7345 | 67.13 | 91.63%
[5 empty] | 67.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65549.2061 | 1058398.4011 | 67.14 | 91.63%
[5 empty] | 67.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65561.0146 | 1058589.0678 | 67.15 | 91.63%
[5 empty] | 67.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65572.823 | 1058779.7345 | 67.16 | 91.63%
[5 empty] | 67.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65584.6315 | 1058970.4011 | 67.17 | 91.63%
[5 empty] | 67.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65596.44 | 1059161.0678 | 67.18 | 91.63%
[5 empty] | 67.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65608.2484 | 1059351.7345 | 67.19 | 91.63%
[5 empty] | 67.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65620.0569 | 1059542.4011 | 67.2 | 91.63%
[5 empty] | 67.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65631.8653 | 1059733.0678 | 67.21 | 91.63%
[5 empty] | 67.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65643.6738 | 1059923.7345 | 67.22 | 91.63%
[5 empty] | 67.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65655.4822 | 1060114.4011 | 67.23 | 91.63%
[5 empty] | 67.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65667.2907 | 1060305.0678 | 67.24 | 91.63%
[5 empty] | 67.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65679.0991 | 1060495.7345 | 67.25 | 91.63%
[5 empty] | 67.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65690.9076 | 1060686.4011 | 67.26 | 91.63%
[5 empty] | 67.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65702.716 | 1060877.0678 | 67.27 | 91.63%
[5 empty] | 67.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65714.5245 | 1061067.7345 | 67.28 | 91.63%
[5 empty] | 67.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65726.3329 | 1061258.4011 | 67.29 | 91.63%
[5 empty] | 67.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65738.1414 | 1061449.0678 | 67.3 | 91.63%
[5 empty] | 67.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65749.9499 | 1061639.7345 | 67.31 | 91.63%
[5 empty] | 67.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65761.7583 | 1061830.4011 | 67.32 | 91.63%
[5 empty] | 67.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65773.5668 | 1062021.0678 | 67.33 | 91.63%
[5 empty] | 67.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65785.3752 | 1062211.7345 | 67.34 | 91.63%
[5 empty] | 67.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65797.1837 | 1062402.4011 | 67.35 | 91.63%
[5 empty] | 67.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65808.9921 | 1062593.0678 | 67.36 | 91.63%
[5 empty] | 67.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65820.8006 | 1062783.7345 | 67.37 | 91.63%
[5 empty] | 67.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65832.609 | 1062974.4011 | 67.38 | 91.63%
[5 empty] | 67.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65844.4175 | 1063165.0678 | 67.39 | 91.63%
[5 empty] | 67.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65856.2259 | 1063355.7345 | 67.4 | 91.63%
[5 empty] | 67.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65868.0344 | 1063546.4011 | 67.41 | 91.63%
[5 empty] | 67.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65879.8428 | 1063737.0678 | 67.42 | 91.63%
[5 empty] | 67.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65891.6513 | 1063927.7345 | 67.43 | 91.63%
[5 empty] | 67.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65903.4598 | 1064118.4011 | 67.44 | 91.63%
[5 empty] | 67.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65915.2682 | 1064309.0678 | 67.45 | 91.63%
[5 empty] | 67.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65927.0767 | 1064499.7345 | 67.46 | 91.63%
[5 empty] | 67.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65938.8851 | 1064690.4011 | 67.47 | 91.63%
[5 empty] | 67.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65950.6936 | 1064881.0678 | 67.48 | 91.63%
[5 empty] | 67.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65962.502 | 1065071.7345 | 67.49 | 91.63%
[5 empty] | 67.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65974.3105 | 1065262.4011 | 67.5 | 91.63%
[5 empty] | 67.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65986.1189 | 1065453.0678 | 67.51 | 91.63%
[5 empty] | 67.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 65997.9274 | 1065643.7345 | 67.52 | 91.63%
[5 empty] | 67.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66009.7358 | 1065834.4011 | 67.53 | 91.63%
[5 empty] | 67.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66021.5443 | 1066025.0678 | 67.54 | 91.63%
[5 empty] | 67.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66033.3527 | 1066215.7345 | 67.55 | 91.63%
[5 empty] | 67.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66045.1612 | 1066406.4011 | 67.56 | 91.63%
[5 empty] | 67.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66056.9697 | 1066597.0678 | 67.57 | 91.63%
[5 empty] | 67.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66068.7781 | 1066787.7345 | 67.58 | 91.63%
[5 empty] | 67.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66080.5866 | 1066978.4011 | 67.59 | 91.63%
[5 empty] | 67.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66092.395 | 1067169.0678 | 67.6 | 91.63%
[5 empty] | 67.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66104.2035 | 1067359.7345 | 67.61 | 91.63%
[5 empty] | 67.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66116.0119 | 1067550.4011 | 67.62 | 91.63%
[5 empty] | 67.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66127.8204 | 1067741.0678 | 67.63 | 91.63%
[5 empty] | 67.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66139.6288 | 1067931.7345 | 67.64 | 91.63%
[5 empty] | 67.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66151.4373 | 1068122.4011 | 67.65 | 91.63%
[5 empty] | 67.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66163.2457 | 1068313.0678 | 67.66 | 91.63%
[5 empty] | 67.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66175.0542 | 1068503.7345 | 67.67 | 91.63%
[5 empty] | 67.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66186.8626 | 1068694.4011 | 67.68 | 91.63%
[5 empty] | 67.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66198.6711 | 1068885.0678 | 67.69 | 91.63%
[5 empty] | 67.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66210.4796 | 1069075.7345 | 67.7 | 91.63%
[5 empty] | 67.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66222.288 | 1069266.4011 | 67.71 | 91.63%
[5 empty] | 67.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66234.0965 | 1069457.0678 | 67.72 | 91.63%
[5 empty] | 67.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66245.9049 | 1069647.7345 | 67.73 | 91.63%
[5 empty] | 67.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66257.7134 | 1069838.4011 | 67.74 | 91.63%
[5 empty] | 67.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66269.5218 | 1070029.0678 | 67.75 | 91.63%
[5 empty] | 67.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66281.3303 | 1070219.7345 | 67.76 | 91.63%
[5 empty] | 67.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66293.1387 | 1070410.4011 | 67.77 | 91.63%
[5 empty] | 67.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66304.9472 | 1070601.0678 | 67.78 | 91.63%
[5 empty] | 67.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66316.7556 | 1070791.7345 | 67.79 | 91.63%
[5 empty] | 67.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66328.5641 | 1070982.4011 | 67.8 | 91.63%
[5 empty] | 67.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66340.3725 | 1071173.0678 | 67.81 | 91.63%
[5 empty] | 67.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66352.181 | 1071363.7345 | 67.82 | 91.63%
[5 empty] | 67.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66363.9895 | 1071554.4011 | 67.83 | 91.63%
[5 empty] | 67.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66375.7979 | 1071745.0678 | 67.84 | 91.63%
[5 empty] | 67.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66387.6064 | 1071935.7345 | 67.85 | 91.63%
[5 empty] | 67.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66399.4148 | 1072126.4011 | 67.86 | 91.63%
[5 empty] | 67.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66411.2233 | 1072317.0678 | 67.87 | 91.63%
[5 empty] | 67.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66423.0317 | 1072507.7345 | 67.88 | 91.63%
[5 empty] | 67.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66434.8402 | 1072698.4011 | 67.89 | 91.63%
[5 empty] | 67.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66446.6486 | 1072889.0678 | 67.9 | 91.63%
[5 empty] | 67.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66458.4571 | 1073079.7345 | 67.91 | 91.63%
[5 empty] | 67.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66470.2655 | 1073270.4011 | 67.92 | 91.63%
[5 empty] | 67.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66482.074 | 1073461.0678 | 67.93 | 91.63%
[5 empty] | 67.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66493.8824 | 1073651.7345 | 67.94 | 91.63%
[5 empty] | 67.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66505.6909 | 1073842.4011 | 67.95 | 91.63%
[5 empty] | 67.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66517.4994 | 1074033.0678 | 67.96 | 91.63%
[5 empty] | 67.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66529.3078 | 1074223.7345 | 67.97 | 91.63%
[5 empty] | 67.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66541.1163 | 1074414.4011 | 67.98 | 91.63%
[5 empty] | 67.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66552.9247 | 1074605.0678 | 67.99 | 91.63%
[5 empty] | 68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66564.7332 | 1074795.7345 | 68 | 91.63%
[5 empty] | 68.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66576.5416 | 1074986.4011 | 68.01 | 91.63%
[5 empty] | 68.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66588.3501 | 1075177.0678 | 68.02 | 91.63%
[5 empty] | 68.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66600.1585 | 1075367.7345 | 68.03 | 91.63%
[5 empty] | 68.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66611.967 | 1075558.4011 | 68.04 | 91.63%
[5 empty] | 68.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66623.7754 | 1075749.0678 | 68.05 | 91.63%
[5 empty] | 68.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66635.5839 | 1075939.7345 | 68.06 | 91.63%
[5 empty] | 68.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66647.3923 | 1076130.4011 | 68.07 | 91.63%
[5 empty] | 68.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66659.2008 | 1076321.0678 | 68.08 | 91.63%
[5 empty] | 68.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66671.0093 | 1076511.7345 | 68.09 | 91.63%
[5 empty] | 68.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66682.8177 | 1076702.4011 | 68.1 | 91.63%
[5 empty] | 68.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66694.6262 | 1076893.0678 | 68.11 | 91.63%
[5 empty] | 68.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66706.4346 | 1077083.7345 | 68.12 | 91.63%
[5 empty] | 68.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66718.2431 | 1077274.4011 | 68.13 | 91.63%
[5 empty] | 68.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66730.0515 | 1077465.0678 | 68.14 | 91.63%
[5 empty] | 68.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66741.86 | 1077655.7345 | 68.15 | 91.63%
[5 empty] | 68.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66753.6684 | 1077846.4011 | 68.16 | 91.63%
[5 empty] | 68.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66765.4769 | 1078037.0678 | 68.17 | 91.63%
[5 empty] | 68.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66777.2853 | 1078227.7345 | 68.18 | 91.63%
[5 empty] | 68.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66789.0938 | 1078418.4011 | 68.19 | 91.63%
[5 empty] | 68.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66800.9022 | 1078609.0678 | 68.2 | 91.63%
[5 empty] | 68.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66812.7107 | 1078799.7345 | 68.21 | 91.63%
[5 empty] | 68.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66824.5192 | 1078990.4011 | 68.22 | 91.63%
[5 empty] | 68.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66836.3276 | 1079181.0678 | 68.23 | 91.63%
[5 empty] | 68.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66848.1361 | 1079371.7345 | 68.24 | 91.63%
[5 empty] | 68.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66859.9445 | 1079562.4011 | 68.25 | 91.63%
[5 empty] | 68.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66871.753 | 1079753.0678 | 68.26 | 91.63%
[5 empty] | 68.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66883.5614 | 1079943.7345 | 68.27 | 91.63%
[5 empty] | 68.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66895.3699 | 1080134.4011 | 68.28 | 91.63%
[5 empty] | 68.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66907.1783 | 1080325.0678 | 68.29 | 91.63%
[5 empty] | 68.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66918.9868 | 1080515.7345 | 68.3 | 91.63%
[5 empty] | 68.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66930.7952 | 1080706.4011 | 68.31 | 91.63%
[5 empty] | 68.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66942.6037 | 1080897.0678 | 68.32 | 91.63%
[5 empty] | 68.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66954.4121 | 1081087.7345 | 68.33 | 91.63%
[5 empty] | 68.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66966.2206 | 1081278.4011 | 68.34 | 91.63%
[5 empty] | 68.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66978.0291 | 1081469.0678 | 68.35 | 91.63%
[5 empty] | 68.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 66989.8375 | 1081659.7345 | 68.36 | 91.63%
[5 empty] | 68.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67001.646 | 1081850.4011 | 68.37 | 91.63%
[5 empty] | 68.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67013.4544 | 1082041.0678 | 68.38 | 91.63%
[5 empty] | 68.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67025.2629 | 1082231.7345 | 68.39 | 91.63%
[5 empty] | 68.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67037.0713 | 1082422.4011 | 68.4 | 91.63%
[5 empty] | 68.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67048.8798 | 1082613.0678 | 68.41 | 91.63%
[5 empty] | 68.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67060.6882 | 1082803.7345 | 68.42 | 91.63%
[5 empty] | 68.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67072.4967 | 1082994.4011 | 68.43 | 91.63%
[5 empty] | 68.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67084.3051 | 1083185.0678 | 68.44 | 91.63%
[5 empty] | 68.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67096.1136 | 1083375.7345 | 68.45 | 91.63%
[5 empty] | 68.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67107.922 | 1083566.4011 | 68.46 | 91.63%
[5 empty] | 68.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67119.7305 | 1083757.0678 | 68.47 | 91.63%
[5 empty] | 68.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67131.539 | 1083947.7345 | 68.48 | 91.63%
[5 empty] | 68.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67143.3474 | 1084138.4011 | 68.49 | 91.63%
[5 empty] | 68.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67155.1559 | 1084329.0678 | 68.5 | 91.63%
[5 empty] | 68.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67166.9643 | 1084519.7345 | 68.51 | 91.63%
[5 empty] | 68.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67178.7728 | 1084710.4011 | 68.52 | 91.63%
[5 empty] | 68.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67190.5812 | 1084901.0678 | 68.53 | 91.63%
[5 empty] | 68.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67202.3897 | 1085091.7345 | 68.54 | 91.63%
[5 empty] | 68.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67214.1981 | 1085282.4011 | 68.55 | 91.63%
[5 empty] | 68.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67226.0066 | 1085473.0678 | 68.56 | 91.63%
[5 empty] | 68.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67237.815 | 1085663.7345 | 68.57 | 91.63%
[5 empty] | 68.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67249.6235 | 1085854.4011 | 68.58 | 91.63%
[5 empty] | 68.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67261.4319 | 1086045.0678 | 68.59 | 91.63%
[5 empty] | 68.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67273.2404 | 1086235.7345 | 68.6 | 91.63%
[5 empty] | 68.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67285.0489 | 1086426.4011 | 68.61 | 91.63%
[5 empty] | 68.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67296.8573 | 1086617.0678 | 68.62 | 91.63%
[5 empty] | 68.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67308.6658 | 1086807.7345 | 68.63 | 91.63%
[5 empty] | 68.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67320.4742 | 1086998.4011 | 68.64 | 91.63%
[5 empty] | 68.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67332.2827 | 1087189.0678 | 68.65 | 91.63%
[5 empty] | 68.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67344.0911 | 1087379.7345 | 68.66 | 91.63%
[5 empty] | 68.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67355.8996 | 1087570.4011 | 68.67 | 91.63%
[5 empty] | 68.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67367.708 | 1087761.0678 | 68.68 | 91.63%
[5 empty] | 68.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67379.5165 | 1087951.7345 | 68.69 | 91.63%
[5 empty] | 68.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67391.3249 | 1088142.4011 | 68.7 | 91.63%
[5 empty] | 68.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67403.1334 | 1088333.0678 | 68.71 | 91.63%
[5 empty] | 68.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67414.9418 | 1088523.7345 | 68.72 | 91.63%
[5 empty] | 68.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67426.7503 | 1088714.4011 | 68.73 | 91.63%
[5 empty] | 68.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67438.5588 | 1088905.0678 | 68.74 | 91.63%
[5 empty] | 68.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67450.3672 | 1089095.7345 | 68.75 | 91.63%
[5 empty] | 68.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67462.1757 | 1089286.4011 | 68.76 | 91.63%
[5 empty] | 68.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67473.9841 | 1089477.0678 | 68.77 | 91.63%
[5 empty] | 68.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67485.7926 | 1089667.7345 | 68.78 | 91.63%
[5 empty] | 68.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67497.601 | 1089858.4011 | 68.79 | 91.63%
[5 empty] | 68.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67509.4095 | 1090049.0678 | 68.8 | 91.63%
[5 empty] | 68.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67521.2179 | 1090239.7345 | 68.81 | 91.63%
[5 empty] | 68.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67533.0264 | 1090430.4011 | 68.82 | 91.63%
[5 empty] | 68.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67544.8348 | 1090621.0678 | 68.83 | 91.63%
[5 empty] | 68.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67556.6433 | 1090811.7345 | 68.84 | 91.63%
[5 empty] | 68.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67568.4517 | 1091002.4011 | 68.85 | 91.63%
[5 empty] | 68.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67580.2602 | 1091193.0678 | 68.86 | 91.63%
[5 empty] | 68.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67592.0687 | 1091383.7345 | 68.87 | 91.63%
[5 empty] | 68.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67603.8771 | 1091574.4011 | 68.88 | 91.63%
[5 empty] | 68.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67615.6856 | 1091765.0678 | 68.89 | 91.63%
[5 empty] | 68.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67627.494 | 1091955.7345 | 68.9 | 91.63%
[5 empty] | 68.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67639.3025 | 1092146.4011 | 68.91 | 91.63%
[5 empty] | 68.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67651.1109 | 1092337.0678 | 68.92 | 91.63%
[5 empty] | 68.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67662.9194 | 1092527.7345 | 68.93 | 91.63%
[5 empty] | 68.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67674.7278 | 1092718.4011 | 68.94 | 91.63%
[5 empty] | 68.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67686.5363 | 1092909.0678 | 68.95 | 91.63%
[5 empty] | 68.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67698.3447 | 1093099.7345 | 68.96 | 91.63%
[5 empty] | 68.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67710.1532 | 1093290.4011 | 68.97 | 91.63%
[5 empty] | 68.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67721.9616 | 1093481.0678 | 68.98 | 91.63%
[5 empty] | 68.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67733.7701 | 1093671.7345 | 68.99 | 91.63%
[5 empty] | 69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67745.5786 | 1093862.4011 | 69 | 91.63%
[5 empty] | 69.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67757.387 | 1094053.0678 | 69.01 | 91.63%
[5 empty] | 69.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67769.1955 | 1094243.7345 | 69.02 | 91.63%
[5 empty] | 69.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67781.0039 | 1094434.4011 | 69.03 | 91.63%
[5 empty] | 69.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67792.8124 | 1094625.0678 | 69.04 | 91.63%
[5 empty] | 69.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67804.6208 | 1094815.7345 | 69.05 | 91.63%
[5 empty] | 69.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67816.4293 | 1095006.4011 | 69.06 | 91.63%
[5 empty] | 69.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67828.2377 | 1095197.0678 | 69.07 | 91.63%
[5 empty] | 69.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67840.0462 | 1095387.7345 | 69.08 | 91.63%
[5 empty] | 69.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67851.8546 | 1095578.4011 | 69.09 | 91.63%
[5 empty] | 69.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67863.6631 | 1095769.0678 | 69.1 | 91.63%
[5 empty] | 69.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67875.4715 | 1095959.7345 | 69.11 | 91.63%
[5 empty] | 69.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67887.28 | 1096150.4011 | 69.12 | 91.63%
[5 empty] | 69.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67899.0885 | 1096341.0678 | 69.13 | 91.63%
[5 empty] | 69.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67910.8969 | 1096531.7345 | 69.14 | 91.63%
[5 empty] | 69.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67922.7054 | 1096722.4011 | 69.15 | 91.63%
[5 empty] | 69.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67934.5138 | 1096913.0678 | 69.16 | 91.63%
[5 empty] | 69.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67946.3223 | 1097103.7345 | 69.17 | 91.63%
[5 empty] | 69.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67958.1307 | 1097294.4011 | 69.18 | 91.63%
[5 empty] | 69.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67969.9392 | 1097485.0678 | 69.19 | 91.63%
[5 empty] | 69.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67981.7476 | 1097675.7345 | 69.2 | 91.63%
[5 empty] | 69.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 67993.5561 | 1097866.4011 | 69.21 | 91.63%
[5 empty] | 69.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68005.3645 | 1098057.0678 | 69.22 | 91.63%
[5 empty] | 69.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68017.173 | 1098247.7345 | 69.23 | 91.63%
[5 empty] | 69.24 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68028.9814 | 1098438.4011 | 69.24 | 91.63%
[5 empty] | 69.25 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68040.7899 | 1098629.0678 | 69.25 | 91.63%
[5 empty] | 69.26 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68052.5983 | 1098819.7345 | 69.26 | 91.63%
[5 empty] | 69.27 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68064.4068 | 1099010.4011 | 69.27 | 91.63%
[5 empty] | 69.28 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68076.2153 | 1099201.0678 | 69.28 | 91.63%
[5 empty] | 69.29 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68088.0237 | 1099391.7345 | 69.29 | 91.63%
[5 empty] | 69.3 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68099.8322 | 1099582.4011 | 69.3 | 91.63%
[5 empty] | 69.31 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68111.6406 | 1099773.0678 | 69.31 | 91.63%
[5 empty] | 69.32 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68123.4491 | 1099963.7345 | 69.32 | 91.63%
[5 empty] | 69.33 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68135.2575 | 1100154.4011 | 69.33 | 91.63%
[5 empty] | 69.34 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68147.066 | 1100345.0678 | 69.34 | 91.63%
[5 empty] | 69.35 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68158.8744 | 1100535.7345 | 69.35 | 91.63%
[5 empty] | 69.36 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68170.6829 | 1100726.4011 | 69.36 | 91.63%
[5 empty] | 69.37 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68182.4913 | 1100917.0678 | 69.37 | 91.63%
[5 empty] | 69.38 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68194.2998 | 1101107.7345 | 69.38 | 91.63%
[5 empty] | 69.39 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68206.1082 | 1101298.4011 | 69.39 | 91.63%
[5 empty] | 69.4 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68217.9167 | 1101489.0678 | 69.4 | 91.63%
[5 empty] | 69.41 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68229.7252 | 1101679.7345 | 69.41 | 91.63%
[5 empty] | 69.42 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68241.5336 | 1101870.4011 | 69.42 | 91.63%
[5 empty] | 69.43 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68253.3421 | 1102061.0678 | 69.43 | 91.63%
[5 empty] | 69.44 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68265.1505 | 1102251.7345 | 69.44 | 91.63%
[5 empty] | 69.45 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68276.959 | 1102442.4011 | 69.45 | 91.63%
[5 empty] | 69.46 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68288.7674 | 1102633.0678 | 69.46 | 91.63%
[5 empty] | 69.47 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68300.5759 | 1102823.7345 | 69.47 | 91.63%
[5 empty] | 69.48 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68312.3843 | 1103014.4011 | 69.48 | 91.63%
[5 empty] | 69.49 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68324.1928 | 1103205.0678 | 69.49 | 91.63%
[5 empty] | 69.5 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68336.0012 | 1103395.7345 | 69.5 | 91.63%
[5 empty] | 69.51 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68347.8097 | 1103586.4011 | 69.51 | 91.63%
[5 empty] | 69.52 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68359.6181 | 1103777.0678 | 69.52 | 91.63%
[5 empty] | 69.53 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68371.4266 | 1103967.7345 | 69.53 | 91.63%
[5 empty] | 69.54 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68383.2351 | 1104158.4011 | 69.54 | 91.63%
[5 empty] | 69.55 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68395.0435 | 1104349.0678 | 69.55 | 91.63%
[5 empty] | 69.56 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68406.852 | 1104539.7345 | 69.56 | 91.63%
[5 empty] | 69.57 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68418.6604 | 1104730.4011 | 69.57 | 91.63%
[5 empty] | 69.58 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68430.4689 | 1104921.0678 | 69.58 | 91.63%
[5 empty] | 69.59 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68442.2773 | 1105111.7345 | 69.59 | 91.63%
[5 empty] | 69.6 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68454.0858 | 1105302.4011 | 69.6 | 91.63%
[5 empty] | 69.61 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68465.8942 | 1105493.0678 | 69.61 | 91.63%
[5 empty] | 69.62 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68477.7027 | 1105683.7345 | 69.62 | 91.63%
[5 empty] | 69.63 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68489.5111 | 1105874.4011 | 69.63 | 91.63%
[5 empty] | 69.64 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68501.3196 | 1106065.0678 | 69.64 | 91.63%
[5 empty] | 69.65 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68513.128 | 1106255.7345 | 69.65 | 91.63%
[5 empty] | 69.66 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68524.9365 | 1106446.4011 | 69.66 | 91.63%
[5 empty] | 69.67 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68536.745 | 1106637.0678 | 69.67 | 91.63%
[5 empty] | 69.68 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68548.5534 | 1106827.7345 | 69.68 | 91.63%
[5 empty] | 69.69 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68560.3619 | 1107018.4011 | 69.69 | 91.63%
[5 empty] | 69.7 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68572.1703 | 1107209.0678 | 69.7 | 91.63%
[5 empty] | 69.71 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68583.9788 | 1107399.7345 | 69.71 | 91.63%
[5 empty] | 69.72 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68595.7872 | 1107590.4011 | 69.72 | 91.63%
[5 empty] | 69.73 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68607.5957 | 1107781.0678 | 69.73 | 91.63%
[5 empty] | 69.74 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68619.4041 | 1107971.7345 | 69.74 | 91.63%
[5 empty] | 69.75 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68631.2126 | 1108162.4011 | 69.75 | 91.63%
[5 empty] | 69.76 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68643.021 | 1108353.0678 | 69.76 | 91.63%
[5 empty] | 69.77 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68654.8295 | 1108543.7345 | 69.77 | 91.63%
[5 empty] | 69.78 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68666.6379 | 1108734.4011 | 69.78 | 91.63%
[5 empty] | 69.79 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68678.4464 | 1108925.0678 | 69.79 | 91.63%
[5 empty] | 69.8 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68690.2549 | 1109115.7345 | 69.8 | 91.63%
[5 empty] | 69.81 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68702.0633 | 1109306.4011 | 69.81 | 91.63%
[5 empty] | 69.82 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68713.8718 | 1109497.0678 | 69.82 | 91.63%
[5 empty] | 69.83 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68725.6802 | 1109687.7345 | 69.83 | 91.63%
[5 empty] | 69.84 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68737.4887 | 1109878.4011 | 69.84 | 91.63%
[5 empty] | 69.85 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68749.2971 | 1110069.0678 | 69.85 | 91.63%
[5 empty] | 69.86 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68761.1056 | 1110259.7345 | 69.86 | 91.63%
[5 empty] | 69.87 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68772.914 | 1110450.4011 | 69.87 | 91.63%
[5 empty] | 69.88 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68784.7225 | 1110641.0678 | 69.88 | 91.63%
[5 empty] | 69.89 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68796.5309 | 1110831.7345 | 69.89 | 91.63%
[5 empty] | 69.9 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68808.3394 | 1111022.4011 | 69.9 | 91.63%
[5 empty] | 69.91 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68820.1478 | 1111213.0678 | 69.91 | 91.63%
[5 empty] | 69.92 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68831.9563 | 1111403.7345 | 69.92 | 91.63%
[5 empty] | 69.93 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68843.7648 | 1111594.4011 | 69.93 | 91.63%
[5 empty] | 69.94 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68855.5732 | 1111785.0678 | 69.94 | 91.63%
[5 empty] | 69.95 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68867.3817 | 1111975.7345 | 69.95 | 91.63%
[5 empty] | 69.96 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68879.1901 | 1112166.4011 | 69.96 | 91.63%
[5 empty] | 69.97 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68890.9986 | 1112357.0678 | 69.97 | 91.63%
[5 empty] | 69.98 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68902.807 | 1112547.7345 | 69.98 | 91.63%
[5 empty] | 69.99 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68914.6155 | 1112738.4011 | 69.99 | 91.63%
[5 empty] | 70 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68926.4239 | 1112929.0678 | 70 | 91.63%
[5 empty] | 70.01 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68938.2324 | 1113119.7345 | 70.01 | 91.63%
[5 empty] | 70.02 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68950.0408 | 1113310.4011 | 70.02 | 91.63%
[5 empty] | 70.03 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68961.8493 | 1113501.0678 | 70.03 | 91.63%
[5 empty] | 70.04 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68973.6577 | 1113691.7345 | 70.04 | 91.63%
[5 empty] | 70.05 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68985.4662 | 1113882.4011 | 70.05 | 91.63%
[5 empty] | 70.06 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 68997.2747 | 1114073.0678 | 70.06 | 91.63%
[5 empty] | 70.07 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69009.0831 | 1114263.7345 | 70.07 | 91.63%
[5 empty] | 70.08 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69020.8916 | 1114454.4011 | 70.08 | 91.63%
[5 empty] | 70.09 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69032.7 | 1114645.0678 | 70.09 | 91.63%
[5 empty] | 70.1 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69044.5085 | 1114835.7345 | 70.1 | 91.63%
[5 empty] | 70.11 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69056.3169 | 1115026.4011 | 70.11 | 91.63%
[5 empty] | 70.12 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69068.1254 | 1115217.0678 | 70.12 | 91.63%
[5 empty] | 70.13 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69079.9338 | 1115407.7345 | 70.13 | 91.63%
[5 empty] | 70.14 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69091.7423 | 1115598.4011 | 70.14 | 91.63%
[5 empty] | 70.15 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69103.5507 | 1115789.0678 | 70.15 | 91.63%
[5 empty] | 70.16 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69115.3592 | 1115979.7345 | 70.16 | 91.63%
[5 empty] | 70.17 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69127.1676 | 1116170.4011 | 70.17 | 91.63%
[5 empty] | 70.18 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69138.9761 | 1116361.0678 | 70.18 | 91.63%
[5 empty] | 70.19 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69150.7846 | 1116551.7345 | 70.19 | 91.63%
[5 empty] | 70.2 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69162.593 | 1116742.4011 | 70.2 | 91.63%
[5 empty] | 70.21 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69174.4015 | 1116933.0678 | 70.21 | 91.63%
[5 empty] | 70.22 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69186.2099 | 1117123.7345 | 70.22 | 91.63%
[5 empty] | 70.23 | 1144000 | 660 | 100% | 100% | 100% | 1 | 54600 | 243540 | 845860 | 1144000 | 69198.0184 | 1117314.4011 | 70.23 | 91.63%

## RadCompList (hidden)
Column Radiators
| Sq Ft Radiation Per Section | Columns |  |  |  |  | FALSE |  |  |  | Rad Types | ft3/edr
Rad Type | Column | 1 | 2 | 3 | 4 | 5 | 1 |  |  |  | Column | 0.025
Column | 13 | - | - | - | - | 3 | 2 |  |  |  | Tube | 0.013
Column | 16 | - | - | - | - | 3.75 | 3 |  |  |  | Cast Rad/Conv | 0.0003
Column | 18 | - | - | 2.25 | 3 | 4.25 | 4 |  |  |  | Copper Cabinet | 0.0003
Column | 20 | 1.5 | 2 | - | - | 5 | 5
Column | 22 | - | - | 3 | 4 | - | 6
Column | 23 | 1.66 | 2.33 | - | - | - | 7
Column | 26 | 2 | 2.66 | 3.75 | 5 | - | 8 |  |  |  |  | Sections list
Column | 32 | 2.5 | 3.33 | 4.5 | 6.5 | - | 9 |  |  |  |  | 1
Column | 38 | 3 | 4 | 5 | 8 | - | 10 |  |  |  |  | 2
Column | 45 | - | 5 | 6 | 10 | - | 11 |  |  |  |  | 3
|  | Columns 1: Tubes |  |  |  |  | 4
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 |  |  | 5
Tube | 13 | , | - | - | - | - | - | 2.625 | 2 |  |  | 6
Tube | 16.5 | - | - | - | - | - | - | 3.5 | 3 |  |  | 7
Tube | 20 | - | - | 1.75 | 2.25 | 2.66 | 3 | 4.25 | 4 |  |  | 8
Tube | 23 | - | - | 2 | 2.5 | 3 | 3.5 | - | 5 |  |  | 9
Tube | 26 | - | - | 2.11 | 2.75 | 3.5 | 4 | - | 6 |  |  | 10
Tube | 32 | - | - | 3 | 3.5 | 4.33 | 5 | - | 7
Tube | 37 | - | - | 3.5 | 4.125 | 5 | 6 | - | 8
Width
|  | 5 | 7.5
Cast Rad/Conv | 20 | Tubes 1: 2.25; Tubes 2: 3.4
10-1/2 X 20-1/2
|  | 10-1/2 X 20-1/2 |  | 1
|  | 18 | #N/A | 31
Height
| Cabinet Depth | Cabinet Length | Dimensions | 18 | 20 | 24 | 26 | 32 | 38
Copper Cabinet | 4-1/2" | 20-1/2" | 4-1/2 X 20-1/2 | 10.4 | 11.3 | 13.1 | 13.4 | 14 | 14.6
Copper Cabinet | 4-1/2" | 24-1/2" | 4-1/2 X 24-1/2 | 12.8 | 13.9 | 16.1 | 16.4 | 17.2 | 18
Copper Cabinet | 4-1/2" | 28-1/2" | 4-1/2 X 28-1/2 | 15.2 | 16.5 | 19.2 | 19.5 | 20.4 | 21.3
Copper Cabinet | 4-1/2" | 32-1/2" | 4-1/2 X 32-1/2 | 17.6 | 19.1 | 22.2 | 22.5 | 23.6 | 24.6
Copper Cabinet | 4-1/2" | 36-1/2" | 4-1/2 X 36-1/2 | 19.7 | 21.7 | 25.2 | 25.6 | 26.8 | 28
Copper Cabinet | 4-1/2" | 40-1/2" | 4-1/2 X 40-1/2 | 22.3 | 24.3 | 28.2 | 28.6 | 30 | 31.3
Copper Cabinet | 4-1/2" | 44-1/2" | 4-1/2 X 44-1/2 | 24.7 | 26.9 | 31.2 | 31.7 | 33.2 | 34.7
Copper Cabinet | 4-1/2" | 48-1/2" | 4-1/2 X 48-1/2 | 27.1 | 29.5 | 34.2 | 34.7 | 36.4 | 38
Copper Cabinet | 4-1/2" | 56-1/2" | 4-1/2 X 56-1/2 | 31.9 | 34.7 | 40.2 | 40.8 | 42.8 | 44.7
Copper Cabinet | 4-1/2" | 64-1/2" | 4-1/2 X 64-1/2 | 36.6 | 39.9 | 46.2 | 46.9 | 49.2 | 51.7
Copper Cabinet | 6-1/2" | 20-1/2" | 6-1/2 X 20-1/2 | 15.3 | 16.3 | 18.4 | 18.8 | 19.6 | 20.6
Copper Cabinet | 6-1/2" | 24-1/2" | 6-1/2 X 24-1/2 | 18.8 | 20.1 | 22.6 | 23.1 | 24.1 | 25.3
Copper Cabinet | 6-1/2" | 28-1/2" | 6-1/2 X 28-1/2 | 22.3 | 23.8 | 26.9 | 27.4 | 28.6 | 30.1
Copper Cabinet | 6-1/2" | 32-1/2" | 6-1/2 X 32-1/2 | 25.8 | 27.6 | 31.1 | 31.7 | 33.2 | 34.8
Copper Cabinet | 6-1/2" | 36-1/2" | 6-1/2 X 36-1/2 | 29.3 | 31.3 | 35.4 | 36 | 37.7 | 39.6
Copper Cabinet | 6-1/2" | 40-1/2" | 6-1/2 X 40-1/2 | 32.8 | 35.1 | 39.6 | 40.3 | 42.2 | 44.3
Copper Cabinet | 6-1/2" | 44-1/2" | 6-1/2 X 44-1/2 | 36.3 | 38.9 | 43.8 | 44.6 | 48.7 | 49.9 | Cabinet Depth
Copper Cabinet | 6-1/2" | 48-1/2" | 6-1/2 X 48-1/2 | 39.8 | 42.6 | 48.1 | 48.9 | 51.2 | 53.8 | 4-1/2"
Copper Cabinet | 6-1/2" | 56-1/2" | 6-1/2 X 56-1/2 | 46.8 | 50.1 | 56.6 | 57.5 | 60.6 | 63.3 | 6-1/2"
Copper Cabinet | 6-1/2" | 64-1/2" | 6-1/2 X 64-1/2 | 53.9 | 57.7 | 65 | 66.2 | 69.3 | 72.7 | 8-1/2"
Copper Cabinet | 8-1/2" | 20-1/2" | 8-1/2 X 20-1/2 | 18.7 | 20 | 22.5 | 23 | 24.4 | 25.8 | 10-1/2"
Copper Cabinet | 8-1/2" | 24-1/2" | 8-1/2 X 24-1/2 | 22.9 | 24.5 | 27.7 | 28.8 | 30 | 3.7
Copper Cabinet | 8-1/2" | 28-1/2" | 8-1/2 X 28-1/2 | 27.2 | 20.1 | 32.8 | 33.5 | 35.6 | 37.7
Copper Cabinet | 8-1/2" | 32-1/2" | 8-1/2 X 32-1/2 | 31.5 | 33.7 | 38 | 38.8 | 41.2 | 43.6
Copper Cabinet | 8-1/2" | 36-1/2" | 8-1/2 X 36-1/2 | 35.8 | 38.3 | 43.2 | 44.1 | 46.8 | 49.5
Copper Cabinet | 8-1/2" | 40-1/2" | 8-1/2 X 40-1/2 | 40.1 | 42.9 | 48.3 | 49.4 | 52.4 | 55.5
Copper Cabinet | 8-1/2" | 44-1/2" | 8-1/2 X 44-1/2 | 44.3 | 47.4 | 53.3 | 54.6 | 58 | 61.4
Copper Cabinet | 8-1/2" | 48-1/2" | 8-1/2 X 48-1/2 | 48.6 | 52 | 58.7 | 59.9 | 63.6 | 67.3
Copper Cabinet | 8-1/2" | 56-1/2" | 8-1/2 X 56-1/2 | 57.2 | 61.2 | 69 | 70.5 | 74.8 | 79.2
Copper Cabinet | 8-1/2" | 64-1/2" | 8-1/2 X 64-1/2 | 65.7 | 70.3 | 79.4 | 81 | 86 | 91
Copper Cabinet | 10-1/2" | 20-1/2" | 10-1/2 X 20-1/2 | 20.4 | 22 | 25 | 25.7 | 27.4 | 29.3
Copper Cabinet | 10-1/2" | 24-1/2" | 10-1/2 X 24-1/2 | 25.2 | 27.1 | 30.9 | 31.7 | 33.8 | 36.2
Copper Cabinet | 10-1/2" | 28-1/2" | 10-1/2 X 28-1/2 | 30 | 32.3 | 36.8 | 37.7 | 40.2 | 43.1
Copper Cabinet | 10-1/2" | 32-1/2" | 10-1/2 X 32-1/2 | 34.8 | 37.4 | 42.6 | 43.7 | 46.6 | 50
Copper Cabinet | 10-1/2" | 36-1/2" | 10-1/2 X 36-1/2 | 39.6 | 42.6 | 48.5 | 49.8 | 53.1 | 56.9
Copper Cabinet | 10-1/2" | 40-1/2" | 10-1/2 X 40-1/2 | 44.4 | 47.7 | 54.4 | 55.8 | 59.5 | 63.7
Copper Cabinet | 10-1/2" | 44-1/2" | 10-1/2 X 44-1/2 | 49.2 | 52.9 | 60.3 | 61.8 | 65.9 | 70.6
Copper Cabinet | 10-1/2" | 48-1/2" | 10-1/2 X 48-1/2 | 53.9 | 58 | 66.1 | 67.8 | 72.3 | 77.5
Copper Cabinet | 10-1/2" | 56-1/2" | 10-1/2 X 56-1/2 | 63.5 | 68.3 | 77.9 | 79.9 | 85.2 | 91.2
Copper Cabinet | 10-1/2" | 64-1/2" | 10-1/2 X 64-1/2 | 73.1 | 78.6 | 89.6 | 91.9 | 98 | 105

## VentList (hidden)
MAIN VENTS | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM |  |  |  |  | Vent Lines
- | 0 | 0 | 0 | Equivalent Orifice ID (in) | Equivalent Orifice ID (in) | Equivalent Orifice ID (in) | Equivalent Orifice (in)
Open 1/8" Steel Pipe | 1.2 | 2 | 2.5 | 0.032313 | 0.038081 | 0.038867 | 0.03642
Open 1/2" Steel Pipe | 2.6 | 3.4 | 4.8 | 0.070012 | 0.064738 | 0.074624 | 0.069791 | A
Open 3/4" Steel Pipe | Note 1 | Note 1 | 9.5 | #VALUE! | #VALUE! | 0.14769 | #VALUE! | B
Open 1" Steel Pipe | Note 1 | Note 1 | 11 | #VALUE! | #VALUE! | 0.17101 | #VALUE! | C
American Radiator Co. Ideal Vac-Vent #822 - (obsolete) | 0.1 | 0.158 | 0.2 | 0.0026928 | 0.0030084 | 0.0031093 | 0.0029368 | D
Barnes & Jones QV 1 (obsolete) | 0.583 | 1.58 | 2 | 0.015699 | 0.030084 | 0.031093 | 0.025625 | E
Barnes & Jones Ventrite #75-- (obsolete) | 0.116 | 0.175 | 0.225 | 0.0031236 | 0.0033321 | 0.003498 | 0.0033179 | F
Detroit Controls #841 Quick Vent (obsolete) | 0.333 | 0.55 | 0.7 | 0.0089669 | 0.010472 | 0.010883 | 0.010107 | G
Dole #5 Quick Vent | 0.066 | 0.116 | 0.15 | 0.0017772 | 0.0022087 | 0.002332 | 0.002106 | H
Gorton #1 | 0.33 | 0.54 | 0.7 | 0.0088861 | 0.010282 | 0.010883 | 0.010017 | I
Gorton #2 | 1.1 | 1.75 | 2.2 | 0.02962 | 0.033321 | 0.034203 | 0.032381 | J
Hoffman #4 | 0.06 | 0.11 | 0.13 | 0.0016157 | 0.0020945 | 0.0020211 | 0.0019104 | K
Hoffman #4A | 0.133 | 0.216 | 0.266 | 0.0035814 | 0.0041128 | 0.0041354 | 0.0039432 | L
Hoffman #6 Vacuum Valve (obsolete) | 0.033 | 0.083 | 0.108 | 0.00088861 | 0.0015804 | 0.001679 | 0.0013827 | M
Hoffman #10 Vapor Vent - (obsolete) | 2.033 | 2.5 | 3.7 | 0.054744 | 0.047602 | 0.057523 | 0.053289 | N
Hoffman #11 Vapor Vacuum Vent (obsolete) | 1 | 2.41 | 3.33 | 0.026928 | 0.045888 | 0.05177 | 0.041529 | O
Hoffman #15 Vacuum Vent (obsolete) Differential Loop | 1.283 | 2.75 | 3.416 | 0.034548 | 0.052362 | 0.053107 | 0.046672 | Single Pipe
Hoffman #16 Vacuum Valve (obsolete) | 0.066 | 0.116 | 0.15 | 0.0017772 | 0.0022087 | 0.002332 | 0.002106
Hoffman #16A Vacuum Valve (obsolete) | 0.1 | 0.183 | 0.241 | 0.0026928 | 0.0034844 | 0.0037467 | 0.003308
Hoffman #75 | 0.5 | 0.75 | 0.96 | 0.013464 | 0.014281 | 0.014925 | 0.014223
Hoffman #76 Vacuum Valve | 0.383 | 0.666 | 0.833 | 0.010313 | 0.012681 | 0.01295 | 0.011982
Ideal Htg. Co. "Wafer Style" - - (obsolete) | 0.09 | 0.13 | 0.166 | 0.0024235 | 0.0024753 | 0.0025807 | 0.0024932
Maid-O-Mist #1 Straight Pattern | 0.333 | 0.59 | 0.766 | 0.0089669 | 0.011234 | 0.011909 | 0.010703
Marsh #55 | 0.01 | 0.021 | 0.033 | 0.00026928 | 0.00039985 | 0.00051304 | 0.00039406
Mouat Cast Iron 'Bullet' Style (obsolete) | 0.53 | 0.91 | 1.11 | 0.014272 | 0.017327 | 0.017257 | 0.016285
Mouat Tri Tube (obsolete) | 1.16 | 1.8 | 2 | 0.031236 | 0.034273 | 0.031093 | 0.032201
Squires Co. Mouat Series Cast Iron Bullet Style (obsolete) | 0.53 | 0.91 | 1.11 | 0.014272 | 0.017327 | 0.017257 | 0.016285
Trane Cast Iron Bullet Style (obsolete) | 0.78 | 1.33 | 1.7 | 0.021004 | 0.025324 | 0.026429 | 0.024252
Vent Rite #35 | 0.11 | 0.2 | 0.25 | 0.002962 | 0.0038081 | 0.0038867 | 0.0035523
Vent Rite #75 (Barnes & Jones Issue) (obsolete) | 0.116 | 0.175 | 0.225 | 0.0031236 | 0.0033321 | 0.003498 | 0.0033179
Vent Rite #77 | 0.19 | 0.31 | 0.4 | 0.0051162 | 0.0059026 | 0.0062187 | 0.0057458
Watts SVS-3 | 0.07 | 0.116 | 0.15 | 0.0018849 | 0.0022087 | 0.002332 | 0.0021419
Warco #3(obsolete) | 0.05 | 0.108 | 0.15 | 0.0013464 | 0.0020564 | 0.002332 | 0.0019116
Warco #87 (obsolete) | 0.108 | 0.175 | 0.233 | 0.0029082 | 0.0033321 | 0.0036224 | 0.0032876
Warren Webster #40-15 Vent Trap (obsolete) | 1.166 | 1.866 | 2.366 | 0.031398 | 0.03553 | 0.036783 | 0.03457
Radiator Vents | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM | #VALUE! | #VALUE! | #VALUE! | #VALUE!
- | 0 | 0 | 0 | 0 | 0 | 0 | 0
#1 (obsolete) Airmatic | 0.045 | 0.222 | 0.1 | 0.0012117 | 0.004227 | 0.0015547 | 0.0023311
American Radiator Co. Detroit Controls #500 Airid (obsolete) | 0.036 | 0.061 | 0.08 | 0.00096939 | 0.0011615 | 0.0012437 | 0.0011249
ARCO Detroit Controls Multiport Setting 1-- (obsolete) | Note 3 | Note 3 | Note 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ARCO Detroit Controls Multiport Setting 2 (obsolete) | Note 3 | Note 3 | Note 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ARCO Detroit Controls Multiport Setting 3- (obsolete) | Note 3 | Note 3 | 0.011 | #VALUE! | #VALUE! | 0.00017101 | #VALUE!
Detroit Controls Multiport Setting 4 (obsolete) ARCO | 0.021 | 0.028 | 0.038 | 0.00056548 | 0.00053314 | 0.00059077 | 0.00056313
ARCO Detroit Controls Multiport Setting 5 (obsolete) | 0.045 | 0.075 | 0.1 | 0.0012117 | 0.0014281 | 0.0015547 | 0.0013982
ARCO Detroit Controls Multiport Setting 6 (obsolete) | 0.05 | 0.108 | 0.141 | 0.0013464 | 0.0020564 | 0.0021921 | 0.0018649
ARCO Detroit Controls Multiport Setting 7-- (obsolete) | 0.066 | 0.116 | 0.158 | 0.0017772 | 0.0022087 | 0.0024564 | 0.0021474
Detroit Controls Multiport Setting 8 (obsolete) ARCO | 0.083 | 0.141 | 0.191 | 0.002235 | 0.0026847 | 0.0029694 | 0.0026297
ARCO Detroit Controls Multiport Setting 9 (obsolete) | 0.1 | 0.158 | 0.208 | 0.0026928 | 0.0030084 | 0.0032337 | 0.0029783
ARCO Detroit Controls Multiport Setting 10- (obsolete) | 0.116 | 0.183 | 0.241 | 0.0031236 | 0.0034844 | 0.0037467 | 0.0034516
Detroit Controls #5000 Airid Variport (obsolete) Low setting | NONE | 0.011 | 0.016 | #VALUE! | 0.00020945 | 0.00024875 | #VALUE!
Detroit Controls #5000 Airid Variport (obsolete) Med setting | 0.036 | 0.051 | 0.061 | 0.00096939 | 0.00097107 | 0.00094835 | 0.00096294
Detroit Controls #5000 Airid Variport (obsolete) High setting | 0.066 | 0.125 | 0.166 | 0.0017772 | 0.0023801 | 0.0025807 | 0.002246
Dole 1933 | 0.033 | 0.055 | 0.07 | 0.00088861 | 0.0010472 | 0.0010883 | 0.001008
Dole 1A Setting 1 | 0.045 | 0.071 | 0.125 | 0.0012117 | 0.0013519 | 0.0019433 | 0.0015023
Dole 1A Setting 2 | 0.068 | 0.116 | 0.15 | 0.0018311 | 0.0022087 | 0.002332 | 0.0021239
Dole 1A Setting 3 | 0.083 | 0.125 | 0.166 | 0.002235 | 0.0023801 | 0.0025807 | 0.0023986
Dole 1A Setting 4 | 0.091 | 0.15 | 0.191 | 0.0024504 | 0.0028561 | 0.0029694 | 0.0027586
Dole 1A Setting 5 | 0.125 | 0.208 | 0.266 | 0.0033659 | 0.0039605 | 0.0041354 | 0.0038206
Dole 1A Setting 6 | 0.133 | 0.216 | 0.283 | 0.0035814 | 0.0041128 | 0.0043997 | 0.0040313
Dole 1A Setting 1 Modern Version W/Plastic Tongue *Note 4 | 0.061 | 0.111 | 0.148 | 0.0016426 | 0.0021135 | 0.0023009 | 0.002019
Dole 1A Setting 2 Modern Version W/Plastic Tongue *Note 4 | 0.084 | 0.141 | 0.186 | 0.0022619 | 0.0026847 | 0.0028917 | 0.0026128
Dole 1A Setting 3 Modern Version W/Plastic Tongue *Note 4 | 0.108 | 0.183 | 0.228 | 0.0029082 | 0.0034844 | 0.0035446 | 0.0033124
Dole 1A Setting 4 Modern Version W/Plastic Tongue *Note 4 | 0.116 | 0.201 | 0.254 | 0.0031236 | 0.0038272 | 0.0039488 | 0.0036332
Dole 1A Setting 5 Modern Version W/Plastic Tongue *Note 4 | 0.129 | 0.21 | 0.266 | 0.0034737 | 0.0039985 | 0.0041354 | 0.0038692
Dole 1A Setting 6 Modern Version W/Plastic Tongue *Note 4 | 0.133 | 0.22 | 0.274 | 0.0035814 | 0.0041889 | 0.0042598 | 0.00401
Dole 1A Setting 7 Modern Version W/Plastic Tongue *Note 4 | 0.143 | 0.233 | 0.295 | 0.0038506 | 0.0044365 | 0.0045863 | 0.0042911
Dole 1A Setting 8 Modern Version W/Plastic Tongue *Note 4 | 0.147 | 0.245 | 0.283 | 0.0039584 | 0.004665 | 0.0043997 | 0.004341
Dole 1A Setting 9 Modern Version W/Plastic Tongue *Note 4 | 0.152 | 0.268 | 0.289 | 0.004093 | 0.0051029 | 0.004493 | 0.004563
Dole 1A Setting 10 Modern Version W/Plastic Tongue *Note 4 | 0.152 | 0.269 | 0.289 | 0.004093 | 0.0051219 | 0.004493 | 0.0045693
Dole 1A Cap Removed Modern Version W/Plastic Tongue | 0.212 | 0.339 | 0.431 | 0.0057086 | 0.0064548 | 0.0067006 | 0.006288
Flair #51 - - (obsolete) | 0.116 | 0.191 | 0.25 | 0.0031236 | 0.0036368 | 0.0038867 | 0.003549
Gorton 4 | 0.025 | 0.04 | 0.055 | 0.00067319 | 0.00076163 | 0.00085507 | 0.00076329
Gorton 5 | 0.08 | 0.13 | 0.16 | 0.0021542 | 0.0024753 | 0.0024875 | 0.0023723
Gorton 6 | 0.15 | 0.235 | 0.3 | 0.0040391 | 0.0044746 | 0.004664 | 0.0043926
Gorton C | 0.27 | 0.45 | 0.57 | 0.0072704 | 0.0085683 | 0.0088616 | 0.0082334
Gorton D | 0.33 | 0.54 | 0.7 | 0.0088861 | 0.010282 | 0.010883 | 0.010017
Heat Timer Varivalve Min Setting Angle Pattern | 0.065 | 0.158 | 0.2 | 0.0017503 | 0.0030084 | 0.0031093 | 0.0026227
Heat Timer Varivalve 50% Setting Angle Pattern | 0.34 | 0.58 | 0.766 | 0.0091554 | 0.011044 | 0.011909 | 0.010703
Heat Timer Varivalve Max Setting Angle Pattern | 0.516 | 0.85 | 1.13 | 0.013895 | 0.016185 | 0.017568 | 0.015882
Heat Timer Varivalve Min Setting Straight Pattern | 0.06 | 0.083 | 0.33 | 0.0016157 | 0.0015804 | 0.0051304 | 0.0027755
Heat Timer Varivalve 50% Setting Straight Pattern | 0.53 | 0.8 | 1.03 | 0.014272 | 0.015233 | 0.016013 | 0.015172
Heat Timer Varivalve Max Setting Straight Pattern | 0.66 | 1.08 | 1.36 | 0.017772 | 0.020564 | 0.021143 | 0.019827
Hoffman #1 - - (obsolete) | 0.016 | 0.075 | 0.1 | 0.00043084 | 0.0014281 | 0.0015547 | 0.0011379
Hoffman 1A Setting 1 | 0.02 | 0.026 | 0.033 | 0.00053855 | 0.00049506 | 0.00051304 | 0.00051555
Hoffman 1A Setting 2 | 0.026 | 0.043 | 0.056 | 0.00070012 | 0.00081875 | 0.00087061 | 0.00079649
Hoffman 1A Setting 3 | 0.1 | 0.158 | 0.2 | 0.0026928 | 0.0030084 | 0.0031093 | 0.0029368
Hoffman 1A Setting 4 | 0.108 | 0.16 | 0.21 | 0.0029082 | 0.0030465 | 0.0032648 | 0.0030732
Hoffman 1A Setting 5 | 0.14 | 0.22 | 0.29 | 0.0037699 | 0.0041889 | 0.0045085 | 0.0041558
Hoffman 1A Setting 6 | 0.145 | 0.225 | 0.3 | 0.0039045 | 0.0042842 | 0.004664 | 0.0042842
Hoffman #2 Vacuum Vent Non Adjustable - - (obsolete) | 0.016 | 0.066 | 0.1 | 0.00043084 | 0.0012567 | 0.0015547 | 0.0010807
Hoffman #2 Vacuum Vent Setting 1 - - (obsolete) | 0.001 | 0.021 | 0.025 | 2.6928e-05 | 0.00039985 | 0.00038867 | 0.00027182
Hoffman #2 Vacuum Vent Setting 2 - - (obsolete) | 0.006 | 0.024 | 0.028 | 0.00016157 | 0.00045698 | 0.00043531 | 0.00035128
Hoffman #2 Vacuum Vent Setting 3 - - (obsolete) | 0.008 | 0.025 | 0.033 | 0.00021542 | 0.00047602 | 0.00051304 | 0.00040149
Hoffman #2 Vacuum Vent Setting 4 - - (obsolete) | 0.01 | 0.026 | 0.036 | 0.00026928 | 0.00049506 | 0.00055968 | 0.00044134
Hoffman #2 Vacuum Vent Setting 5 - - (obsolete) | 0.013 | 0.029 | 0.04 | 0.00035006 | 0.00055218 | 0.00062187 | 0.00050803
Hoffman #2 Vacuum Vent Setting 6 - - (obsolete) | 0.016 | 0.031 | 0.045 | 0.00043084 | 0.00059026 | 0.0006996 | 0.00057357
Hoffman #2A Vacuum Vent Setting 1 - - (obsolete) | 0.001 | 0.023 | 0.025 | 2.6928e-05 | 0.00043794 | 0.00038867 | 0.00028451
Hoffman #2A Vacuum Vent Setting 2 - - (obsolete) | 0.018 | 0.03 | 0.043 | 0.0004847 | 0.00057122 | 0.00066851 | 0.00057481
Hoffman #2A Vacuum Vent Setting 3 - - (obsolete) | 0.021 | 0.038 | 0.053 | 0.00056548 | 0.00072355 | 0.00082397 | 0.00070433
Hoffman #2A Vacuum Vent Setting 4 - - (obsolete) | 0.028 | 0.058 | 0.068 | 0.00075397 | 0.0011044 | 0.0010572 | 0.00097183
Hoffman #2A Vacuum Vent Setting 5 - - (obsolete) | 0.036 | 0.063 | 0.088 | 0.00096939 | 0.0011996 | 0.0013681 | 0.001179
Hoffman #2A Vacuum Vent Setting 6 - - (obsolete) | 0.041 | 0.083 | 0.116 | 0.001104 | 0.0015804 | 0.0018034 | 0.0014959
Hoffman #3 (Paul Vent) | 0.175 | 0.283 | 0.416 | 0.0047123 | 0.0053885 | 0.0064674 | 0.0055227
Hoffman 40 | 0.042 | 0.067 | 0.087 | 0.001131 | 0.0012757 | 0.0013526 | 0.0012531
Hoffman 41 | 0.058 | 0.1 | 0.125 | 0.0015618 | 0.0019041 | 0.0019433 | 0.0018031
Hoffman #70 Airport Non Adjustable - - (obsolete) | 0.05 | 0.108 | 0.141 | 0.0013464 | 0.0020564 | 0.0021921 | 0.0018649
Hoffman #70 Airport Setting #1 - - (obsolete) | 0.045 | 0.078 | 0.125 | 0.0012117 | 0.0014852 | 0.0019433 | 0.0015467
Hoffman #70 Airport Setting #2 - - (obsolete) | 0.05 | 0.087 | 0.15 | 0.0013464 | 0.0016565 | 0.002332 | 0.0017783
Hoffman #70 Airport Setting #3 - - (obsolete) | 0.053 | 0.116 | 0.166 | 0.0014272 | 0.0022087 | 0.0025807 | 0.0020722
Hoffman #70 Airport Setting #4 - - (obsolete) | 0.056 | 0.141 | 0.183 | 0.0015079 | 0.0026847 | 0.002845 | 0.0023459
Hoffman #70 Airport Setting #5 - - (obsolete) | 0.06 | 0.15 | 0.191 | 0.0016157 | 0.0028561 | 0.0029694 | 0.0024804
Hoffman #70 Airport Setting #6 - - (obsolete) | 0.066 | 0.15 | 0.191 | 0.0017772 | 0.0028561 | 0.0029694 | 0.0025342
Hoffman #74 Unit Heater Vent | 0.033 | 0.083 | 0.108 | 0.00088861 | 0.0015804 | 0.001679 | 0.0013827
Hoffman #500 | 0.066 | 0.112 | 0.142 | 0.0017772 | 0.0021326 | 0.0022076 | 0.0020391
Homart #775.8812 | 0.083 | 0.133 | 0.175 | 0.002235 | 0.0025324 | 0.0027207 | 0.002496
Marsh Paul Vent (circa 1901) - - (obsolete) | 0.35 | 0.583 | 0.75 | 0.0094246 | 0.011101 | 0.01166 | 0.010728
Marsh #3 (Paul Vent) - - (obsolete) | 0.183 | 0.295 | 0.375 | 0.0049277 | 0.005617 | 0.00583 | 0.0054582
Maid-O-Mist 4 | 0.028 | 0.045 | 0.06 | 0.00075397 | 0.00085683 | 0.0009328 | 0.00084787
Maid-O-Mist 5 | 0.1 | 0.158 | 0.2 | 0.0026928 | 0.0030084 | 0.0031093 | 0.0029368
Maid-O-Mist 6 | 0.15 | 0.241 | 0.3 | 0.0040391 | 0.0045888 | 0.004664 | 0.0044306
Maid-O-Mist C | 0.283 | 0.45 | 0.583 | 0.0076205 | 0.0085683 | 0.0090637 | 0.0084175
Maid-O-Mist D | 0.341 | 0.6 | 0.783 | 0.0091823 | 0.011424 | 0.012173 | 0.010927
M.S. Little Co. #L-15 - - (obsolete) | 0.026 | 0.045 | 0.055 | 0.00070012 | 0.00085683 | 0.00085507 | 0.000804
National Steam Specialty Co. Paul Vent - - (obsolete) | 0.15 | 0.266 | 0.333 | 0.0040391 | 0.0050648 | 0.005177 | 0.0047603
U.S. Radiator #3 Triton - - (obsolete) | 0.023 | 0.033 | 0.041 | 0.00061933 | 0.00062834 | 0.00063741 | 0.00062836
Ventrite #1 Setting 1 | Off | Off | Off | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Ventrite #1 Setting 2 | 0.033 | 0.02 | 0.021 | 0.00088861 | 0.00038081 | 0.00032648 | 0.00053197
Ventrite #1 Setting 3 | 0.025 | 0.036 | 0.046 | 0.00067319 | 0.00068546 | 0.00071515 | 0.00069127
Ventrite #1 Setting 4 | 0.03 | 0.053 | 0.066 | 0.00080783 | 0.0010092 | 0.0010261 | 0.00094769
Ventrite #1 Setting 5 | 0.045 | 0.071 | 0.091 | 0.0012117 | 0.0013519 | 0.0014147 | 0.0013261
Ventrite #1 Setting 6 | 0.056 | 0.091 | 0.116 | 0.0015079 | 0.0017327 | 0.0018034 | 0.0016814
Ventrite #1 Setting 7 | 0.07 | 0.108 | 0.133 | 0.0018849 | 0.0020564 | 0.0020677 | 0.002003
Ventrite #1 Setting 8 | 0.083 | 0.125 | 0.158 | 0.002235 | 0.0023801 | 0.0024564 | 0.0023571
Ventrite #2 IVS (obsolete Anderson Manufacturing) | 0.028 | 0.053 | 0.078 | 0.00075397 | 0.0010092 | 0.0012126 | 0.00099192
Ventrite #11 | 0.06 | 0.1 | 0.116 | 0.0016157 | 0.0019041 | 0.0018034 | 0.0017744
Watts SV | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 1/8 | 0.03 | 0.063 | 0.075 | 0.00080783 | 0.0011996 | 0.001166 | 0.0010578
Watts SVA setting 1/4 | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 1/2 ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 3/4 ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 7/8 ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting Full ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
STEAM TRAPS | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Barnes & Jones 1/2" #122 | 1.5 | 1.8 | 2.7 | 0.040391 | 0.034273 | 0.041976 | 0.03888
Dunham #1 1/2" - - (obsolete) | 1.45 | 2.41 | 3 | 0.039045 | 0.045888 | 0.04664 | 0.043858
Dunham #1 W/B&J Cage Unit | 0.73 | 1.16 | 1.5 | 0.019657 | 0.022087 | 0.02332 | 0.021688
Dunham - Bush #1E - - (obsolete) | 1.08 | 1.8 | 2.25 | 0.029082 | 0.034273 | 0.03498 | 0.032778
Dunham - Bush #1E W/B&J Cage Unit | 0.71 | 1.13 | 1.41 | 0.019119 | 0.021516 | 0.021921 | 0.020852
Hoffman 17C 1/2" W/Dura-Stat Capsule | 0.53 | 0.85 | 1.1 | 0.014272 | 0.016185 | 0.017101 | 0.015852
Hoffman 17C W/B&J Cage Unit | 1.3 | 2.116 | 2.7 | 0.035006 | 0.04029 | 0.041976 | 0.039091
Hoffman 17D 1/2" Model 1939 - - (obsolete) | 1.45 | 2.38 | 3 | 0.039045 | 0.045317 | 0.04664 | 0.043667
Ideal Heating Co. Thermostatic 1/2" - - (obsolete) | 1.53 | 2.33 | 3.08 | 0.041199 | 0.044365 | 0.047884 | 0.044483
Ideal W/B&J Cage Unit Installed | 1.25 | 2 | 2.58 | 0.033659 | 0.038081 | 0.04011 | 0.037284
Illinois 1/2" #1G | 0.86 | 1.2 | 1.6 | 0.023158 | 0.022849 | 0.024875 | 0.023627
Marsh #1 Reflux - - (obsolete) | 1.13 | 1.83 | 2.36 | 0.030428 | 0.034844 | 0.03669 | 0.033988
Marsh #1 Reflux W/B&J Cage Unit | 0.73 | 1.16 | 1.5 | 0.019657 | 0.022087 | 0.02332 | 0.021688
Marsh 1N 1/2" | 0.53 | 0.91 | 1.16 | 0.014272 | 0.017327 | 0.018034 | 0.016544
Mepco 1/2" #1E | 1.08 | 1.4 | 1.9 | 0.029082 | 0.026657 | 0.029539 | 0.028426
Mepco 1/2" #1R | 1.08 | 1.4 | 1.9 | 0.029082 | 0.026657 | 0.029539 | 0.028426
Milvaco Model #0 - - (obsolete) | 1.08 | 1.71 | 2.13 | 0.029082 | 0.03256 | 0.033114 | 0.031585
Milvaco Model #0 W/B&J Cage Unit | 1 | 1.58 | 1.966 | 0.026928 | 0.030084 | 0.030565 | 0.029192
Monash #30 1/2" | 0.86 | 1.2 | 1.6 | 0.023158 | 0.022849 | 0.024875 | 0.023627
Monash #34 1/2" | 1.21 | 2 | 2.5 | 0.032582 | 0.038081 | 0.038867 | 0.03651
Monash #38 1/2" | 1.45 | 2.45 | 3.08 | 0.039045 | 0.04665 | 0.047884 | 0.044526
Mouat Model 1924 Thermostatic 1/2" - - (obsolete) | 1.53 | 2.33 | 3.08 | 0.041199 | 0.044365 | 0.047884 | 0.044483
Mouat 1924 W/B&J Cage Unit Installed | 1.25 | 2 | 2.58 | 0.033659 | 0.038081 | 0.04011 | 0.037284
Mouat #35 1/2" - - (Obsolete) | 1.33 | 1.66 | 2.08 | 0.035814 | 0.031608 | 0.032337 | 0.033253
Mouat #35 1/2" W/B&J Cage Unit Installed | 1.366 | 2.33 | 2.91 | 0.036783 | 0.044365 | 0.045241 | 0.04213
Mouat #36 1/2" - - (Obsolete) | 1.083 | 1.533 | 1.83 | 0.029163 | 0.029189 | 0.02845 | 0.028934
Mouat #36 1/2" W/B&J Cage Unit Installed | 1.266 | 2 | 2.5 | 0.03409 | 0.038081 | 0.038867 | 0.037013
Mouat Water Seal Trap 1/2" Oval - - (obsolete) | 2 | 2.4 | 3.4 | 0.053855 | 0.045698 | 0.052859 | 0.050804
Mouat Water Seal Trap 1/2" Round - - (obsolete) | 2 | 2.4 | 3.6 | 0.053855 | 0.045698 | 0.055968 | 0.05184
Nicholson #N125 | 1.53 | 2.53 | 3.08 | 0.041199 | 0.048173 | 0.047884 | 0.045752
Sarco A125 1/2" | 0.5 | 0.78 | 1 | 0.013464 | 0.014852 | 0.015547 | 0.014621
Sterling 7-50-A-1/2" | 1.08 | 1.75 | 2.16 | 0.029082 | 0.033321 | 0.033581 | 0.031995
Trane B1 W/Original Bellows - - (obsolete) | 0.5 | 0.75 | 1 | 0.013464 | 0.014281 | 0.015547 | 0.01443
Trane B1 W/Modern Trane Element | 0.78 | 1.25 | 1.58 | 0.021004 | 0.023801 | 0.024564 | 0.023123
Trane B1 W/B&J Cage Unit | 0.75 | 1.2 | 1.5 | 0.020196 | 0.022849 | 0.02332 | 0.022121
Trane 1/2" (no number) - - (obsolete) | 1.58 | 2.66 | 3.33 | 0.042546 | 0.050648 | 0.05177 | 0.048321
Warren Webster 02H 1/2" W/B&J Cage Unit | 0.783 | 1.333 | 1.75 | 0.021084 | 0.025381 | 0.027207 | 0.024557
Warren Webster 02H 1/2" W/Tunstall Capsule | 0.616 | 0.966 | 1.21 | 0.016587 | 0.018393 | 0.018811 | 0.017931
Warren Webster 512H 1/2" W/512A seat (5/16") - - (obsolete) | 1.08 | 1.75 | 2.25 | 0.029082 | 0.033321 | 0.03498 | 0.032461
Warren Webster 512H 1/2" W/512S seat (1/4") - - (obsolete) | 0.783 | 1.28 | 1.66 | 0.021084 | 0.024372 | 0.025807 | 0.023755
Warren Webster 512H 1/2" W/B&J Cage Unit | 1.36 | 2.25 | 2.83 | 0.036621 | 0.042842 | 0.043997 | 0.041153
Warren Webster 712HB 1/2" W/H57 Seat (.368") - - (obsolete) | 0.75 | 1.233 | 1.433 | 0.020196 | 0.023477 | 0.022278 | 0.021984
Warren Webster 712 HB 1/2" W/522S Seat (.332") - - (obsolete) | 0.5 | 0.8 | 1.25 | 0.013464 | 0.015233 | 0.019433 | 0.016043
Warren Webster 712 HB 1/2" W/B&J Cage Unit | 1.55 | 2.55 | 3.216 | 0.041738 | 0.048554 | 0.049998 | 0.046763
Barnes & Jones 3/4" #134A | 1.36 | 2.28 | 2.88 | 0.036621 | 0.043413 | 0.044774 | 0.041603
Hoffman 8C 3/4" | 1 | 1.58 | 2 | 0.026928 | 0.030084 | 0.031093 | 0.029368
Mepco 3/4" 2E | 1.53 | 2.55 | 3.16 | 0.041199 | 0.048554 | 0.049127 | 0.046293
Monash #48 3/4" | 2.16 | 3.5 | 5 | 0.058164 | 0.066642 | 0.077733 | 0.067513
Sterling 3/4" #753A | 1.25 | 2 | 2.58 | 0.033659 | 0.038081 | 0.04011 | 0.037284
Spirax Sarco F&T Traps (FT-15, FT-30, etc.) | 0.5 | 0.75 | 0.966 | 0.013464 | 0.014281 | 0.015018 | 0.014254
Hoffman F&T Traps (FT015H, FT015C, etc.) | 0.5 | 0.75 | 0.95 | 0.013464 | 0.014281 | 0.014769 | 0.014171
Sterling F&T Traps (vac. to 15 lb.) | 1.3 | 2.083 | 2.666 | 0.035006 | 0.039662 | 0.041447 | 0.038705
Barnes & Jones F&T Traps (vac. to 15 lb.) | 0.75 | 1.2 | 1.5 | 0.020196 | 0.022849 | 0.02332 | 0.022121

## Radiators
Heat Load(%) | Radiator Type | Height(In) | Cols/Tubes/(WxL) | Sections | Upfeed Length(ft) | Vent/Trap Type | Trap Status | EDR Sqft | EDR Ideal | Btu/hr | Vent Capacity(3oz) | Radiator Vol(ft3) | Supply Pipe Size | Radiator Pressure(PSI) | Condensate(lb/hr) | Pipe Radiation(BTU/hr) | Pipe Volume(ft3) | Pipe Condensate(lb/hr) | Radiator Weight(lbs) | Pipe weight(lbs) | Failed Open Trap Steam Flow(lb/hr) | Total BTUs Radiation | Total EDR | Min PSI | Total Steam Pass Through(lb/hr)
100% | Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506 | 1193940 | 4974.75 | 0.06755 | 9.2782
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Failed-Open | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0.17506
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
| Column | 45 | 2 | 8 | 20 | Illinois 1/2" #1G | Operational | 40 | 40 | 9600 | 0.86 | 1 | 1 | 0.06755 | 9.6289 | 2460 | 0.10914 | 9.8969 | 280 | 33.58 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.073808 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## REPORT
Address:
Boiler Information |  | Relavent Calculations
Boiler Manufacturer | Weil-Mclain | Water @ Waterline(gal) | 69.1
Boiler Model | LGB-12 | Time to Steam(minutes) | 9
Rated Power Input(BTU/HR) | 1430000 | Time to Vent(minutes) | 19
Gross Power Output(BTU/HR) | 1144000 | Time to Steady State(min) | 49.9233
Water @ Waterline(gal) | 69.1
Radiator Calcuations |  | System Status
TOTAL RADIATION (BTU/HR) | 1248540 | Trap Operating % | 46.46%
Radiator Output(EDR) | 3960 | Radiator Operable % | 100%
Steam Main Output(EDR) | 227.5 | Steam Loss(BTU/Hr) | 0
Steam Upfeed Output(EDR) | 1014.75
Column Radiators | 99
Tube Radiators | 0
Convectors | 0
Copper Cabinets | 0
NOTES

## Boiler List (hidden)
Manufacturer | Boiler Model | Input MBH (Note 2) | Gross Output MBH (Note 2) | Sq. Ft. Steam | Boiler Water Content Gallons (Steam to Waterline) | Approx. Shipping Weight (lbs.) |  | Manufactuer List
Weil-Mclain | LGB-4 | 400 | 312 | 975 | 23.2 | 1185 | Weil-Mclain
Weil-Mclain | LGB-5 | 520 | 409 | 1279 | 28.9 | 1455 | Weil-Mclain | Weil-Mclain
Weil-Mclain | LGB-6 | 650 | 514 | 1607 | 34.6 | 1725 | Weil-Mclain | Burnham
Weil-Mclain | LGB-7 | 780 | 619 | 1936 | 40.3 | 2005 | Weil-Mclain | Peerless
Weil-Mclain | LGB-8 | 910 | 724 | 2264 | 46 | 2290 | Weil-Mclain | Green Mountain
Weil-Mclain | LGB-9 | 1040 | 829 | 2591 | 51.9 | 2560 | Weil-Mclain
Weil-Mclain | LGB-10 | 1170 | 934 | 2918 | 57.6 | 2800 | Weil-Mclain
Weil-Mclain | LGB-11 | 1300 | 1039 | 3246 | 63.4 | 3105 | Weil-Mclain
Weil-Mclain | LGB-12 | 1430 | 1144 | 3576 | 69.1 | 3365 | Weil-Mclain
Weil-Mclain | LGB-13 | 1560 | 1239 | 3868 | 74.9 | 3785 | Weil-Mclain
Weil-Mclain | LGB-14 | 1690 | 1344 | 4228 | 80.7 | 4085 | Weil-Mclain
Weil-Mclain | LGB-15 | 1820 | 1449 | 4592 | 86.4 | 4355 | Weil-Mclain
Weil-Mclain | LGB-16 | 1950 | 1552 | 4950 | 92.2 | 4725 | Weil-Mclain
Weil-Mclain | LGB-17 | 2080 | 1658 | 5316 | 98 | 4975 | Weil-Mclain
Weil-Mclain | LGB-18 | 2210 | 1764 | 5682 | 103.6 | 5270 | Weil-Mclain
Weil-Mclain | LGB-19 | 2340 | 1867 | 6034 | 109.5 | 5540 | Weil-Mclain
Weil-Mclain | LGB-20 | 2470 | 1974 | 6384 | 115.3 | 5820 | Weil-Mclain
Weil-Mclain | LGB-21 | 2600 | 2077 | 6720 | 121 | 6080 | Weil-Mclain
Weil-Mclain | LGB-22 | 2730 | 2184 | 7065 | 126.8 | 6365 | Weil-Mclain
Weil-Mclain | LGB-23 | 2860 | 2288 | 7402 | 132.5 | 6625 | Weil-Mclain
Weil-Mclain | Series 80 - 380 | 346 | 278 | 867 | 27.5 | 1058 | Weil-Mclain
Weil-Mclain | Series 80 - 480 | 491 | 396 | 1238 | 36 | 1203 | Weil-Mclain
Weil-Mclain | Series 80 - 580 | 639 | 515 | 1608 | 44.5 | 1448 | Weil-Mclain
Weil-Mclain | Series 80 - 680 | 787 | 634 | 1983 | 53 | 1843 | Weil-Mclain
Weil-Mclain | Series 80 - 780 | 935 | 753 | 2354 | 61.5 | 2088 | Weil-Mclain
Weil-Mclain | Series 80 - 880 | 1082 | 872 | 2725 | 70 | 2317 | Weil-Mclain
Weil-Mclain | Series 80 - 980 | 1230 | 991 | 3096 | 78.5 | 2678 | Weil-Mclain
Weil-Mclain | Series 80 - 1080 | 1378 | 1110 | 3471 | 87 | 2923 | Weil-Mclain
Weil-Mclain | Series 80 - 1180 | 1526 | 1229 | 3842 | 95.5 | 3068 | Weil-Mclain
Weil-Mclain | Series 80 - 1280 | 1674 | 1348 | 4242 | 104 | 3313 | Weil-Mclain
Weil-Mclain | Series 88 - 488R | 996 | 827 | 2583 | 109 | 2860 | Weil-Mclain
Weil-Mclain | Series 88 - 488 | 1010 | 839 | 2621 | 109 | 2860 | Weil-Mclain
Weil-Mclain | Series 88 - 588 | 1356 | 1126 | 3521 | 132 | 3340 | Weil-Mclain
Weil-Mclain | Series 88 - 688 | 1701 | 1413 | 4469 | 155 | 3820 | Weil-Mclain
Weil-Mclain | Series 88 - 788 | 2046 | 1700 | 5463 | 178 | 4345 | Weil-Mclain
Weil-Mclain | Series 88 - 788R | 1999 | 1661 | 5463 | 178 | 4345 | Weil-Mclain
Weil-Mclain | Series 88 - 888 | 2382 | 1987 | 6427 | 201 | 4925 | Weil-Mclain
Weil-Mclain | Series 88 - 988R | 2482 | 2062 | 6671 | 224 | 5600 | Weil-Mclain
Weil-Mclain | Series 88 - 988 | 2737 | 2274 | 7358 | 224 | 5600 | Weil-Mclain
Weil-Mclain | Series 88 - 1088R | 2887 | 2399 | 7763 | 247 | 6130 | Weil-Mclain
Weil-Mclain | Series 88 - 1088 | 3082 | 2561 | 8283 | 247 | 6130 | Weil-Mclain
Weil-Mclain | Series 88 - 1188 | 3428 | 2848 | 9213 | 270 | 6695 | Weil-Mclain
Weil-Mclain | Series 88 - 1288 | 3773 | 3135 | 10147 | 293 | 7260 | Weil-Mclain
Weil-Mclain | Series 88 - 1388 | 4119 | 3422 | 11071 | 316 | 7890 | Weil-Mclain
Weil-Mclain | Series 88 - 1488 | 4464 | 3709 | 12000 | 339 | 8410 | Weil-Mclain
Weil-Mclain | Series 88 - 1588 | 4809 | 3996 | 12925 | 362 | 9005 | Weil-Mclain
Weil-Mclain | Series 88 - 1688R | 4979 | 4137 | 13383 | 385 | 9525 | Weil-Mclain
Weil-Mclain | Series 88 - 1688 | 5155 | 4283 | 13854 | 385 | 9525 | Weil-Mclain
Weil-Mclain | Series 88 - 1788 | 5494 | 4570 | 14783 | 408 | 9780 | Weil-Mclain
Weil-Mclain | Series 88 - 1888 | 5845 | 4857 | 15713 | 431 | 10775 | Weil-Mclain
Weil-Mclain | Series 94 - H-1094 | 3247 | 2607 | 8435 | 329.8 | 12320 | Weil-Mclain
Weil-Mclain | Series 94 - H-1194 | 3608 | 2897 | 9372 | 357.5 | 13162 | Weil-Mclain
Weil-Mclain | Series 94 - H-1294 | 3969 | 3187 | 10310 | 385.2 | 14004 | Weil-Mclain
Weil-Mclain | Series 94 - H-1394 | 4330 | 3481 | 11262 | 413 | 14846 | Weil-Mclain
Weil-Mclain | Series 94 - H-1494 | 4691 | 3772 | 12201 | 440.7 | 15688 | Weil-Mclain
Weil-Mclain | Series 94 - H-1594 | 5052 | 4062 | 13140 | 468.4 | 16530 | Weil-Mclain
Weil-Mclain | Series 94 - H-1694 | 5412 | 4351 | 14076 | 496.2 | 17372 | Weil-Mclain
Weil-Mclain | Series 94 - H-1794 | 5773 | 4641 | 15015 | 523.9 | 19014 | Weil-Mclain
Weil-Mclain | Series 94 - H-1894 | 6134 | 4938 | 15974 | 551.6 | 19856 | Weil-Mclain
Weil-Mclain | Series 94 - H-1994 | 6495 | 5228 | 16914 | 579.4 | 20698 | Weil-Mclain
Weil-Mclain | Series 94 - H-2094 | 6856 | 5519 | 17854 | 607.1 | 21540 | Weil-Mclain
Weil-Mclain | Series 94 - H-2194 | 7216 | 5809 | 18792 | 634.8 | 22552 | Weil-Mclain
Weil-Mclain | Series 94 - H-2294 | 7649 | 6157 | 19919 | 662.6 | 23419 | Weil-Mclain
Weil-Mclain | Series 94 - H-2394 | 7938 | 6390 | 20672 | 690.3 | 24286 | Weil-Mclain
Weil-Mclain | Series 94 - H-2494 | 8371 | 6739 | 21799 | 718 | 25153 | Weil-Mclain
Weil-Mclain | Series 94 - H-2594 | 8660 | 6971 | 22552 | 745.8 | 26020 | Weil-Mclain
Weil-Mclain | Series 94 - H-894 | 2540 | 2040 | 6598 | 274.3 | 10636 | Weil-Mclain
Weil-Mclain | Series 94 - H-994 | 2887 | 2318 | 7500 | 302 | 11478 | Weil-Mclain
Weil-Mclain | *EG-30- | 75 | 62 | 196 | 8.4 | 430 | Weil-Mclain
Weil-Mclain | *EG-35- | 100 | 82 | 258 | 8.4 | 430 | Weil-Mclain
Weil-Mclain | *EG-40- | 125 | 103 | 321 | 9.8 | 505 | Weil-Mclain
Weil-Mclain | *EG-45- | 150 | 124 | 388 | 9.8 | 505 | Weil-Mclain
Weil-Mclain | *EG-50- | 175 | 145 | 454 | 11.2 | 585 | Weil-Mclain
Weil-Mclain | *EG-55- | 200 | 166 | 521 | 11.2 | 585 | Weil-Mclain
Weil-Mclain | *EG-65- | 238 | 198 | 621 | 12.6 | 660 | Weil-Mclain
Weil-Mclain | EG-75- | 282 | 234 | 733 | 14 | 735 | Weil-Mclain
Weil-Mclain | EGH-85-S | 315 | 240.24 | 760 | 15.4 | 825 | Weil-Mclain
Weil-Mclain | EGH-95-S | 360 | 275.88 | 868 | 16.8 | 915 | Weil-Mclain
Weil-Mclain | EGH-105-S | 405 | 308.88 | 977 | 18.2 | 1005 | Weil-Mclain
Weil-Mclain | EGH-115-S | 450 | 343.2 | 1085 | 19.6 | 1095 | Weil-Mclain
Weil-Mclain | EGH-125-S | 495 | 378.84 | 1193 | 21 | 1185 | Weil-Mclain
Burnham | V1104H | 837 | 674 | 2106 | 59 | 2103.94 | Burnham
Burnham | V1105H | 1068 | 862 | 2694 | 68 | 2508.88 | Burnham
Burnham | V1106H | 1328 | 1074 | 3358 | 77 | 2918.82 | Burnham
Burnham | V1107H | 1588 | 1288 | 4036 | 87 | 3324.42 | Burnham
Burnham | V1108H | 1876 | 1525 | 4857 | 96 | 3732.36 | Burnham
Burnham | V1109H | 2136 | 1741 | 5604 | 105 | 4146.3 | Burnham
Burnham | V1110H | 2396 | 1958 | 6333 | 115 | 4555.9 | Burnham
Burnham | V1111H | 2656 | 2175 | 7037 | 124 | 4962.84 | Burnham
Burnham | V1112H | 2887 | 2370 | 7668 | 133 | 5372.78 | Burnham
Burnham | V1113H | 3103 | 2546 | 8236 | 143 | 5769.38 | Burnham
Burnham | V1114H | 3392 | 2781 | 8997 | 152 | 6182.32 | Burnham
Burnham | V1115H | 3680 | 3015 | 9754 | 161 | 6599.26 | Burnham
Burnham | V1116H | 3897 | 3191 | 10323 | 171 | 7005.86 | Burnham
Burnham | V1117H | 4186 | 3425 | 11081 | 180 | 7414.8 | Burnham
Burnham | V1118H | 4474 | 3659 | 11835 | 189 | 7820.74 | Burnham
Burnham | V1119H | 4691 | 3833 | 12401 | 199 | 8229.34 | Burnham
Burnham | V1120H | 4979 | 4066 | 13154 | 208 | 8636.28 | Burnham
Burnham | V1121H | 5268 | 4299 | 13908 | 217 | 9051.22 | Burnham
Burnham | V1122H | 5485 | 4473 | 14471 | 227 | 9453.82 | Burnham
Burnham | V1123H | 5773 | 4705 | 15221 | 236 | 9862.76 | Burnham
Burnham | V903A | 447 | 347 | 1083 | 44.5 | 1067.87 | Burnham
Burnham | V904A | 606 | 483 | 1508 | 53 | 1368.98 | Burnham
Burnham | V905A | 808 | 646 | 2021 | 61.5 | 1671.09 | Burnham
Burnham | V906A | 1010 | 808 | 2525 | 70 | 1973.2 | Burnham
Burnham | V907A | 1198 | 959 | 2996 | 78.5 | 2275.31 | Burnham
Burnham | V908A | 1386 | 1110 | 3471 | 87 | 2577.42 | Burnham
Burnham | V909A | 1674 | 1342 | 4225 | 95.5 | 2879.53 | Burnham
Burnham | V910A | 1905 | 1528 | 4867 | 104 | 3180.64 | Burnham
Burnham | V911A | 2136 | 1714 | 5513 | 112.5 | 3482.75 | Burnham
Burnham | V912A | 2367 | 1900 | 6142 | 121 | 3784.86 | Burnham
Burnham | STMX075 | 75 | 62 | 169 | 6.8 | 484 | Burnham
Burnham | STMX100 | 100 | 82 | 258 | 6.8 | 484 | Burnham
Burnham | STMX125 | 125 | 103 | 321 | 9 | 600 | Burnham
Burnham | STMX150 | 150 | 124 | 388 | 9 | 600 | Burnham
Burnham | STMX175 | 175 | 144 | 450 | 11.2 | 729 | Burnham
Burnham | STMX200 | 200 | 165 | 517 | 11.2 | 729 | Burnham
Burnham | STMX250 | 250 | 206 | 646 | 13.2 | 842 | Burnham
Burnham | STMX299 | 299 | 246 | 771 | 15.6 | 881 | Burnham
Burnham | STMX350 | 350 | 284 | 892 | 27.8 | 1008 | Burnham
Burnham | STMX399 | 399 | 323 | 1013 | 20.1 | 1123 | Burnham
Burnham | STMX450 | 450 | 365 | 1142 | 22.2 | 1239 | Burnham
Burnham | STMX500 | 500 | 405 | 1271 | 24.4 | 1354 | Burnham
Burnham | STMX550 | 550 | 446 | 1396 | 26.6 | 1469 | Burnham
Burnham | Independence3 | 62 | 51 | 158 | 5.1 | 350 | Burnham
Burnham | Independence4 | 105 | 87 | 271 | 6.5 | 420 | Burnham
Burnham | Independence5 | 140 | 115 | 358 | 7.9 | 485 | Burnham
Burnham | Independence6 | 175 | 144 | 450 | 9.3 | 555 | Burnham
Burnham | Independence7 | 210 | 173 | 542 | 10.7 | 620 | Burnham
Burnham | Independence8 | 245 | 202 | 633 | 12.1 | 690 | Burnham
Burnham | Independence9 | 280 | 231 | 721 | 13.5 | 760 | Burnham
Peerless | 63-03L | 88.5 | 74 | 233 | 9.3 | 465 | Peerless
Peerless | 63-03 | 118 | 98 | 308 | 9.3 | 465 | Peerless
Peerless | 63-04L | 147.5 | 123 | 383 | 10.8 | 576 | Peerless
Peerless | 63-04 | 177 | 147 | 458 | 10.8 | 576 | Peerless
Peerless | 63-05L | 206.5 | 171 | 533 | 12.4 | 700 | Peerless
Peerless | 63-05 | 236 | 196 | 613 | 12.4 | 700 | Peerless
Peerless | 63-06 | 287.5 | 238 | 746 | 13.9 | 812 | Peerless
Peerless | SC(T)-05 | 404 | 327 | 1022 | 20.4 | 815 | Peerless
Peerless | SC(T)-06 | 505 | 409 | 1278 | 23.52 | 910 | Peerless
Peerless | SC(T)-07 | 577 | 468 | 1463 | 26.64 | 1005 | Peerless
Peerless | SC(T)-08 | 649 | 527 | 1647 | 29.76 | 1100 | Peerless
Peerless | SC(T)-09 | 722 | 586 | 1832 | 32.88 | 1195 | Peerless
Peerless | SC(T)-10 | 794 | 645 | 2016 | 36 | 1280 | Peerless
Peerless | 64-07 | 345 | 274 | 858 | 15.5 | 945 | Peerless
Peerless | 64-08 | 399 | 318 | 996 | 17 | 1081 | Peerless
Peerless | 64-09 | 460 | 367 | 1146 | 18.6 | 1218 | Peerless
Peerless | 64-10 | 517.5 | 413 | 1292 | 20.1 | 1354 | Peerless
Peerless | 64-11 | 575 | 459 | 1433 | 21.7 | 1490 | Peerless
Peerless | 64-12 | 632.5 | 506 | 1583 | 23.2 | 1527 | Peerless
Peerless | TCII-04 | 1143 | 931 | 2908 | 104 | 3185.844 | Peerless
Peerless | TCII-05 | 1458 | 1194 | 3733 | 126 | 3784.498 | Peerless
Peerless | TCII-06 | 1773 | 1458 | 4625 | 148 | 4383.152 | Peerless
Peerless | TCII-07 | 2088 | 1722 | 5542 | 169 | 4981.806 | Peerless
Peerless | TCII-08 | 2403 | 1985 | 6421 | 192 | 5580.46 | Peerless
Peerless | TCII-09 | 2718 | 2249 | 7275 | 214 | 6180.114 | Peerless
Peerless | TCII-10 | 3033 | 2513 | 8129 | 236 | 6793.768 | Peerless
Peerless | TCII-11 | 3348 | 2776 | 8979 | 258 | 7392.422 | Peerless
Peerless | TCII-12 | 3663 | 3040 | 9833 | 280 | 7991.076 | Peerless
Peerless | TCII-13 | 3978 | 3304 | 10688 | 302 | 8600.73 | Peerless
Peerless | TCII-14 | 4293 | 3567 | 11538 | 324 | 9194.384 | Peerless
Peerless | TCII-15 | 4608 | 3851 | 12392 | 346 | 10014.038 | Peerless
Peerless | TCII-16 | 4923 | 4095 | 13246 | 368 | 10653.692 | Peerless
Peerless | TCII-17 | 5238 | 4358 | 14100 | 390 | 11293.346 | Peerless
Peerless | TCII-18 | 5553 | 4622 | 14954 | 412 | 11933 | Peerless
Peerless | LC-04 | 686 | 1708 | 410 | 40.57 | 890 | Peerless
Peerless | LC-05R | 808 | 2029 | 487 | 47.29 | 1080 | Peerless
Peerless | LC-05 | 881 | 2208 | 530 | 47.29 | 1080 | Peerless
Peerless | LC-06 | 1077 | 2713 | 651 | 54.01 | 1270 | Peerless
Peerless | LC-07 | 1273 | 3217 | 772 | 60.73 | 1460 | Peerless
Peerless | LC-08 | 1469 | 3717 | 892 | 67.45 | 1650 | Peerless
Peerless | LC-09 | 1664 | 4250 | 1020 | 74.17 | 1840 | Peerless
Peerless | LC-10 | 1860 | 4804 | 1153 | 80.89 | 2030 | Peerless
Peerless | LC-11 | 2056 | 5367 | 1288 | 87.61 | 2220 | Peerless
Peerless | LC-12 | 2252 | 5917 | 1420 | 94.33 | 2410 | Peerless
Peerless | LCE-13 | 2464 | 6358 | 1526 | 101.05 | 2600 | Peerless
Peerless | LCE-14 | 2657 | 6875 | 1650 | 107.77 | 2790 | Peerless
Peerless | LCE-15 | 2850 | 7388 | 1773 | 114.49 | 2980 | Peerless
Peerless | LCE-16 | 3043 | 7908 | 1898 | 121.21 | 3170 | Peerless
Peerless | LCE-17 | 3236 | 8421 | 2021 | 127.93 | 3360 | Peerless
Peerless | LCE-18 | 3429 | 8938 | 2145 | 134.65 | 3550 | Peerless
Peerless | LCE-19 | 3622 | 9454 | 2269 | 141.37 | 3740 | Peerless
Peerless | LCE-20 | 3815 | 9971 | 2393 | 148.09 | 3930 | Peerless
Peerless | LCE-21 | 4027 | 10533 | 2528 | 154.81 | 4120 | Peerless
Peerless | LCE-22 | 4239 | 11096 | 2663 | 161.53 | 4310 | Peerless
Peerless | LCE-23 | 4451 | 11658 | 2798 | 168.25 | 4500 | Peerless
Peerless | LCE-24 | 4663 | 12217 | 2932 | 174.97 | 4690 | Peerless
Peerless | CC-03 | 375 | 308 | 963 | 33 | 1440.78 | Peerless
Peerless | CC-04 | 520 | 421 | 1316 | 41 | 1780.06 | Peerless
Peerless | CC-05 | 722 | 587 | 1725 | 49 | 2119.34 | Peerless
Peerless | CC-06 | 938 | 762 | 2382 | 56 | 2465.96 | Peerless
Peerless | CC-07 | 1140 | 924 | 2888 | 64 | 2805.24 | Peerless
Peerless | CC-08 | 1342 | 1087 | 3398 | 72 | 3144.52 | Peerless
Peerless | CC-09 | 1559 | 1262 | 3947 | 80 | 3482.8 | Peerless
Peerless | CC-10 | 1761 | 1424 | 4506 | 88 | 3821.08 | Peerless
Peerless | CC-11 | 1963 | 1587 | 5071 | 96 | 4159.36 | Peerless
Peerless | CC-12 | 2165 | 1750 | 5635 | 104 | 4498.64 | Peerless
Peerless | 211A-04 | 630 | 486 | 1521 | 15.1 | 2523 | Peerless
Peerless | 211A-05 | 840 | 664 | 2075 | 18.2 | 2900 | Peerless
Peerless | 211A-06 | 1050 | 830 | 2596 | 21.3 | 3450 | Peerless
Peerless | 211A-07 | 1260 | 995 | 3108 | 24.4 | 3900 | Peerless
Peerless | 211A-08 | 1470 | 1161 | 3629 | 27.5 | 4390 | Peerless
Peerless | 211A-09 | 1680 | 1327 | 4146 | 30.6 | 4875 | Peerless
Peerless | 211A-10 | 1890 | 1493 | 4667 | 33.7 | 5320 | Peerless
Peerless | 211A-11 | 2100 | 1659 | 5183 | 36.8 | 5900 | Peerless
Peerless | 211A-12 | 2310 | 1825 | 5704 | 39.9 | 6370 | Peerless
Peerless | 211A-13 | 2520 | 1958 | 6333 | 43 | 7150 | Peerless
Peerless | 211A-14 | 2730 | 2124 | 6871 | 46.1 | 7700 | Peerless
Peerless | 211A-15 | 2940 | 2290 | 7408 | 49.2 | 8250 | Peerless
Peerless | 211A-16 | 3150 | 2454 | 7938 | 52.3 | 8800 | Peerless
Peerless | 211A-17 | 3360 | 2621 | 8479 | 55.4 | 9350 | Peerless
Peerless | 211A-18 | 3570 | 2785 | 9008 | 58.5 | 9900 | Peerless
Peerless | 211A-19 | 3780 | 2952 | 9550 | 61.75 | 10450 | Peerless
Peerless | 211A-20 | 3990 | 3116 | 10079 | 65 | 11000 | Peerless
Peerless | 211A-21 | 4200 | 3280 | 10613 | 68.25 | 11550 | Peerless
Peerless | 211A-22 | 4410 | 3449 | 11158 | 71.5 | 12100 | Peerless
Peerless | 211A-23 | 4620 | 3599 | 11642 | 74.75 | 12650 | Peerless
Peerless | 211A-24 | 4830 | 3763 | 12175 | 78 | 13200 | Peerless
Peerless | 211A-25 | 5040 | 3931 | 12717 | 81.25 | 13750 | Peerless
Peerless | 211A-26 | 5250 | 4095 | 13246 | 84.5 | 14300 | Peerless
Peerless | 211A-27 | 5460 | 4259 | 13779 | 87.75 | 14850 | Peerless
Peerless | 211A-28 | 5670 | 4428 | 14325 | 91 | 15400 | Peerless
Peerless | 211A-29 | 5880 | 4592 | 14854 | 94.25 | 15950 | Peerless
Peerless | 211A-30 | 6090 | 4756 | 15388 | 97.5 | 16500 | Peerless
Peerless | 211A-31 | 6300 | 4920 | 15917 | 100.75 | 17050 | Peerless
Peerless | 211A-32 | 6510 | 5084 | 16446 | 104 | 17600 | Peerless
Peerless | 211A-33 | 6720 | 5255 | 17000 | 107.25 | 18150 | Peerless
Peerless | 211A-34 | 6930 | 5419 | 17529 | 110.5 | 18700 | Peerless
Peerless | 211A-35 | 7140 | 5583 | 18063 | 113.75 | 19250 | Peerless
Peerless | 211A-36 | 7350 | 5748 | 18596 | 117 | 19800 | Peerless
Peerless | 211A-37 | 7560 | 5904 | 19100 | 120.25 | 20350 | Peerless
Peerless | EC(T)-e-03 | 105 | 92 | 288 | 14.16 | 570 | Peerless
Peerless | EC(T)-e-03 | 140 | 121 | 379 | 14.16 | 570 | Peerless
Peerless | EC(T)-e-04 | 175 | 152 | 475 | 17.28 | 710 | Peerless
Peerless | EC(T)-e-04 | 210 | 181 | 567 | 17.28 | 710 | Peerless
Peerless | EC(T)-e-05 | 245 | 213 | 667 | 20.4 | 840 | Peerless
Peerless | EC(T)-e-05 | 280 | 242 | 758 | 20.4 | 840 | Peerless
Peerless | EC(T)-05† | 336 | 279 | 874 | 20.4 | 840 | Peerless
Peerless | EC(T)-e-06† | 308 | 259 | 811 | 23.52 | 990 | Peerless
Peerless | EC(T)-e-06† | 336 | 282 | 883 | 23.52 | 990 | Peerless
Peerless | EC(T)-06† | 385 | 321 | 1006 | 23.52 | 990 | Peerless
Peerless | EC(T)-06† | 420 | 347 | 1087 | 23.52 | 990 | Peerless
Peerless | WBV-e-03-085-S | 119 | 104 | 325 | 12 | 584 | Peerless
Peerless | WBV-e-03-105-S | 147 | 127 | 396 | 12 | 584 | Peerless
Peerless | WBV-e-04-125-S | 175 | 152 | 475 | 14.87 | 685 | Peerless
Peerless | WBV-e-04-150-S | 210 | 180 | 563 | 14.87 | 685 | Peerless
Peerless | 63-03L | 88.5 | 74 | 233 | 9.3 | 465 | Peerless
Peerless | 63-03 | 118 | 98 | 308 | 9.3 | 465 | Peerless
Peerless | 63-04L | 147.5 | 123 | 383 | 10.8 | 576 | Peerless
Peerless | 63-04 | 177 | 147 | 458 | 10.8 | 576 | Peerless
Peerless | 63-05L | 206.5 | 171 | 533 | 12.4 | 700 | Peerless
Peerless | 63-05 | 236 | 196 | 613 | 12.4 | 700 | Peerless
Peerless | 63-06 | 287.5 | 238 | 746 | 13.9 | 812 | Peerless
Peerless | 63-x-03 | 100 | 82 | 258 | 7 | 480 | Peerless
Peerless | 63-x-04 | 150 | 124 | 388 | 9 | 595 | Peerless
Peerless | 63-x-05 | 200 | 165 | 517 | 11 | 725 | Peerless
Peerless | 63-x-06 | 250 | 206 | 646 | 13 | 840 | Peerless
Green Mountain | GMGS-75 | 75 | 62 | 195 | 1.8 | 297 | Green Mountain
Green Mountain | GMGS-112 | 112.5 | 91 | 283 | 2.7 | 368 | Green Mountain
Green Mountain | GMGS-150 | 150 | 122 | 383 | 3.7 | 440 | Green Mountain
Green Mountain | GMGS-187 | 187.5 | 153 | 479 | 4.7 | 512 | Green Mountain
Green Mountain | GMGS-225 | 225 | 183 | 570 | 5.7 | 584 | Green Mountain
Green Mountain | GMGS-262 | 262.5 | 214 | 670 | 6.7 | 659 | Green Mountain
Green Mountain | GMGS-299 | 299 | 245 | 766 | 7.7 | 736 | Green Mountain

## Calculations (hidden)
Schd 40 Pipe stats
| ID(in) | Area(ft2) | BTU/ft @ 210°F | linear ft3/ft | Lb/ft | Supply BTU Horizontal Runout | Return BTU Return Riser | Dry Return BTU |  | List generator | Trap Status
1/2 | 0.662 | 0.0023903 | 82 | 0.0013657 | 0.851 | 0 | 0 | 0 |  |  | Failed-Closed
3/4 | 0.824 | 0.0037032 | 100 | 0.0030671 | 1.131 | 6720 | 46080 | 98880 | 3/4 | 1 | Failed-Open
1 | 1.049 | 0.0060018 | 123 | 0.0054572 | 1.679 | 13440 | 108480 | 208320 | 1 | 2 | Operational
1 1/4 | 1.38 | 0.010387 | 152 | 0.0085069 | 2.273 | 25920 | 238080 | 326400 | 1 1/4 | 3
1 1/2 | 1.61 | 0.014138 | 173 | 0.012269 | 2.718 | 40320 | 360000 | 710400 | 1 1/2 | 4
2 | 2.067 | 0.023303 | 212 | 0.021817 | 3.653 | 86880 | 720000 | 1180800 | 2 | 5
2 1/2 | 2.469 | 0.033248 | 252 | 0.034086 | 5.793 | 126720 |  | 2160000 | 2 1/2 | 6
3 | 3.068 | 0.051338 | 303 | 0.049074 | 7.576 | 192000 |  | 3100800 | 3 | 7
3 1/2 | 3.548 | 0.068659 | 342 | 0.068171 | 9.183 | 276480 |  | 4636800 | 3 1/2 | 8
4 | 4.026 | 0.088405 | 381 | 0.087269 | 10.79 | 408800 |  |  | 4 | 9
5 | 5.047 | 0.13893 | 464 | 0.13634 | 14.882 | 756480 |  |  | 5 | 10
6 | 6.065 | 0.20063 | 546 | 0.19635 | 18.974 |  |  |  | 6
6 | 6.065 | 0.20063 | 546 | 0.19635 | 18.974 |  |  |  | 6
5 | 5.047 | 0.13893 | 464 | 0.13634 | 14.882 | 756480 |  |  | 5
4 | 4.026 | 0.088405 | 381 | 0.087269 | 10.79 | 408800 |  |  | 4
3 1/2 | 3.548 | 0.068659 | 342 | 0.068171 | 9.183 | 276480 |  | 4636800 | 3 1/2
3 | 3.068 | 0.051338 | 303 | 0.049074 | 7.576 | 192000 |  | 3100800 | 3
2 1/2 | 2.469 | 0.033248 | 252 | 0.034086 | 5.793 | 126720 |  | 2160000 | 2 1/2
2 | 2.067 | 0.023303 | 212 | 0.021817 | 3.653 | 86880 | 720000 | 1180800 | 2
1 1/2 | 1.61 | 0.014138 | 173 | 0.012269 | 2.718 | 40320 | 360000 | 710400 | 1 1/2
1 1/4 | 1.38 | 0.010387 | 152 | 0.0085069 | 2.273 | 25920 | 238080 | 326400 | 1 1/4
1 | 1.049 | 0.0060018 | 123 | 0.0054572 | 1.679 | 13440 | 108480 | 208320 | 1
3/4 | 0.824 | 0.0037032 | 100 | 0.0030671 | 1.131 | 6720 | 46080 | 98880 | 3/4
1/2 | 0.662 | 0.0023903 | 82 | 0.0013657 | 0.851 | 0

## SteamProperties (hidden)
Gauge Pressure | Temperature | Specific Volume Saturated Vapor | Enthalpy
(psig) | (oF) | (ft3/lb) | Saturated Liquid | Evaporated | Saturated Vapor
PSI | F | ft3/lb | (Btu/lb) | (Btu/lb) | (Btu/lb)
-2.456 | 203 | 31.8 | 171 | 976 | 1147 |  | 0.039683 | 1 | 0.92016
0 | 212 | 26.8 | 180 | 970 | 1150 |  | 0.042553 | 2 | 2.0884
1 | 215 | 25.2 | 183 | 968 | 1151
2 | 219 | 23.5 | 187 | 966 | 1153
3 | 222 | 22.3 | 190 | 964 | 1154
4 | 224 | 21.4 | 192 | 962 | 1154
5 | 227 | 20.1 | 195 | 960 | 1155
6 | 230 | 19.4 | 198 | 959 | 1157
Pipe Size | BTU/linear ft | [7 empty] | Branch Supply List | Supply Line List
| 100°F | 120°F | 150°F | 180°F | 210°F | 240°F | in3/ft | ID(in)
1/2 | 13 | 22 | 40 | 60 | 82 | 106 | 2.36 | 0.622 | AA | A
3/4 | 15 | 27 | 50 | 74 | 100 | 131 | 5.3 | 0.824 | BB | B
1 | 19 | 34 | 61 | 90 | 123 | 160 | 9.43 | 1.049 | CC | C
1 1/4 | 23 | 42 | 75 | 111 | 152 | 198 | 14.7 | 1.38 | DD | D
1 1/2 | 27 | 48 | 85 | 126 | 173 | 224 | 21.2 | 1.61 | EE | E
2 | 33 | 59 | 104 | 154 | 212 | 275 | 37.7 | 2.067 | FF | F
2 1/2 | 39 | 70 | 123 | 184 | 252 | 327 | 58.9 | 2.469 | GG | G
3 | 46 | 84 | 148 | 221 | 303 | 393 | 84.8 | 3.068 | HH | H
3 1/2 | 52 | 95 | 168 | 250 | 342 | 444 | 117.8 | 3.548 | II | I
4 | 59 | 106 | 187 | 278 | 381 | 496 | 150.8 | 4.026 | JJ
5 | 71 | 129 | 227 | 339 | 464 | 603 | 235.6 | 5.047 | KK
6 | 84 | 151 | 267 | 398 | 546 | 709 | 339.3 | 6.065 | LL
8 | 107 | 194 | 341 | 509 | 697 | 906
10 | 132 | 238 | 420 | 626 | 857 | 1114
12 | 154 | 279 | 491 | 732 | 1003 | 1305
14 | 181 | 326 | 575 | 856 | 1173 | 1527
16 | 203 | 366 | 644 | 960 | 1314 | 1711
18 | 214 | 385 | 678 | 1011 | 1385 | 1802
20 | 236 | 426 | 748 | 1115 | 1529 | 1990
Pressur Drop