## MainSheet
Input | BOILER CALCULATIONS |  |  | STEAM MAINS CALCULATIONS |  | VENT CALCULATIONS
Output | Manufacturer Selection | Burnham |  | Riser Size(Schd40) | 2 1/2 | Main Vol(ft3) | 4.9074
| Boiler Selection | STMX299 |  | Riser Count | 2 | Radiator Vol(ft3) | 74.25
| Gross BTU/HR | 246000 |  | Main Diameter(Schd40) | 3 | Upfeed Vol(ft3) | 5.2788
| Water@Waterline(gal) | 15.6 |  | Main Length(ft) | 100 | Total Vol(ft3) | 84.4363
| Operating Pressure(PSIG) | 0.16 |  | Riser Velocity(fps) | 28.1746 | Total Rad Vent(cfm) | 18.06
| Section Weight(lbs) | 881 |  | Main Velocity | 36.4938 | Main Vent | Gorton #2
| Enthalpy(BTU/LB) | 968.6656 |  | Main end pressure(psig) | 0.11032 | Main Vent Count | 3
| Steam Density(lb/ft3) | 0.037653 |  | Main Instulation | 1" | Main Vent Cap(cfm) | 6.6
| Steam Rate(Lb/HR) | 253.9576 |  |  |  | Time to Vent(min) | 12.7934
| Time to Steam(min) | 9.1347 |  |  |  | Return Size | 1
| Boiler Duty Cycle | 89.25% |  |  |  | Return Length | 40
| RADIATION CALCULATIONS |  |  | FAILED TRAP CALCULATIONS
| Radiators(BTU/HR) | 212160 | 275808 | Steam Pass thru(Lb/Hr) | 4.6113
| Radiator Condensate(lbs/hr) | 212.7984 | 318240 | BTU/Hr to Condense | 4472.9633
| Upfeed(BTU/HR) | 5474.8509 |  | Lost Steam(Lb/Hr) | 0
| Upfeed Condensate(lb/hr) | 5.6442 |  | Lost Heat(BTU/HR) | 0
| Main Radiation(BTU/HR) | 1910.8108
| Main Condensate(lb/hr) | 2.1689
| Total Radiation(BTU/HR) | 219545.6618
| Total condensate(lb/hr) | 220.6115
| Min Radiator Pressure(psig) | 0.10045
| Init BTU to Heat Pipes(BTU) | 16748.8289
| Init BTU to Heat Radiators(BTU) | 124156.032
| Init Time to heat Metal(min) | 34.367
| Time to Steady State(min) | 56.2951
| Return Max Radiation(BTU/HR) | 4920
| Initial Warm Up Condensate(Lbs) | 145.2627
| Time to Warm Metal(Min) | 34.367

## Radiators
Heat Load(%) | Radiator Type | Height(In) | Cols/Tubes/(WxL) | Sections | Upfeed Length(ft) | Upfeed Insulation | Vent/Trap Type | Trap Status | Orifice D(in) | EDR Sqft | EDR Ideal | Btu/hr | Vent Capacity(3oz) | Radiator Vol(ft3) | Supply Pipe Size | Radiator Pressure(PSI) | Condensate(lb/hr) | Pipe Radiation(BTU/hr) | Pipe Volume(ft3) | Pipe Condensate(lb/hr) | Radiator Weight(lbs) | Pipe weight(lbs) | Failed Open Trap Steam Flow(lb/hr) | Total BTUs Radiation | Total EDR | Min PSI | Total Steam Pass Through(lb/hr)
100% | Tube | 37 | 5 | 13 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.14724 | 65 | 65 | 15600 | 0.86 | 0.845 | 1 1/4 | 0.10895 | 15.6469 | 139.541 | 0.068056 | 0.14386 | 455 | 18.184 | 0.22229 | 217634.8509 | 906.8119 | 0.10045 | 4.6113
| Tube | 37 | 5 | 7 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.12535 | 35 | 35 | 8400 | 0.86 | 0.455 | 1 | 0.10841 | 8.4253 | 109.3333 | 0.043657 | 0.11271 | 245 | 13.432 | 0.22173
| Tube | 37 | 5 | 5 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.13724 | 25 | 25 | 6000 | 0.86 | 0.325 | 3/4 | 0.10637 | 6.0181 | 294.6462 | 0.54537 | 0.30376 | 175 | 73.464 | 0.21964
| Tube | 37 | 5 | 6 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.16004 | 30 | 30 | 7200 | 0.86 | 0.39 | 1 | 0.10891 | 7.2217 | 109.3333 | 0.043657 | 0.11271 | 210 | 13.432 | 0.22225
| Tube | 20 | 7 | 10 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.20724 | 42.5 | 42.5 | 10200 | 0.86 | 0.5525 | 1 | 0.1075 | 10.2307 | 109.3333 | 0.043657 | 0.11271 | 297.5 | 13.432 | 0.2208
| Tube | 20 | 7 | 17 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.14724 | 72.25 | 72.25 | 17340 | 0.86 | 0.93925 | 1 1/4 | 0.10863 | 17.3922 | 139.541 | 0.068056 | 0.14386 | 505.75 | 18.184 | 0.22196
| Tube | 37 | 5 | 7 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.12535 | 35 | 35 | 8400 | 0.86 | 0.455 | 1 | 0.10841 | 8.4253 | 109.3333 | 0.043657 | 0.11271 | 245 | 13.432 | 0.22173
| Tube | 37 | 5 | 5 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.13724 | 25 | 25 | 6000 | 0.86 | 0.325 | 3/4 | 0.10637 | 6.0181 | 294.6462 | 0.54537 | 0.30376 | 175 | 73.464 | 0.21964
| Tube | 37 | 5 | 6 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.16004 | 30 | 30 | 7200 | 0.86 | 0.39 | 1 | 0.10891 | 7.2217 | 109.3333 | 0.043657 | 0.11271 | 210 | 13.432 | 0.22225
| Tube | 20 | 7 | 10 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.20724 | 42.5 | 42.5 | 10200 | 0.86 | 0.5525 | 1 | 0.1075 | 10.2307 | 109.3333 | 0.043657 | 0.11271 | 297.5 | 13.432 | 0.2208
| Tube | 20 | 7 | 17 | 8 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.14724 | 72.25 | 72.25 | 17340 | 0.86 | 0.93925 | 1 1/4 | 0.10863 | 17.3922 | 139.541 | 0.068056 | 0.14386 | 505.75 | 18.184 | 0.22196
| Tube | 37 | 5 | 7 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.12535 | 35 | 35 | 8400 | 0.86 | 0.455 | 1 | 0.10554 | 8.4253 | 273.3333 | 0.10914 | 0.28179 | 245 | 33.58 | 0.21878
| Tube | 37 | 5 | 5 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.13724 | 25 | 25 | 6000 | 0.86 | 0.325 | 3/4 | 0.10045 | 6.0181 | 736.6154 | 1.3634 | 0.7594 | 175 | 183.66 | 0.21345
| Tube | 37 | 5 | 6 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.16004 | 30 | 30 | 7200 | 0.86 | 0.39 | 1 | 0.10681 | 7.2217 | 273.3333 | 0.10914 | 0.28179 | 210 | 33.58 | 0.22009
| Tube | 20 | 7 | 10 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.20724 | 42.5 | 42.5 | 10200 | 0.86 | 0.5525 | 1 | 0.10328 | 10.2307 | 273.3333 | 0.10914 | 0.28179 | 297.5 | 33.58 | 0.21643
| Tube | 20 | 7 | 17 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.14724 | 72.25 | 72.25 | 17340 | 0.86 | 0.93925 | 1 1/4 | 0.10611 | 17.3922 | 348.8525 | 0.17014 | 0.35964 | 505.75 | 45.46 | 0.21937
| Tube | 37 | 5 | 7 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.12535 | 35 | 35 | 8400 | 0.86 | 0.455 | 1 | 0.10554 | 8.4253 | 273.3333 | 0.10914 | 0.28179 | 245 | 33.58 | 0.21878
| Tube | 37 | 5 | 5 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.13724 | 25 | 25 | 6000 | 0.86 | 0.325 | 3/4 | 0.10045 | 6.0181 | 736.6154 | 1.3634 | 0.7594 | 175 | 183.66 | 0.21345
| Tube | 37 | 5 | 6 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.16004 | 30 | 30 | 7200 | 0.86 | 0.39 | 1 | 0.10681 | 7.2217 | 273.3333 | 0.10914 | 0.28179 | 210 | 33.58 | 0.22009
| Tube | 20 | 7 | 10 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.20724 | 42.5 | 42.5 | 10200 | 0.86 | 0.5525 | 1 | 0.10328 | 10.2307 | 273.3333 | 0.10914 | 0.28179 | 297.5 | 33.58 | 0.21643
| Tube | 20 | 7 | 17 | 20 | 1/2" | Illinois 1/2" #1G | Failed-Open | 0.0087161 | 72.25 | 72.25 | 17340 | 0.86 | 0.93925 | 1 1/4 | 0.10611 | 17.3922 | 348.8525 | 0.17014 | 0.35964 | 505.75 | 45.46 | 0.21937
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0.0087161 | 0 | 0 | 0 | 0 | 0 | 1/2 | 0.11032 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Combustion Air
Based on IFGC 2021 |  | 1 Permanent Opening |  | 2 Permanent Opening
Rated Power Input(BTU/HR) | 299000 | Louver Type | Metal | Louver Type | Metal
Additional Power Input(BTU/HR) | 120000 | Raw(in2) | 186.2222 | Openining Setup | Vertical
Mechanical room volume(ft3) | 3000 | Square size(in) | 13.6463 | Raw(in2) | 139.6667
Required Volume(ft3) | 20950 | Adj for mech rm vol(in2) | 159.5556 | Square size(in) | 11.8181
|  | Adj square size(in) | 12.6315 | Adj for mech rm vol(in2) | 119.6667
|  |  |  | Adj square size(in) | 10.9392
Mechanical Air Intake
|  | CFM Required | 142.46

## TimeAnalysis (hidden)
| Main | Supplies | Radiators | Timestep(min) | Time(min) | BTU Output | ft3/hr gen | Main Venting(%) | Supply Venting(%) | Radiator Venting(%) | Total Venting | Main Heating | Supply Heating | Radiator Heating | Total Radiation(BTU/hr) | Condensate Gen(lb/hr) | Energy(BTUs) | Time | % Load
Volf(ft3) | 4.9074 | 5.2788 | 11.492 | 0.01 | 0 | 246000 | 396 | 0 |  |  | 0 | 0 |  |  |  | 0 |  | 0 | 0%
BTU Heat | 12586.7664 | 15646.9323 | 115987.872 |  | 0.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0%
Radiation(btu/hr) | 1910.8108 | 5474.8509 | 212160 |  | 0.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0%
TTH(min) | 3.0699 | 3.8163 | 28.2897 |  | 0.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0%
TTV(min) | 0.74355 | 0.79982 | 1.7412 |  | 0.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0%
[5 empty] | 0.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0%
[5 empty] | 0.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0%
[5 empty] | 0.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0%
Start Temp(f) |  |  |  |  | 0.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0%
70 |  |  |  |  | 0.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0%
[5 empty] | 0.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0%
Time to Hourly Output |  |  |  |  | 0.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0%
12.42 |  |  |  |  | 0.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0%
[5 empty] | 0.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0%
[5 empty] | 0.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0%
[5 empty] | 0.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0%
[5 empty] | 0.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0%
[5 empty] | 0.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0%
[5 empty] | 0.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0%
[5 empty] | 0.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0%
[5 empty] | 0.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0%
[5 empty] | 0.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0%
[5 empty] | 0.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0%
[5 empty] | 0.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0%
[5 empty] | 0.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0%
[5 empty] | 0.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0%
[5 empty] | 0.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0%
[5 empty] | 0.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0%
[5 empty] | 0.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0%
[5 empty] | 0.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 0%
[5 empty] | 0.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0%
[5 empty] | 0.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0%
[5 empty] | 0.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0%
[5 empty] | 0.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0%
[5 empty] | 0.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0%
[5 empty] | 0.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0%
[5 empty] | 0.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 0%
[5 empty] | 0.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 0%
[5 empty] | 0.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0%
[5 empty] | 0.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0%
[5 empty] | 0.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0%
[5 empty] | 0.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0%
[5 empty] | 0.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 0%
[5 empty] | 0.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0%
[5 empty] | 0.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0%
[5 empty] | 0.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0%
[5 empty] | 0.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 0%
[5 empty] | 0.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47 | 0%
[5 empty] | 0.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0%
[5 empty] | 0.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0%
[5 empty] | 0.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0%
[5 empty] | 0.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0%
[5 empty] | 0.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0%
[5 empty] | 0.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0%
[5 empty] | 0.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0%
[5 empty] | 0.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55 | 0%
[5 empty] | 0.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 0%
[5 empty] | 0.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0%
[5 empty] | 0.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0%
[5 empty] | 0.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59 | 0%
[5 empty] | 0.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0%
[5 empty] | 0.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0%
[5 empty] | 0.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0%
[5 empty] | 0.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0%
[5 empty] | 0.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0%
[5 empty] | 0.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0%
[5 empty] | 0.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 0%
[5 empty] | 0.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0%
[5 empty] | 0.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0%
[5 empty] | 0.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 0%
[5 empty] | 0.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0%
[5 empty] | 0.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0%
[5 empty] | 0.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0%
[5 empty] | 0.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 0%
[5 empty] | 0.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 0%
[5 empty] | 0.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0%
[5 empty] | 0.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 0%
[5 empty] | 0.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0%
[5 empty] | 0.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0%
[5 empty] | 0.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0%
[5 empty] | 0.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0%
[5 empty] | 0.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0%
[5 empty] | 0.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 0%
[5 empty] | 0.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0%
[5 empty] | 0.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0%
[5 empty] | 0.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0%
[5 empty] | 0.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0%
[5 empty] | 0.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87 | 0%
[5 empty] | 0.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0%
[5 empty] | 0.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0%
[5 empty] | 0.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0%
[5 empty] | 0.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0%
[5 empty] | 0.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 0%
[5 empty] | 0.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93 | 0%
[5 empty] | 0.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 0%
[5 empty] | 0.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0%
[5 empty] | 0.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0%
[5 empty] | 0.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | 0%
[5 empty] | 0.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0%
[5 empty] | 0.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0%
[5 empty] | 1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0%
[5 empty] | 1.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 0%
[5 empty] | 1.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0%
[5 empty] | 1.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03 | 0%
[5 empty] | 1.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0%
[5 empty] | 1.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0%
[5 empty] | 1.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 0%
[5 empty] | 1.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 0%
[5 empty] | 1.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0%
[5 empty] | 1.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 0%
[5 empty] | 1.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0%
[5 empty] | 1.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.11 | 0%
[5 empty] | 1.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0%
[5 empty] | 1.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.13 | 0%
[5 empty] | 1.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0%
[5 empty] | 1.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0%
[5 empty] | 1.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16 | 0%
[5 empty] | 1.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 0%
[5 empty] | 1.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 0%
[5 empty] | 1.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.19 | 0%
[5 empty] | 1.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0%
[5 empty] | 1.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 0%
[5 empty] | 1.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0%
[5 empty] | 1.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0%
[5 empty] | 1.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.24 | 0%
[5 empty] | 1.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 0%
[5 empty] | 1.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0%
[5 empty] | 1.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 0%
[5 empty] | 1.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 0%
[5 empty] | 1.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29 | 0%
[5 empty] | 1.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0%
[5 empty] | 1.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.31 | 0%
[5 empty] | 1.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.32 | 0%
[5 empty] | 1.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0%
[5 empty] | 1.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 0%
[5 empty] | 1.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.35 | 0%
[5 empty] | 1.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36 | 0%
[5 empty] | 1.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 0%
[5 empty] | 1.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 0%
[5 empty] | 1.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.39 | 0%
[5 empty] | 1.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0%
[5 empty] | 1.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.41 | 0%
[5 empty] | 1.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0%
[5 empty] | 1.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 0%
[5 empty] | 1.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 0%
[5 empty] | 1.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 0%
[5 empty] | 1.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.46 | 0%
[5 empty] | 1.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 0%
[5 empty] | 1.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 0%
[5 empty] | 1.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.49 | 0%
[5 empty] | 1.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0%
[5 empty] | 1.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 0%
[5 empty] | 1.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.52 | 0%
[5 empty] | 1.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.53 | 0%
[5 empty] | 1.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.54 | 0%
[5 empty] | 1.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 0%
[5 empty] | 1.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0%
[5 empty] | 1.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.57 | 0%
[5 empty] | 1.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0%
[5 empty] | 1.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.59 | 0%
[5 empty] | 1.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0%
[5 empty] | 1.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 0%
[5 empty] | 1.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 0%
[5 empty] | 1.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0%
[5 empty] | 1.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.64 | 0%
[5 empty] | 1.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 0%
[5 empty] | 1.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 0%
[5 empty] | 1.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 0%
[5 empty] | 1.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 0%
[5 empty] | 1.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.69 | 0%
[5 empty] | 1.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0%
[5 empty] | 1.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 0%
[5 empty] | 1.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 0%
[5 empty] | 1.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 0%
[5 empty] | 1.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 0%
[5 empty] | 1.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0%
[5 empty] | 1.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.76 | 0%
[5 empty] | 1.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.77 | 0%
[5 empty] | 1.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0%
[5 empty] | 1.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.79 | 0%
[5 empty] | 1.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0%
[5 empty] | 1.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.81 | 0%
[5 empty] | 1.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 0%
[5 empty] | 1.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.83 | 0%
[5 empty] | 1.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 0%
[5 empty] | 1.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.85 | 0%
[5 empty] | 1.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.86 | 0%
[5 empty] | 1.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 0%
[5 empty] | 1.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 0%
[5 empty] | 1.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.89 | 0%
[5 empty] | 1.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0%
[5 empty] | 1.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.91 | 0%
[5 empty] | 1.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 0%
[5 empty] | 1.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.93 | 0%
[5 empty] | 1.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 0%
[5 empty] | 1.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.95 | 0%
[5 empty] | 1.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 0%
[5 empty] | 1.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97 | 0%
[5 empty] | 1.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 0%
[5 empty] | 1.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.99 | 0%
[5 empty] | 2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0%
[5 empty] | 2.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | 0%
[5 empty] | 2.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 0%
[5 empty] | 2.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.03 | 0%
[5 empty] | 2.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 0%
[5 empty] | 2.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.05 | 0%
[5 empty] | 2.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 0%
[5 empty] | 2.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 0%
[5 empty] | 2.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0%
[5 empty] | 2.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 0%
[5 empty] | 2.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0%
[5 empty] | 2.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.11 | 0%
[5 empty] | 2.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0%
[5 empty] | 2.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0%
[5 empty] | 2.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.14 | 0%
[5 empty] | 2.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | 0%
[5 empty] | 2.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0%
[5 empty] | 2.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0%
[5 empty] | 2.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.18 | 0%
[5 empty] | 2.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.19 | 0%
[5 empty] | 2.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0%
[5 empty] | 2.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.21 | 0%
[5 empty] | 2.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 0%
[5 empty] | 2.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.23 | 0%
[5 empty] | 2.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 0%
[5 empty] | 2.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 0%
[5 empty] | 2.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | 0%
[5 empty] | 2.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.27 | 0%
[5 empty] | 2.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.28 | 0%
[5 empty] | 2.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.29 | 0%
[5 empty] | 2.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0%
[5 empty] | 2.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 0%
[5 empty] | 2.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 0%
[5 empty] | 2.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.33 | 0%
[5 empty] | 2.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.34 | 0%
[5 empty] | 2.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.35 | 0%
[5 empty] | 2.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.36 | 0%
[5 empty] | 2.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.37 | 0%
[5 empty] | 2.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0%
[5 empty] | 2.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.39 | 0%
[5 empty] | 2.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0%
[5 empty] | 2.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.41 | 0%
[5 empty] | 2.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 0%
[5 empty] | 2.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.43 | 0%
[5 empty] | 2.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.44 | 0%
[5 empty] | 2.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.45 | 0%
[5 empty] | 2.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.46 | 0%
[5 empty] | 2.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 0%
[5 empty] | 2.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.48 | 0%
[5 empty] | 2.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.49 | 0%
[5 empty] | 2.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0%
[5 empty] | 2.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 0%
[5 empty] | 2.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.52 | 0%
[5 empty] | 2.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 0%
[5 empty] | 2.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 0%
[5 empty] | 2.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.55 | 0%
[5 empty] | 2.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 0%
[5 empty] | 2.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57 | 0%
[5 empty] | 2.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58 | 0%
[5 empty] | 2.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.59 | 0%
[5 empty] | 2.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0%
[5 empty] | 2.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.61 | 0%
[5 empty] | 2.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 0%
[5 empty] | 2.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 0%
[5 empty] | 2.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.64 | 0%
[5 empty] | 2.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.65 | 0%
[5 empty] | 2.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.66 | 0%
[5 empty] | 2.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.67 | 0%
[5 empty] | 2.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.68 | 0%
[5 empty] | 2.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 0%
[5 empty] | 2.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0%
[5 empty] | 2.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 0%
[5 empty] | 2.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 0%
[5 empty] | 2.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.73 | 0%
[5 empty] | 2.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 0%
[5 empty] | 2.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.75 | 0%
[5 empty] | 2.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.76 | 0%
[5 empty] | 2.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.77 | 0%
[5 empty] | 2.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.78 | 0%
[5 empty] | 2.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.79 | 0%
[5 empty] | 2.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0%
[5 empty] | 2.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.81 | 0%
[5 empty] | 2.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.82 | 0%
[5 empty] | 2.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.83 | 0%
[5 empty] | 2.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.84 | 0%
[5 empty] | 2.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 0%
[5 empty] | 2.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 0%
[5 empty] | 2.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.87 | 0%
[5 empty] | 2.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 0%
[5 empty] | 2.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 0%
[5 empty] | 2.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0%
[5 empty] | 2.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.91 | 0%
[5 empty] | 2.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.92 | 0%
[5 empty] | 2.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.93 | 0%
[5 empty] | 2.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 0%
[5 empty] | 2.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 0%
[5 empty] | 2.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.96 | 0%
[5 empty] | 2.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.97 | 0%
[5 empty] | 2.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.98 | 0%
[5 empty] | 2.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.99 | 0%
[5 empty] | 3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0%
[5 empty] | 3.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 0%
[5 empty] | 3.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 0%
[5 empty] | 3.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.03 | 0%
[5 empty] | 3.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.04 | 0%
[5 empty] | 3.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.05 | 0%
[5 empty] | 3.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.06 | 0%
[5 empty] | 3.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 0%
[5 empty] | 3.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 0%
[5 empty] | 3.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.09 | 0%
[5 empty] | 3.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0%
[5 empty] | 3.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.11 | 0%
[5 empty] | 3.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 0%
[5 empty] | 3.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 0%
[5 empty] | 3.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 0%
[5 empty] | 3.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 0%
[5 empty] | 3.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 0%
[5 empty] | 3.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 0%
[5 empty] | 3.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.18 | 0%
[5 empty] | 3.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.19 | 0%
[5 empty] | 3.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0%
[5 empty] | 3.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.21 | 0%
[5 empty] | 3.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 0%
[5 empty] | 3.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.23 | 0%
[5 empty] | 3.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.24 | 0%
[5 empty] | 3.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 0%
[5 empty] | 3.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.26 | 0%
[5 empty] | 3.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 0%
[5 empty] | 3.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 0%
[5 empty] | 3.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.29 | 0%
[5 empty] | 3.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0%
[5 empty] | 3.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 0%
[5 empty] | 3.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.32 | 0%
[5 empty] | 3.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.33 | 0%
[5 empty] | 3.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.34 | 0%
[5 empty] | 3.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.35 | 0%
[5 empty] | 3.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.36 | 0%
[5 empty] | 3.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 0%
[5 empty] | 3.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.38 | 0%
[5 empty] | 3.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.39 | 0%
[5 empty] | 3.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0%
[5 empty] | 3.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.41 | 0%
[5 empty] | 3.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.42 | 0%
[5 empty] | 3.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.43 | 0%
[5 empty] | 3.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.44 | 0%
[5 empty] | 3.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.45 | 0%
[5 empty] | 3.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.46 | 0%
[5 empty] | 3.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.47 | 0%
[5 empty] | 3.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.48 | 0%
[5 empty] | 3.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.49 | 0%
[5 empty] | 3.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0%
[5 empty] | 3.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 0%
[5 empty] | 3.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.52 | 0%
[5 empty] | 3.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.53 | 0%
[5 empty] | 3.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.54 | 0%
[5 empty] | 3.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.55 | 0%
[5 empty] | 3.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56 | 0%
[5 empty] | 3.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.57 | 0%
[5 empty] | 3.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 0%
[5 empty] | 3.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.59 | 0%
[5 empty] | 3.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0%
[5 empty] | 3.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.61 | 0%
[5 empty] | 3.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.62 | 0%
[5 empty] | 3.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.63 | 0%
[5 empty] | 3.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.64 | 0%
[5 empty] | 3.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.65 | 0%
[5 empty] | 3.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.66 | 0%
[5 empty] | 3.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.67 | 0%
[5 empty] | 3.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.68 | 0%
[5 empty] | 3.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 0%
[5 empty] | 3.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0%
[5 empty] | 3.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.71 | 0%
[5 empty] | 3.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0%
[5 empty] | 3.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.73 | 0%
[5 empty] | 3.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.74 | 0%
[5 empty] | 3.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.75 | 0%
[5 empty] | 3.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.76 | 0%
[5 empty] | 3.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.77 | 0%
[5 empty] | 3.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.78 | 0%
[5 empty] | 3.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.79 | 0%
[5 empty] | 3.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0%
[5 empty] | 3.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.81 | 0%
[5 empty] | 3.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.82 | 0%
[5 empty] | 3.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 0%
[5 empty] | 3.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.84 | 0%
[5 empty] | 3.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.85 | 0%
[5 empty] | 3.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 0%
[5 empty] | 3.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.87 | 0%
[5 empty] | 3.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.88 | 0%
[5 empty] | 3.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.89 | 0%
[5 empty] | 3.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0%
[5 empty] | 3.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.91 | 0%
[5 empty] | 3.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 0%
[5 empty] | 3.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.93 | 0%
[5 empty] | 3.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.94 | 0%
[5 empty] | 3.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.95 | 0%
[5 empty] | 3.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.96 | 0%
[5 empty] | 3.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.97 | 0%
[5 empty] | 3.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.98 | 0%
[5 empty] | 3.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 0%
[5 empty] | 4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0%
[5 empty] | 4.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.01 | 0%
[5 empty] | 4.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.02 | 0%
[5 empty] | 4.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.03 | 0%
[5 empty] | 4.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 0%
[5 empty] | 4.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.05 | 0%
[5 empty] | 4.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0%
[5 empty] | 4.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.07 | 0%
[5 empty] | 4.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.08 | 0%
[5 empty] | 4.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.09 | 0%
[5 empty] | 4.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0%
[5 empty] | 4.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.11 | 0%
[5 empty] | 4.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.12 | 0%
[5 empty] | 4.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.13 | 0%
[5 empty] | 4.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.14 | 0%
[5 empty] | 4.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.15 | 0%
[5 empty] | 4.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.16 | 0%
[5 empty] | 4.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.17 | 0%
[5 empty] | 4.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.18 | 0%
[5 empty] | 4.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.19 | 0%
[5 empty] | 4.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0%
[5 empty] | 4.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.21 | 0%
[5 empty] | 4.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.22 | 0%
[5 empty] | 4.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.23 | 0%
[5 empty] | 4.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.24 | 0%
[5 empty] | 4.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.25 | 0%
[5 empty] | 4.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.26 | 0%
[5 empty] | 4.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.27 | 0%
[5 empty] | 4.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.28 | 0%
[5 empty] | 4.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.29 | 0%
[5 empty] | 4.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0%
[5 empty] | 4.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.31 | 0%
[5 empty] | 4.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.32 | 0%
[5 empty] | 4.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.33 | 0%
[5 empty] | 4.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.34 | 0%
[5 empty] | 4.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.35 | 0%
[5 empty] | 4.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.36 | 0%
[5 empty] | 4.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.37 | 0%
[5 empty] | 4.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.38 | 0%
[5 empty] | 4.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.39 | 0%
[5 empty] | 4.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0%
[5 empty] | 4.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.41 | 0%
[5 empty] | 4.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.42 | 0%
[5 empty] | 4.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.43 | 0%
[5 empty] | 4.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.44 | 0%
[5 empty] | 4.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.45 | 0%
[5 empty] | 4.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.46 | 0%
[5 empty] | 4.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.47 | 0%
[5 empty] | 4.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.48 | 0%
[5 empty] | 4.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 0%
[5 empty] | 4.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0%
[5 empty] | 4.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.51 | 0%
[5 empty] | 4.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.52 | 0%
[5 empty] | 4.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.53 | 0%
[5 empty] | 4.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.54 | 0%
[5 empty] | 4.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.55 | 0%
[5 empty] | 4.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.56 | 0%
[5 empty] | 4.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.57 | 0%
[5 empty] | 4.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.58 | 0%
[5 empty] | 4.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.59 | 0%
[5 empty] | 4.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0%
[5 empty] | 4.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.61 | 0%
[5 empty] | 4.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.62 | 0%
[5 empty] | 4.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.63 | 0%
[5 empty] | 4.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 0%
[5 empty] | 4.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.65 | 0%
[5 empty] | 4.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.66 | 0%
[5 empty] | 4.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.67 | 0%
[5 empty] | 4.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.68 | 0%
[5 empty] | 4.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 0%
[5 empty] | 4.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0%
[5 empty] | 4.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.71 | 0%
[5 empty] | 4.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.72 | 0%
[5 empty] | 4.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 0%
[5 empty] | 4.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.74 | 0%
[5 empty] | 4.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.75 | 0%
[5 empty] | 4.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.76 | 0%
[5 empty] | 4.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.77 | 0%
[5 empty] | 4.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.78 | 0%
[5 empty] | 4.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.79 | 0%
[5 empty] | 4.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0%
[5 empty] | 4.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.81 | 0%
[5 empty] | 4.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.82 | 0%
[5 empty] | 4.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.83 | 0%
[5 empty] | 4.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.84 | 0%
[5 empty] | 4.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.85 | 0%
[5 empty] | 4.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.86 | 0%
[5 empty] | 4.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.87 | 0%
[5 empty] | 4.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.88 | 0%
[5 empty] | 4.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.89 | 0%
[5 empty] | 4.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0%
[5 empty] | 4.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.91 | 0%
[5 empty] | 4.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.92 | 0%
[5 empty] | 4.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.93 | 0%
[5 empty] | 4.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.94 | 0%
[5 empty] | 4.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 0%
[5 empty] | 4.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | 0%
[5 empty] | 4.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.97 | 0%
[5 empty] | 4.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.98 | 0%
[5 empty] | 4.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.99 | 0%
[5 empty] | 5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0%
[5 empty] | 5.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.01 | 0%
[5 empty] | 5.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.02 | 0%
[5 empty] | 5.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.03 | 0%
[5 empty] | 5.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.04 | 0%
[5 empty] | 5.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.05 | 0%
[5 empty] | 5.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.06 | 0%
[5 empty] | 5.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.07 | 0%
[5 empty] | 5.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.08 | 0%
[5 empty] | 5.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.09 | 0%
[5 empty] | 5.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0%
[5 empty] | 5.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 0%
[5 empty] | 5.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.12 | 0%
[5 empty] | 5.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.13 | 0%
[5 empty] | 5.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.14 | 0%
[5 empty] | 5.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.15 | 0%
[5 empty] | 5.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.16 | 0%
[5 empty] | 5.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.17 | 0%
[5 empty] | 5.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.18 | 0%
[5 empty] | 5.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.19 | 0%
[5 empty] | 5.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0%
[5 empty] | 5.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.21 | 0%
[5 empty] | 5.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.22 | 0%
[5 empty] | 5.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.23 | 0%
[5 empty] | 5.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.24 | 0%
[5 empty] | 5.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.25 | 0%
[5 empty] | 5.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.26 | 0%
[5 empty] | 5.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.27 | 0%
[5 empty] | 5.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.28 | 0%
[5 empty] | 5.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.29 | 0%
[5 empty] | 5.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0%
[5 empty] | 5.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.31 | 0%
[5 empty] | 5.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.32 | 0%
[5 empty] | 5.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.33 | 0%
[5 empty] | 5.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.34 | 0%
[5 empty] | 5.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.35 | 0%
[5 empty] | 5.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.36 | 0%
[5 empty] | 5.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.37 | 0%
[5 empty] | 5.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.38 | 0%
[5 empty] | 5.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.39 | 0%
[5 empty] | 5.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0%
[5 empty] | 5.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.41 | 0%
[5 empty] | 5.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.42 | 0%
[5 empty] | 5.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.43 | 0%
[5 empty] | 5.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.44 | 0%
[5 empty] | 5.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.45 | 0%
[5 empty] | 5.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.46 | 0%
[5 empty] | 5.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.47 | 0%
[5 empty] | 5.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.48 | 0%
[5 empty] | 5.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.49 | 0%
[5 empty] | 5.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0%
[5 empty] | 5.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.51 | 0%
[5 empty] | 5.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.52 | 0%
[5 empty] | 5.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.53 | 0%
[5 empty] | 5.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.54 | 0%
[5 empty] | 5.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.55 | 0%
[5 empty] | 5.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.56 | 0%
[5 empty] | 5.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.57 | 0%
[5 empty] | 5.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.58 | 0%
[5 empty] | 5.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.59 | 0%
[5 empty] | 5.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0%
[5 empty] | 5.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.61 | 0%
[5 empty] | 5.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.62 | 0%
[5 empty] | 5.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.63 | 0%
[5 empty] | 5.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.64 | 0%
[5 empty] | 5.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.65 | 0%
[5 empty] | 5.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.66 | 0%
[5 empty] | 5.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.67 | 0%
[5 empty] | 5.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.68 | 0%
[5 empty] | 5.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.69 | 0%
[5 empty] | 5.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 0%
[5 empty] | 5.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.71 | 0%
[5 empty] | 5.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.72 | 0%
[5 empty] | 5.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.73 | 0%
[5 empty] | 5.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.74 | 0%
[5 empty] | 5.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.75 | 0%
[5 empty] | 5.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.76 | 0%
[5 empty] | 5.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.77 | 0%
[5 empty] | 5.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.78 | 0%
[5 empty] | 5.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.79 | 0%
[5 empty] | 5.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0%
[5 empty] | 5.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.81 | 0%
[5 empty] | 5.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.82 | 0%
[5 empty] | 5.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.83 | 0%
[5 empty] | 5.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.84 | 0%
[5 empty] | 5.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.85 | 0%
[5 empty] | 5.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.86 | 0%
[5 empty] | 5.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.87 | 0%
[5 empty] | 5.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.88 | 0%
[5 empty] | 5.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.89 | 0%
[5 empty] | 5.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0%
[5 empty] | 5.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.91 | 0%
[5 empty] | 5.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.92 | 0%
[5 empty] | 5.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.93 | 0%
[5 empty] | 5.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 0%
[5 empty] | 5.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.95 | 0%
[5 empty] | 5.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.96 | 0%
[5 empty] | 5.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.97 | 0%
[5 empty] | 5.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.98 | 0%
[5 empty] | 5.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.99 | 0%
[5 empty] | 6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0%
[5 empty] | 6.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.01 | 0%
[5 empty] | 6.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.02 | 0%
[5 empty] | 6.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.03 | 0%
[5 empty] | 6.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.04 | 0%
[5 empty] | 6.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.05 | 0%
[5 empty] | 6.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.06 | 0%
[5 empty] | 6.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.07 | 0%
[5 empty] | 6.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.08 | 0%
[5 empty] | 6.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.09 | 0%
[5 empty] | 6.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 0%
[5 empty] | 6.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.11 | 0%
[5 empty] | 6.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.12 | 0%
[5 empty] | 6.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.13 | 0%
[5 empty] | 6.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.14 | 0%
[5 empty] | 6.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.15 | 0%
[5 empty] | 6.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.16 | 0%
[5 empty] | 6.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.17 | 0%
[5 empty] | 6.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18 | 0%
[5 empty] | 6.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.19 | 0%
[5 empty] | 6.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 0%
[5 empty] | 6.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.21 | 0%
[5 empty] | 6.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.22 | 0%
[5 empty] | 6.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.23 | 0%
[5 empty] | 6.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 0%
[5 empty] | 6.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 0%
[5 empty] | 6.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.26 | 0%
[5 empty] | 6.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.27 | 0%
[5 empty] | 6.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.28 | 0%
[5 empty] | 6.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.29 | 0%
[5 empty] | 6.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 0%
[5 empty] | 6.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.31 | 0%
[5 empty] | 6.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.32 | 0%
[5 empty] | 6.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.33 | 0%
[5 empty] | 6.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0%
[5 empty] | 6.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.35 | 0%
[5 empty] | 6.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.36 | 0%
[5 empty] | 6.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.37 | 0%
[5 empty] | 6.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.38 | 0%
[5 empty] | 6.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.39 | 0%
[5 empty] | 6.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0%
[5 empty] | 6.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.41 | 0%
[5 empty] | 6.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.42 | 0%
[5 empty] | 6.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.43 | 0%
[5 empty] | 6.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.44 | 0%
[5 empty] | 6.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.45 | 0%
[5 empty] | 6.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.46 | 0%
[5 empty] | 6.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.47 | 0%
[5 empty] | 6.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.48 | 0%
[5 empty] | 6.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.49 | 0%
[5 empty] | 6.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 0%
[5 empty] | 6.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.51 | 0%
[5 empty] | 6.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.52 | 0%
[5 empty] | 6.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.53 | 0%
[5 empty] | 6.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.54 | 0%
[5 empty] | 6.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.55 | 0%
[5 empty] | 6.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.56 | 0%
[5 empty] | 6.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.57 | 0%
[5 empty] | 6.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.58 | 0%
[5 empty] | 6.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.59 | 0%
[5 empty] | 6.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0%
[5 empty] | 6.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.61 | 0%
[5 empty] | 6.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.62 | 0%
[5 empty] | 6.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.63 | 0%
[5 empty] | 6.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.64 | 0%
[5 empty] | 6.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.65 | 0%
[5 empty] | 6.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.66 | 0%
[5 empty] | 6.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.67 | 0%
[5 empty] | 6.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.68 | 0%
[5 empty] | 6.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.69 | 0%
[5 empty] | 6.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0%
[5 empty] | 6.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.71 | 0%
[5 empty] | 6.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 0%
[5 empty] | 6.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.73 | 0%
[5 empty] | 6.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.74 | 0%
[5 empty] | 6.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.75 | 0%
[5 empty] | 6.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.76 | 0%
[5 empty] | 6.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.77 | 0%
[5 empty] | 6.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.78 | 0%
[5 empty] | 6.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.79 | 0%
[5 empty] | 6.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0%
[5 empty] | 6.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.81 | 0%
[5 empty] | 6.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.82 | 0%
[5 empty] | 6.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.83 | 0%
[5 empty] | 6.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 0%
[5 empty] | 6.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.85 | 0%
[5 empty] | 6.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.86 | 0%
[5 empty] | 6.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.87 | 0%
[5 empty] | 6.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.88 | 0%
[5 empty] | 6.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.89 | 0%
[5 empty] | 6.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0%
[5 empty] | 6.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.91 | 0%
[5 empty] | 6.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.92 | 0%
[5 empty] | 6.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.93 | 0%
[5 empty] | 6.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.94 | 0%
[5 empty] | 6.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.95 | 0%
[5 empty] | 6.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.96 | 0%
[5 empty] | 6.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.97 | 0%
[5 empty] | 6.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.98 | 0%
[5 empty] | 6.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.99 | 0%
[5 empty] | 7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0%
[5 empty] | 7.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.01 | 0%
[5 empty] | 7.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.02 | 0%
[5 empty] | 7.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.03 | 0%
[5 empty] | 7.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.04 | 0%
[5 empty] | 7.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.05 | 0%
[5 empty] | 7.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.06 | 0%
[5 empty] | 7.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.07 | 0%
[5 empty] | 7.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.08 | 0%
[5 empty] | 7.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.09 | 0%
[5 empty] | 7.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0%
[5 empty] | 7.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.11 | 0%
[5 empty] | 7.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.12 | 0%
[5 empty] | 7.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.13 | 0%
[5 empty] | 7.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.14 | 0%
[5 empty] | 7.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.15 | 0%
[5 empty] | 7.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.16 | 0%
[5 empty] | 7.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.17 | 0%
[5 empty] | 7.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.18 | 0%
[5 empty] | 7.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.19 | 0%
[5 empty] | 7.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 0%
[5 empty] | 7.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.21 | 0%
[5 empty] | 7.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.22 | 0%
[5 empty] | 7.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.23 | 0%
[5 empty] | 7.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0%
[5 empty] | 7.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.25 | 0%
[5 empty] | 7.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.26 | 0%
[5 empty] | 7.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.27 | 0%
[5 empty] | 7.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.28 | 0%
[5 empty] | 7.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.29 | 0%
[5 empty] | 7.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 0%
[5 empty] | 7.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.31 | 0%
[5 empty] | 7.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.32 | 0%
[5 empty] | 7.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.33 | 0%
[5 empty] | 7.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.34 | 0%
[5 empty] | 7.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.35 | 0%
[5 empty] | 7.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.36 | 0%
[5 empty] | 7.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.37 | 0%
[5 empty] | 7.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.38 | 0%
[5 empty] | 7.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.39 | 0%
[5 empty] | 7.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0%
[5 empty] | 7.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.41 | 0%
[5 empty] | 7.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.42 | 0%
[5 empty] | 7.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.43 | 0%
[5 empty] | 7.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.44 | 0%
[5 empty] | 7.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.45 | 0%
[5 empty] | 7.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.46 | 0%
[5 empty] | 7.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.47 | 0%
[5 empty] | 7.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.48 | 0%
[5 empty] | 7.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.49 | 0%
[5 empty] | 7.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0%
[5 empty] | 7.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.51 | 0%
[5 empty] | 7.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 0%
[5 empty] | 7.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.53 | 0%
[5 empty] | 7.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.54 | 0%
[5 empty] | 7.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.55 | 0%
[5 empty] | 7.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.56 | 0%
[5 empty] | 7.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.57 | 0%
[5 empty] | 7.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.58 | 0%
[5 empty] | 7.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.59 | 0%
[5 empty] | 7.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6 | 0%
[5 empty] | 7.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.61 | 0%
[5 empty] | 7.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.62 | 0%
[5 empty] | 7.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.63 | 0%
[5 empty] | 7.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.64 | 0%
[5 empty] | 7.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.65 | 0%
[5 empty] | 7.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.66 | 0%
[5 empty] | 7.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.67 | 0%
[5 empty] | 7.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.68 | 0%
[5 empty] | 7.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.69 | 0%
[5 empty] | 7.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7 | 0%
[5 empty] | 7.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.71 | 0%
[5 empty] | 7.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.72 | 0%
[5 empty] | 7.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.73 | 0%
[5 empty] | 7.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.74 | 0%
[5 empty] | 7.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 0%
[5 empty] | 7.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.76 | 0%
[5 empty] | 7.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.77 | 0%
[5 empty] | 7.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.78 | 0%
[5 empty] | 7.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.79 | 0%
[5 empty] | 7.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 0%
[5 empty] | 7.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.81 | 0%
[5 empty] | 7.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.82 | 0%
[5 empty] | 7.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.83 | 0%
[5 empty] | 7.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.84 | 0%
[5 empty] | 7.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.85 | 0%
[5 empty] | 7.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.86 | 0%
[5 empty] | 7.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.87 | 0%
[5 empty] | 7.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.88 | 0%
[5 empty] | 7.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89 | 0%
[5 empty] | 7.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 0%
[5 empty] | 7.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.91 | 0%
[5 empty] | 7.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.92 | 0%
[5 empty] | 7.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.93 | 0%
[5 empty] | 7.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.94 | 0%
[5 empty] | 7.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.95 | 0%
[5 empty] | 7.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.96 | 0%
[5 empty] | 7.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.97 | 0%
[5 empty] | 7.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.98 | 0%
[5 empty] | 7.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.99 | 0%
[5 empty] | 8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0%
[5 empty] | 8.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.01 | 0%
[5 empty] | 8.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.02 | 0%
[5 empty] | 8.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.03 | 0%
[5 empty] | 8.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.04 | 0%
[5 empty] | 8.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.05 | 0%
[5 empty] | 8.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.06 | 0%
[5 empty] | 8.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.07 | 0%
[5 empty] | 8.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.08 | 0%
[5 empty] | 8.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.09 | 0%
[5 empty] | 8.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 0%
[5 empty] | 8.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.11 | 0%
[5 empty] | 8.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12 | 0%
[5 empty] | 8.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.13 | 0%
[5 empty] | 8.14 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 0%
[5 empty] | 8.15 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.15 | 0%
[5 empty] | 8.16 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.16 | 0%
[5 empty] | 8.17 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.17 | 0%
[5 empty] | 8.18 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.18 | 0%
[5 empty] | 8.19 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.19 | 0%
[5 empty] | 8.2 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0%
[5 empty] | 8.21 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.21 | 0%
[5 empty] | 8.22 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.22 | 0%
[5 empty] | 8.23 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.23 | 0%
[5 empty] | 8.24 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.24 | 0%
[5 empty] | 8.25 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.25 | 0%
[5 empty] | 8.26 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.26 | 0%
[5 empty] | 8.27 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.27 | 0%
[5 empty] | 8.28 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.28 | 0%
[5 empty] | 8.29 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.29 | 0%
[5 empty] | 8.3 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 0%
[5 empty] | 8.31 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.31 | 0%
[5 empty] | 8.32 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.32 | 0%
[5 empty] | 8.33 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.33 | 0%
[5 empty] | 8.34 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.34 | 0%
[5 empty] | 8.35 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.35 | 0%
[5 empty] | 8.36 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.36 | 0%
[5 empty] | 8.37 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.37 | 0%
[5 empty] | 8.38 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.38 | 0%
[5 empty] | 8.39 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.39 | 0%
[5 empty] | 8.4 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 0%
[5 empty] | 8.41 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.41 | 0%
[5 empty] | 8.42 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.42 | 0%
[5 empty] | 8.43 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.43 | 0%
[5 empty] | 8.44 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.44 | 0%
[5 empty] | 8.45 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.45 | 0%
[5 empty] | 8.46 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.46 | 0%
[5 empty] | 8.47 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.47 | 0%
[5 empty] | 8.48 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.48 | 0%
[5 empty] | 8.49 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.49 | 0%
[5 empty] | 8.5 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0%
[5 empty] | 8.51 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.51 | 0%
[5 empty] | 8.52 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 0%
[5 empty] | 8.53 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.53 | 0%
[5 empty] | 8.54 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.54 | 0%
[5 empty] | 8.55 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.55 | 0%
[5 empty] | 8.56 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.56 | 0%
[5 empty] | 8.57 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.57 | 0%
[5 empty] | 8.58 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.58 | 0%
[5 empty] | 8.59 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.59 | 0%
[5 empty] | 8.6 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 0%
[5 empty] | 8.61 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.61 | 0%
[5 empty] | 8.62 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.62 | 0%
[5 empty] | 8.63 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.63 | 0%
[5 empty] | 8.64 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.64 | 0%
[5 empty] | 8.65 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.65 | 0%
[5 empty] | 8.66 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.66 | 0%
[5 empty] | 8.67 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.67 | 0%
[5 empty] | 8.68 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.68 | 0%
[5 empty] | 8.69 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.69 | 0%
[5 empty] | 8.7 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0%
[5 empty] | 8.71 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.71 | 0%
[5 empty] | 8.72 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.72 | 0%
[5 empty] | 8.73 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.73 | 0%
[5 empty] | 8.74 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.74 | 0%
[5 empty] | 8.75 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.75 | 0%
[5 empty] | 8.76 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.76 | 0%
[5 empty] | 8.77 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.77 | 0%
[5 empty] | 8.78 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.78 | 0%
[5 empty] | 8.79 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.79 | 0%
[5 empty] | 8.8 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0%
[5 empty] | 8.81 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.81 | 0%
[5 empty] | 8.82 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.82 | 0%
[5 empty] | 8.83 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.83 | 0%
[5 empty] | 8.84 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.84 | 0%
[5 empty] | 8.85 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.85 | 0%
[5 empty] | 8.86 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.86 | 0%
[5 empty] | 8.87 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.87 | 0%
[5 empty] | 8.88 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.88 | 0%
[5 empty] | 8.89 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.89 | 0%
[5 empty] | 8.9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0%
[5 empty] | 8.91 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.91 | 0%
[5 empty] | 8.92 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.92 | 0%
[5 empty] | 8.93 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.93 | 0%
[5 empty] | 8.94 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.94 | 0%
[5 empty] | 8.95 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.95 | 0%
[5 empty] | 8.96 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.96 | 0%
[5 empty] | 8.97 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 0%
[5 empty] | 8.98 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.98 | 0%
[5 empty] | 8.99 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.99 | 0%
[5 empty] | 9 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0%
[5 empty] | 9.01 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.01 | 0%
[5 empty] | 9.02 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.02 | 0%
[5 empty] | 9.03 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.03 | 0%
[5 empty] | 9.04 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.04 | 0%
[5 empty] | 9.05 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.05 | 0%
[5 empty] | 9.06 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.06 | 0%
[5 empty] | 9.07 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.07 | 0%
[5 empty] | 9.08 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.08 | 0%
[5 empty] | 9.09 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.09 | 0%
[5 empty] | 9.1 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 0%
[5 empty] | 9.11 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.11 | 0%
[5 empty] | 9.12 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.12 | 0%
[5 empty] | 9.13 | 246000 | 396 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.13 | 0%
[5 empty] | 9.14 | 246000 | 396 | 0.7154% | 0% | 0% | 0.0016194 | 0 | 0 | 0 | 0 | 0 | 0 | 9.14 | 0%
[5 empty] | 9.15 | 246000 | 396 | 2.06% | 0% | 0% | 0.0046639 | 12366.8135 | 0 | 0 | 12366.8135 | 0.12767 | 2.0611 | 9.15 | 5.633%
[5 empty] | 9.16 | 246000 | 396 | 3.405% | 0% | 0% | 0.0077084 | 12223.232 | 0 | 0 | 12223.232 | 0.25385 | 4.0983 | 9.16 | 5.568%
[5 empty] | 9.17 | 246000 | 396 | 4.75% | 0% | 0% | 0.010753 | 12079.6504 | 0 | 0 | 12079.6504 | 0.37856 | 6.1116 | 9.17 | 5.502%
[5 empty] | 9.18 | 246000 | 396 | 6.095% | 0% | 0% | 0.013797 | 11936.0689 | 0 | 0 | 11936.0689 | 0.50178 | 8.101 | 9.18 | 5.437%
[5 empty] | 9.19 | 246000 | 396 | 7.44% | 0% | 0% | 0.016842 | 11792.4874 | 0 | 0 | 11792.4874 | 0.62352 | 10.0664 | 9.19 | 5.371%
[5 empty] | 9.2 | 246000 | 396 | 8.785% | 0% | 0% | 0.019887 | 11648.9058 | 0 | 0 | 11648.9058 | 0.74378 | 12.0079 | 9.2 | 5.306%
[5 empty] | 9.21 | 246000 | 396 | 10.13% | 0% | 0% | 0.022931 | 11505.3243 | 0 | 0 | 11505.3243 | 0.86255 | 13.9254 | 9.21 | 5.241%
[5 empty] | 9.22 | 246000 | 396 | 11.47% | 0% | 0% | 0.025976 | 11361.7428 | 0 | 0 | 11361.7428 | 0.97985 | 15.819 | 9.22 | 5.175%
[5 empty] | 9.23 | 246000 | 396 | 12.82% | 0% | 0% | 0.02902 | 11218.1613 | 0 | 0 | 11218.1613 | 1.0957 | 17.6887 | 9.23 | 5.11%
[5 empty] | 9.24 | 246000 | 396 | 14.16% | 0% | 0% | 0.032065 | 11074.5797 | 0 | 0 | 11074.5797 | 1.21 | 19.5345 | 9.24 | 5.044%
[5 empty] | 9.25 | 246000 | 396 | 15.51% | 0% | 0% | 0.035109 | 10930.9982 | 0 | 0 | 10930.9982 | 1.3228 | 21.3563 | 9.25 | 4.979%
[5 empty] | 9.26 | 246000 | 396 | 16.85% | 0% | 0% | 0.038154 | 10787.4167 | 0 | 0 | 10787.4167 | 1.4342 | 23.1542 | 9.26 | 4.914%
[5 empty] | 9.27 | 246000 | 396 | 18.2% | 0% | 0% | 0.041198 | 10643.8351 | 0 | 0 | 10643.8351 | 1.5441 | 24.9282 | 9.27 | 4.848%
[5 empty] | 9.28 | 246000 | 396 | 19.54% | 0% | 0% | 0.044243 | 10500.2536 | 0 | 0 | 10500.2536 | 1.6525 | 26.6782 | 9.28 | 4.783%
[5 empty] | 9.29 | 246000 | 396 | 20.89% | 0% | 0% | 0.047287 | 10356.6721 | 0 | 0 | 10356.6721 | 1.7594 | 28.4044 | 9.29 | 4.717%
[5 empty] | 9.3 | 246000 | 396 | 22.23% | 0% | 0% | 0.050332 | 10213.0905 | 0 | 0 | 10213.0905 | 1.8648 | 30.1065 | 9.3 | 4.652%
[5 empty] | 9.31 | 246000 | 396 | 23.58% | 0% | 0% | 0.053376 | 10069.509 | 0 | 0 | 10069.509 | 1.9688 | 31.7848 | 9.31 | 4.587%
[5 empty] | 9.32 | 246000 | 396 | 24.92% | 0% | 0% | 0.056421 | 9925.9275 | 0 | 0 | 9925.9275 | 2.0712 | 33.4391 | 9.32 | 4.521%
[5 empty] | 9.33 | 246000 | 396 | 26.27% | 0% | 0% | 0.059465 | 9782.3459 | 0 | 0 | 9782.3459 | 2.1722 | 35.0695 | 9.33 | 4.456%
[5 empty] | 9.34 | 246000 | 396 | 27.61% | 0% | 0% | 0.06251 | 9638.7644 | 0 | 0 | 9638.7644 | 2.2717 | 36.676 | 9.34 | 4.39%
[5 empty] | 9.35 | 246000 | 396 | 28.96% | 0% | 0% | 0.065554 | 9495.1829 | 0 | 0 | 9495.1829 | 2.3698 | 38.2585 | 9.35 | 4.325%
[5 empty] | 9.36 | 246000 | 396 | 30.3% | 0% | 0% | 0.068599 | 9351.6014 | 0 | 0 | 9351.6014 | 2.4663 | 39.8171 | 9.36 | 4.26%
[5 empty] | 9.37 | 246000 | 396 | 31.65% | 0% | 0% | 0.071643 | 9208.0198 | 0 | 0 | 9208.0198 | 2.5614 | 41.3518 | 9.37 | 4.194%
[5 empty] | 9.38 | 246000 | 396 | 32.99% | 0% | 0% | 0.074688 | 9064.4383 | 0 | 0 | 9064.4383 | 2.6549 | 42.8625 | 9.38 | 4.129%
[5 empty] | 9.39 | 246000 | 396 | 34.34% | 0% | 0% | 0.077733 | 8920.8568 | 0 | 0 | 8920.8568 | 2.747 | 44.3493 | 9.39 | 4.063%
[5 empty] | 9.4 | 246000 | 396 | 35.68% | 0% | 0% | 0.080777 | 8777.2752 | 0 | 0 | 8777.2752 | 2.8376 | 45.8122 | 9.4 | 3.998%
[5 empty] | 9.41 | 246000 | 396 | 37.03% | 0% | 0% | 0.083822 | 8633.6937 | 0 | 0 | 8633.6937 | 2.9268 | 47.2511 | 9.41 | 3.933%
[5 empty] | 9.42 | 246000 | 396 | 38.37% | 0% | 0% | 0.086866 | 8490.1122 | 0 | 0 | 8490.1122 | 3.0144 | 48.6662 | 9.42 | 3.867%
[5 empty] | 9.43 | 246000 | 396 | 39.72% | 0% | 0% | 0.089911 | 8346.5306 | 0 | 0 | 8346.5306 | 3.1006 | 50.0572 | 9.43 | 3.802%
[5 empty] | 9.44 | 246000 | 396 | 41.06% | 0% | 0% | 0.092955 | 8202.9491 | 0 | 0 | 8202.9491 | 3.1853 | 51.4244 | 9.44 | 3.736%
[5 empty] | 9.45 | 246000 | 396 | 42.41% | 0% | 0% | 0.096 | 8059.3676 | 0 | 0 | 8059.3676 | 3.2685 | 52.7676 | 9.45 | 3.671%
[5 empty] | 9.46 | 246000 | 396 | 43.75% | 0% | 0% | 0.099044 | 7915.786 | 0 | 0 | 7915.786 | 3.3502 | 54.0869 | 9.46 | 3.606%
[5 empty] | 9.47 | 246000 | 396 | 45.1% | 0% | 0% | 0.10209 | 7772.2045 | 0 | 0 | 7772.2045 | 3.4304 | 55.3823 | 9.47 | 3.54%
[5 empty] | 9.48 | 246000 | 396 | 46.44% | 0% | 0% | 0.10513 | 7628.623 | 0 | 0 | 7628.623 | 3.5092 | 56.6537 | 9.48 | 3.475%
[5 empty] | 9.49 | 246000 | 396 | 47.79% | 0% | 0% | 0.10818 | 7485.0414 | 0 | 0 | 7485.0414 | 3.5865 | 57.9012 | 9.49 | 3.409%
[5 empty] | 9.5 | 246000 | 396 | 49.13% | 0% | 0% | 0.11122 | 7341.4599 | 0 | 0 | 7341.4599 | 3.6622 | 59.1248 | 9.5 | 3.344%
[5 empty] | 9.51 | 246000 | 396 | 50.48% | 0% | 0% | 0.11427 | 7197.8784 | 0 | 0 | 7197.8784 | 3.7366 | 60.3245 | 9.51 | 3.279%
[5 empty] | 9.52 | 246000 | 396 | 51.82% | 0% | 0% | 0.11731 | 7054.2969 | 0 | 0 | 7054.2969 | 3.8094 | 61.5002 | 9.52 | 3.213%
[5 empty] | 9.53 | 246000 | 396 | 53.17% | 0% | 0% | 0.12036 | 6910.7153 | 0 | 0 | 6910.7153 | 3.8807 | 62.652 | 9.53 | 3.148%
[5 empty] | 9.54 | 246000 | 396 | 54.51% | 0% | 0% | 0.1234 | 6767.1338 | 0 | 0 | 6767.1338 | 3.9506 | 63.7798 | 9.54 | 3.082%
[5 empty] | 9.55 | 246000 | 396 | 55.86% | 0% | 0% | 0.12644 | 6623.5523 | 0 | 0 | 6623.5523 | 4.019 | 64.8837 | 9.55 | 3.017%
[5 empty] | 9.56 | 246000 | 396 | 57.2% | 0% | 0% | 0.12949 | 6479.9707 | 0 | 0 | 6479.9707 | 4.0859 | 65.9637 | 9.56 | 2.952%
[5 empty] | 9.57 | 246000 | 396 | 58.55% | 0% | 0% | 0.13253 | 6336.3892 | 0 | 0 | 6336.3892 | 4.1513 | 67.0198 | 9.57 | 2.886%
[5 empty] | 9.58 | 246000 | 396 | 59.89% | 0% | 0% | 0.13558 | 6192.8077 | 0 | 0 | 6192.8077 | 4.2152 | 68.0519 | 9.58 | 2.821%
[5 empty] | 9.59 | 246000 | 396 | 61.24% | 0% | 0% | 0.13862 | 6049.2261 | 0 | 0 | 6049.2261 | 4.2776 | 69.0601 | 9.59 | 2.755%
[5 empty] | 9.6 | 246000 | 396 | 62.58% | 0% | 0% | 0.14167 | 5905.6446 | 0 | 0 | 5905.6446 | 4.3386 | 70.0444 | 9.6 | 2.69%
[5 empty] | 9.61 | 246000 | 396 | 63.93% | 0% | 0% | 0.14471 | 5762.0631 | 0 | 0 | 5762.0631 | 4.3981 | 71.0048 | 9.61 | 2.625%
[5 empty] | 9.62 | 246000 | 396 | 65.27% | 0% | 0% | 0.14776 | 5618.4815 | 0 | 0 | 5618.4815 | 4.4561 | 71.9412 | 9.62 | 2.559%
[5 empty] | 9.63 | 246000 | 396 | 66.62% | 0% | 0% | 0.1508 | 5474.9 | 0 | 0 | 5474.9 | 4.5126 | 72.8537 | 9.63 | 2.494%
[5 empty] | 9.64 | 246000 | 396 | 67.96% | 0% | 0% | 0.15385 | 5331.3185 | 0 | 0 | 5331.3185 | 4.5677 | 73.7422 | 9.64 | 2.428%
[5 empty] | 9.65 | 246000 | 396 | 69.31% | 0% | 0% | 0.15689 | 5187.737 | 0 | 0 | 5187.737 | 4.6212 | 74.6068 | 9.65 | 2.363%
[5 empty] | 9.66 | 246000 | 396 | 70.65% | 0% | 0% | 0.15993 | 5044.1554 | 0 | 0 | 5044.1554 | 4.6733 | 75.4475 | 9.66 | 2.298%
[5 empty] | 9.67 | 246000 | 396 | 72% | 0% | 0% | 0.16298 | 4900.5739 | 0 | 0 | 4900.5739 | 4.7239 | 76.2643 | 9.67 | 2.232%
[5 empty] | 9.68 | 246000 | 396 | 73.34% | 0% | 0% | 0.16602 | 4756.9924 | 0 | 0 | 4756.9924 | 4.773 | 77.0571 | 9.68 | 2.167%
[5 empty] | 9.69 | 246000 | 396 | 74.69% | 0% | 0% | 0.16907 | 4613.4108 | 0 | 0 | 4613.4108 | 4.8206 | 77.826 | 9.69 | 2.101%
[5 empty] | 9.7 | 246000 | 396 | 76.03% | 0% | 0% | 0.17211 | 4469.8293 | 0 | 0 | 4469.8293 | 4.8668 | 78.571 | 9.7 | 2.036%
[5 empty] | 9.71 | 246000 | 396 | 77.37% | 0% | 0% | 0.17516 | 4326.2478 | 0 | 0 | 4326.2478 | 4.9114 | 79.292 | 9.71 | 1.971%
[5 empty] | 9.72 | 246000 | 396 | 78.72% | 0% | 0% | 0.1782 | 4182.6662 | 0 | 0 | 4182.6662 | 4.9546 | 79.9892 | 9.72 | 1.905%
[5 empty] | 9.73 | 246000 | 396 | 80.06% | 0% | 0% | 0.18125 | 4039.0847 | 0 | 0 | 4039.0847 | 4.9963 | 80.6623 | 9.73 | 1.84%
[5 empty] | 9.74 | 246000 | 396 | 81.41% | 0% | 0% | 0.18429 | 3895.5032 | 0 | 0 | 3895.5032 | 5.0365 | 81.3116 | 9.74 | 1.774%
[5 empty] | 9.75 | 246000 | 396 | 82.75% | 0% | 0% | 0.18734 | 3751.9216 | 0 | 0 | 3751.9216 | 5.0752 | 81.9369 | 9.75 | 1.709%
[5 empty] | 9.76 | 246000 | 396 | 84.1% | 0% | 0% | 0.19038 | 3608.3401 | 0 | 0 | 3608.3401 | 5.1125 | 82.5383 | 9.76 | 1.644%
[5 empty] | 9.77 | 246000 | 396 | 85.44% | 0% | 0% | 0.19342 | 3464.7586 | 0 | 0 | 3464.7586 | 5.1483 | 83.1158 | 9.77 | 1.578%
[5 empty] | 9.78 | 246000 | 396 | 86.79% | 0% | 0% | 0.19647 | 3321.177 | 0 | 0 | 3321.177 | 5.1825 | 83.6693 | 9.78 | 1.513%
[5 empty] | 9.79 | 246000 | 396 | 88.13% | 0% | 0% | 0.19951 | 3177.5955 | 0 | 0 | 3177.5955 | 5.2154 | 84.1989 | 9.79 | 1.447%
[5 empty] | 9.8 | 246000 | 396 | 89.48% | 0% | 0% | 0.20256 | 3034.014 | 0 | 0 | 3034.014 | 5.2467 | 84.7046 | 9.8 | 1.382%
[5 empty] | 9.81 | 246000 | 396 | 90.82% | 0% | 0% | 0.2056 | 2890.4325 | 0 | 0 | 2890.4325 | 5.2765 | 85.1863 | 9.81 | 1.317%
[5 empty] | 9.82 | 246000 | 396 | 92.17% | 0% | 0% | 0.20865 | 2746.8509 | 0 | 0 | 2746.8509 | 5.3049 | 85.6441 | 9.82 | 1.251%
[5 empty] | 9.83 | 246000 | 396 | 93.51% | 0% | 0% | 0.21169 | 2603.2694 | 0 | 0 | 2603.2694 | 5.3317 | 86.078 | 9.83 | 1.186%
[5 empty] | 9.84 | 246000 | 396 | 94.86% | 0% | 0% | 0.21474 | 2459.6879 | 0 | 0 | 2459.6879 | 5.3571 | 86.4879 | 9.84 | 1.12%
[5 empty] | 9.85 | 246000 | 396 | 96.2% | 0% | 0% | 0.21778 | 2316.1063 | 0 | 0 | 2316.1063 | 5.381 | 86.8739 | 9.85 | 1.055%
[5 empty] | 9.86 | 246000 | 396 | 97.55% | 0% | 0% | 0.22083 | 2172.5248 | 0 | 0 | 2172.5248 | 5.4035 | 87.236 | 9.86 | 0.9896%
[5 empty] | 9.87 | 246000 | 396 | 98.89% | 0% | 0% | 0.22387 | 2028.9433 | 0 | 0 | 2028.9433 | 5.4244 | 87.5742 | 9.87 | 0.9242%
[5 empty] | 9.88 | 246000 | 396 | 100.2% | 0.2216% | 0% | 0.22745 | 1885.3617 | 0 | 0 | 1885.3617 | 5.4439 | 87.8884 | 9.88 | 0.8588%
[5 empty] | 9.89 | 246000 | 396 | 100% | 1.472% | 0% | 0.22996 | 1910.8108 | 15497.2116 | 0 | 17408.0224 | 5.6236 | 90.7898 | 9.89 | 7.929%
[5 empty] | 9.9 | 246000 | 396 | 100% | 2.722% | 0% | 0.233 | 1910.8108 | 15370.0327 | 0 | 17280.8435 | 5.802 | 93.6699 | 9.9 | 7.871%
[5 empty] | 9.91 | 246000 | 396 | 100% | 3.972% | 0% | 0.23605 | 1910.8108 | 15242.8538 | 0 | 17153.6646 | 5.9791 | 96.5288 | 9.91 | 7.813%
[5 empty] | 9.92 | 246000 | 396 | 100% | 5.223% | 0% | 0.23909 | 1910.8108 | 15115.6749 | 0 | 17026.4857 | 6.1549 | 99.3666 | 9.92 | 7.755%
[5 empty] | 9.93 | 246000 | 396 | 100% | 6.473% | 0% | 0.24214 | 1910.8108 | 14988.496 | 0 | 16899.3068 | 6.3293 | 102.1831 | 9.93 | 7.697%
[5 empty] | 9.94 | 246000 | 396 | 100% | 7.723% | 0% | 0.24518 | 1910.8108 | 14861.3171 | 0 | 16772.1279 | 6.5025 | 104.9785 | 9.94 | 7.639%
[5 empty] | 9.95 | 246000 | 396 | 100% | 8.974% | 0% | 0.24823 | 1910.8108 | 14734.1382 | 0 | 16644.949 | 6.6743 | 107.7526 | 9.95 | 7.582%
[5 empty] | 9.96 | 246000 | 396 | 100% | 10.22% | 0% | 0.25127 | 1910.8108 | 14606.9593 | 0 | 16517.7701 | 6.8448 | 110.5056 | 9.96 | 7.524%
[5 empty] | 9.97 | 246000 | 396 | 100% | 11.47% | 0% | 0.25432 | 1910.8108 | 14479.7804 | 0 | 16390.5913 | 7.014 | 113.2374 | 9.97 | 7.466%
[5 empty] | 9.98 | 246000 | 396 | 100% | 12.72% | 0% | 0.25736 | 1910.8108 | 14352.6015 | 0 | 16263.4124 | 7.1819 | 115.9479 | 9.98 | 7.408%
[5 empty] | 9.99 | 246000 | 396 | 100% | 13.97% | 0% | 0.2604 | 1910.8108 | 14225.4226 | 0 | 16136.2335 | 7.3485 | 118.6373 | 9.99 | 7.35%
[5 empty] | 10 | 246000 | 396 | 100% | 15.22% | 0% | 0.26345 | 1910.8108 | 14098.2438 | 0 | 16009.0546 | 7.5138 | 121.3055 | 10 | 7.292%
[5 empty] | 10.01 | 246000 | 396 | 100% | 16.48% | 0% | 0.26649 | 1910.8108 | 13971.0649 | 0 | 15881.8757 | 7.6777 | 123.9525 | 10.01 | 7.234%
[5 empty] | 10.02 | 246000 | 396 | 100% | 17.73% | 0% | 0.26954 | 1910.8108 | 13843.886 | 0 | 15754.6968 | 7.8404 | 126.5783 | 10.02 | 7.176%
[5 empty] | 10.03 | 246000 | 396 | 100% | 18.98% | 0% | 0.27258 | 1910.8108 | 13716.7071 | 0 | 15627.5179 | 8.0017 | 129.1828 | 10.03 | 7.118%
[5 empty] | 10.04 | 246000 | 396 | 100% | 20.23% | 0% | 0.27563 | 1910.8108 | 13589.5282 | 0 | 15500.339 | 8.1617 | 131.7662 | 10.04 | 7.06%
[5 empty] | 10.05 | 246000 | 396 | 100% | 21.48% | 0% | 0.27867 | 1910.8108 | 13462.3493 | 0 | 15373.1601 | 8.3204 | 134.3284 | 10.05 | 7.002%
[5 empty] | 10.06 | 246000 | 396 | 100% | 22.73% | 0% | 0.28172 | 1910.8108 | 13335.1704 | 0 | 15245.9812 | 8.4778 | 136.8694 | 10.06 | 6.944%
[5 empty] | 10.07 | 246000 | 396 | 100% | 23.98% | 0% | 0.28476 | 1910.8108 | 13207.9915 | 0 | 15118.8023 | 8.6339 | 139.3892 | 10.07 | 6.886%
[5 empty] | 10.08 | 246000 | 396 | 100% | 25.23% | 0% | 0.2878 | 1910.8108 | 13080.8126 | 0 | 14991.6234 | 8.7887 | 141.8878 | 10.08 | 6.828%
[5 empty] | 10.09 | 246000 | 396 | 100% | 26.48% | 0% | 0.29085 | 1910.8108 | 12953.6337 | 0 | 14864.4445 | 8.9421 | 144.3652 | 10.09 | 6.771%
[5 empty] | 10.1 | 246000 | 396 | 100% | 27.73% | 0% | 0.29389 | 1910.8108 | 12826.4548 | 0 | 14737.2656 | 9.0942 | 146.8214 | 10.1 | 6.713%
[5 empty] | 10.11 | 246000 | 396 | 100% | 28.98% | 0% | 0.29694 | 1910.8108 | 12699.2759 | 0 | 14610.0867 | 9.2451 | 149.2565 | 10.11 | 6.655%
[5 empty] | 10.12 | 246000 | 396 | 100% | 30.23% | 0% | 0.29998 | 1910.8108 | 12572.097 | 0 | 14482.9078 | 9.3946 | 151.6703 | 10.12 | 6.597%
[5 empty] | 10.13 | 246000 | 396 | 100% | 31.48% | 0% | 0.30303 | 1910.8108 | 12444.9181 | 0 | 14355.7289 | 9.5428 | 154.0629 | 10.13 | 6.539%
[5 empty] | 10.14 | 246000 | 396 | 100% | 32.73% | 0% | 0.30607 | 1910.8108 | 12317.7392 | 0 | 14228.55 | 9.6897 | 156.4343 | 10.14 | 6.481%
[5 empty] | 10.15 | 246000 | 396 | 100% | 33.98% | 0% | 0.30912 | 1910.8108 | 12190.5603 | 0 | 14101.3711 | 9.8353 | 158.7845 | 10.15 | 6.423%
[5 empty] | 10.16 | 246000 | 396 | 100% | 35.23% | 0% | 0.31216 | 1910.8108 | 12063.3814 | 0 | 13974.1922 | 9.9795 | 161.1136 | 10.16 | 6.365%
[5 empty] | 10.17 | 246000 | 396 | 100% | 36.48% | 0% | 0.31521 | 1910.8108 | 11936.2025 | 0 | 13847.0133 | 10.1225 | 163.4214 | 10.17 | 6.307%
[5 empty] | 10.18 | 246000 | 396 | 100% | 37.73% | 0% | 0.31825 | 1910.8108 | 11809.0236 | 0 | 13719.8345 | 10.2641 | 165.7081 | 10.18 | 6.249%
[5 empty] | 10.19 | 246000 | 396 | 100% | 38.98% | 0% | 0.32129 | 1910.8108 | 11681.8447 | 0 | 13592.6556 | 10.4044 | 167.9735 | 10.19 | 6.191%
[5 empty] | 10.2 | 246000 | 396 | 100% | 40.23% | 0% | 0.32434 | 1910.8108 | 11554.6659 | 0 | 13465.4767 | 10.5434 | 170.2177 | 10.2 | 6.133%
[5 empty] | 10.21 | 246000 | 396 | 100% | 41.48% | 0% | 0.32738 | 1910.8108 | 11427.487 | 0 | 13338.2978 | 10.6811 | 172.4408 | 10.21 | 6.075%
[5 empty] | 10.22 | 246000 | 396 | 100% | 42.73% | 0% | 0.33043 | 1910.8108 | 11300.3081 | 0 | 13211.1189 | 10.8175 | 174.6426 | 10.22 | 6.017%
[5 empty] | 10.23 | 246000 | 396 | 100% | 43.98% | 0% | 0.33347 | 1910.8108 | 11173.1292 | 0 | 13083.94 | 10.9526 | 176.8233 | 10.23 | 5.96%
[5 empty] | 10.24 | 246000 | 396 | 100% | 45.23% | 0% | 0.33652 | 1910.8108 | 11045.9503 | 0 | 12956.7611 | 11.0863 | 178.9828 | 10.24 | 5.902%
[5 empty] | 10.25 | 246000 | 396 | 100% | 46.48% | 0% | 0.33956 | 1910.8108 | 10918.7714 | 0 | 12829.5822 | 11.2188 | 181.121 | 10.25 | 5.844%
[5 empty] | 10.26 | 246000 | 396 | 100% | 47.73% | 0% | 0.34261 | 1910.8108 | 10791.5925 | 0 | 12702.4033 | 11.3499 | 183.2381 | 10.26 | 5.786%
[5 empty] | 10.27 | 246000 | 396 | 100% | 48.98% | 0% | 0.34565 | 1910.8108 | 10664.4136 | 0 | 12575.2244 | 11.4797 | 185.334 | 10.27 | 5.728%
[5 empty] | 10.28 | 246000 | 396 | 100% | 50.23% | 0% | 0.3487 | 1910.8108 | 10537.2347 | 0 | 12448.0455 | 11.6083 | 187.4086 | 10.28 | 5.67%
[5 empty] | 10.29 | 246000 | 396 | 100% | 51.48% | 0% | 0.35174 | 1910.8108 | 10410.0558 | 0 | 12320.8666 | 11.7355 | 189.4621 | 10.29 | 5.612%
[5 empty] | 10.3 | 246000 | 396 | 100% | 52.73% | 0% | 0.35478 | 1910.8108 | 10282.8769 | 0 | 12193.6877 | 11.8613 | 191.4944 | 10.3 | 5.554%
[5 empty] | 10.31 | 246000 | 396 | 100% | 53.98% | 0% | 0.35783 | 1910.8108 | 10155.698 | 0 | 12066.5088 | 11.9859 | 193.5055 | 10.31 | 5.496%
[5 empty] | 10.32 | 246000 | 396 | 100% | 55.23% | 0% | 0.36087 | 1910.8108 | 10028.5191 | 0 | 11939.3299 | 12.1092 | 195.4954 | 10.32 | 5.438%
[5 empty] | 10.33 | 246000 | 396 | 100% | 56.48% | 0% | 0.36392 | 1910.8108 | 9901.3402 | 0 | 11812.151 | 12.2311 | 197.4641 | 10.33 | 5.38%
[5 empty] | 10.34 | 246000 | 396 | 100% | 57.73% | 0% | 0.36696 | 1910.8108 | 9774.1613 | 0 | 11684.9721 | 12.3517 | 199.4116 | 10.34 | 5.322%
[5 empty] | 10.35 | 246000 | 396 | 100% | 58.98% | 0% | 0.37001 | 1910.8108 | 9646.9824 | 0 | 11557.7932 | 12.471 | 201.3379 | 10.35 | 5.264%
[5 empty] | 10.36 | 246000 | 396 | 100% | 60.23% | 0% | 0.37305 | 1910.8108 | 9519.8035 | 0 | 11430.6143 | 12.589 | 203.243 | 10.36 | 5.206%
[5 empty] | 10.37 | 246000 | 396 | 100% | 61.49% | 0% | 0.3761 | 1910.8108 | 9392.6246 | 0 | 11303.4354 | 12.7057 | 205.1269 | 10.37 | 5.149%
[5 empty] | 10.38 | 246000 | 396 | 100% | 62.74% | 0% | 0.37914 | 1910.8108 | 9265.4457 | 0 | 11176.2565 | 12.8211 | 206.9896 | 10.38 | 5.091%
[5 empty] | 10.39 | 246000 | 396 | 100% | 63.99% | 0% | 0.38219 | 1910.8108 | 9138.2668 | 0 | 11049.0777 | 12.9352 | 208.8311 | 10.39 | 5.033%
[5 empty] | 10.4 | 246000 | 396 | 100% | 65.24% | 0% | 0.38523 | 1910.8108 | 9011.0879 | 0 | 10921.8988 | 13.0479 | 210.6514 | 10.4 | 4.975%
[5 empty] | 10.41 | 246000 | 396 | 100% | 66.49% | 0% | 0.38827 | 1910.8108 | 8883.9091 | 0 | 10794.7199 | 13.1594 | 212.4505 | 10.41 | 4.917%
[5 empty] | 10.42 | 246000 | 396 | 100% | 67.74% | 0% | 0.39132 | 1910.8108 | 8756.7302 | 0 | 10667.541 | 13.2695 | 214.2284 | 10.42 | 4.859%
[5 empty] | 10.43 | 246000 | 396 | 100% | 68.99% | 0% | 0.39436 | 1910.8108 | 8629.5513 | 0 | 10540.3621 | 13.3783 | 215.9852 | 10.43 | 4.801%
[5 empty] | 10.44 | 246000 | 396 | 100% | 70.24% | 0% | 0.39741 | 1910.8108 | 8502.3724 | 0 | 10413.1832 | 13.4858 | 217.7207 | 10.44 | 4.743%
[5 empty] | 10.45 | 246000 | 396 | 100% | 71.49% | 0% | 0.40045 | 1910.8108 | 8375.1935 | 0 | 10286.0043 | 13.592 | 219.435 | 10.45 | 4.685%
[5 empty] | 10.46 | 246000 | 396 | 100% | 72.74% | 0% | 0.4035 | 1910.8108 | 8248.0146 | 0 | 10158.8254 | 13.6969 | 221.1282 | 10.46 | 4.627%
[5 empty] | 10.47 | 246000 | 396 | 100% | 73.99% | 0% | 0.40654 | 1910.8108 | 8120.8357 | 0 | 10031.6465 | 13.8004 | 222.8001 | 10.47 | 4.569%
[5 empty] | 10.48 | 246000 | 396 | 100% | 75.24% | 0% | 0.40959 | 1910.8108 | 7993.6568 | 0 | 9904.4676 | 13.9027 | 224.4509 | 10.48 | 4.511%
[5 empty] | 10.49 | 246000 | 396 | 100% | 76.49% | 0% | 0.41263 | 1910.8108 | 7866.4779 | 0 | 9777.2887 | 14.0036 | 226.0804 | 10.49 | 4.453%
[5 empty] | 10.5 | 246000 | 396 | 100% | 77.74% | 0% | 0.41567 | 1910.8108 | 7739.299 | 0 | 9650.1098 | 14.1032 | 227.6888 | 10.5 | 4.395%
[5 empty] | 10.51 | 246000 | 396 | 100% | 78.99% | 0% | 0.41872 | 1910.8108 | 7612.1201 | 0 | 9522.9309 | 14.2016 | 229.2759 | 10.51 | 4.338%
[5 empty] | 10.52 | 246000 | 396 | 100% | 80.24% | 0% | 0.42176 | 1910.8108 | 7484.9412 | 0 | 9395.752 | 14.2985 | 230.8419 | 10.52 | 4.28%
[5 empty] | 10.53 | 246000 | 396 | 100% | 81.49% | 0% | 0.42481 | 1910.8108 | 7357.7623 | 0 | 9268.5731 | 14.3942 | 232.3866 | 10.53 | 4.222%
[5 empty] | 10.54 | 246000 | 396 | 100% | 82.74% | 0% | 0.42785 | 1910.8108 | 7230.5834 | 0 | 9141.3942 | 14.4886 | 233.9102 | 10.54 | 4.164%
[5 empty] | 10.55 | 246000 | 396 | 100% | 83.99% | 0% | 0.4309 | 1910.8108 | 7103.4045 | 0 | 9014.2153 | 14.5817 | 235.4126 | 10.55 | 4.106%
[5 empty] | 10.56 | 246000 | 396 | 100% | 85.24% | 0% | 0.43394 | 1910.8108 | 6976.2256 | 0 | 8887.0364 | 14.6734 | 236.8937 | 10.56 | 4.048%
[5 empty] | 10.57 | 246000 | 396 | 100% | 86.49% | 0% | 0.43699 | 1910.8108 | 6849.0467 | 0 | 8759.8575 | 14.7638 | 238.3537 | 10.57 | 3.99%
[5 empty] | 10.58 | 246000 | 396 | 100% | 87.74% | 0% | 0.44003 | 1910.8108 | 6721.8678 | 0 | 8632.6786 | 14.853 | 239.7925 | 10.58 | 3.932%
[5 empty] | 10.59 | 246000 | 396 | 100% | 88.99% | 0% | 0.44308 | 1910.8108 | 6594.6889 | 0 | 8505.4998 | 14.9408 | 241.2101 | 10.59 | 3.874%
[5 empty] | 10.6 | 246000 | 396 | 100% | 90.24% | 0% | 0.44612 | 1910.8108 | 6467.51 | 0 | 8378.3209 | 15.0273 | 242.6065 | 10.6 | 3.816%
[5 empty] | 10.61 | 246000 | 396 | 100% | 91.49% | 0% | 0.44916 | 1910.8108 | 6340.3312 | 0 | 8251.142 | 15.1124 | 243.9817 | 10.61 | 3.758%
[5 empty] | 10.62 | 246000 | 396 | 100% | 92.74% | 0% | 0.45221 | 1910.8108 | 6213.1523 | 0 | 8123.9631 | 15.1963 | 245.3357 | 10.62 | 3.7%
[5 empty] | 10.63 | 246000 | 396 | 100% | 93.99% | 0% | 0.45525 | 1910.8108 | 6085.9734 | 0 | 7996.7842 | 15.2789 | 246.6685 | 10.63 | 3.642%
[5 empty] | 10.64 | 246000 | 396 | 100% | 95.24% | 0% | 0.4583 | 1910.8108 | 5958.7945 | 0 | 7869.6053 | 15.3601 | 247.9801 | 10.64 | 3.584%
[5 empty] | 10.65 | 246000 | 396 | 100% | 96.49% | 0% | 0.46134 | 1910.8108 | 5831.6156 | 0 | 7742.4264 | 15.44 | 249.2705 | 10.65 | 3.527%
[5 empty] | 10.66 | 246000 | 396 | 100% | 97.74% | 0% | 0.46439 | 1910.8108 | 5704.4367 | 0 | 7615.2475 | 15.5186 | 250.5397 | 10.66 | 3.469%
[5 empty] | 10.67 | 246000 | 396 | 100% | 98.99% | 0% | 0.46743 | 1910.8108 | 5577.2578 | 0 | 7488.0686 | 15.596 | 251.7877 | 10.67 | 3.411%
[5 empty] | 10.68 | 246000 | 396 | 100% | 100.2% | 0.1119% | 0.47107 | 1910.8108 | 5450.0789 | 116095.4552 | 123456.3449 | 16.8704 | 272.3637 | 10.68 | 56.23%
[5 empty] | 10.69 | 246000 | 396 | 100% | 100% | 0.6862% | 0.47352 | 1910.8108 | 5474.8509 | 116647.7839 | 124033.4456 | 18.1509 | 293.036 | 10.69 | 56.5%
[5 empty] | 10.7 | 246000 | 396 | 100% | 100% | 1.26% | 0.47657 | 1910.8108 | 5474.8509 | 117200.1125 | 124585.7742 | 19.4371 | 313.8003 | 10.7 | 56.75%
[5 empty] | 10.71 | 246000 | 396 | 100% | 100% | 1.835% | 0.47961 | 1910.8108 | 5474.8509 | 117752.4411 | 125138.1028 | 20.7289 | 334.6566 | 10.71 | 57%
[5 empty] | 10.72 | 246000 | 396 | 100% | 100% | 2.409% | 0.48265 | 1910.8108 | 5474.8509 | 118304.7697 | 125690.4315 | 22.0265 | 355.605 | 10.72 | 57.25%
[5 empty] | 10.73 | 246000 | 396 | 100% | 100% | 2.983% | 0.4857 | 1910.8108 | 5474.8509 | 118857.0983 | 126242.7601 | 23.3298 | 376.6455 | 10.73 | 57.5%
[5 empty] | 10.74 | 246000 | 396 | 100% | 100% | 3.558% | 0.48874 | 1910.8108 | 5474.8509 | 119409.4269 | 126795.0887 | 24.6387 | 397.778 | 10.74 | 57.75%
[5 empty] | 10.75 | 246000 | 396 | 100% | 100% | 4.132% | 0.49179 | 1910.8108 | 5474.8509 | 119961.7556 | 127347.4173 | 25.9534 | 419.0026 | 10.75 | 58%
[5 empty] | 10.76 | 246000 | 396 | 100% | 100% | 4.706% | 0.49483 | 1910.8108 | 5474.8509 | 120514.0842 | 127899.7459 | 27.2738 | 440.3192 | 10.76 | 58.26%
[5 empty] | 10.77 | 246000 | 396 | 100% | 100% | 5.281% | 0.49788 | 1910.8108 | 5474.8509 | 121066.4128 | 128452.0745 | 28.5998 | 461.7279 | 10.77 | 58.51%
[5 empty] | 10.78 | 246000 | 396 | 100% | 100% | 5.855% | 0.50092 | 1910.8108 | 5474.8509 | 121618.7414 | 129004.4032 | 29.9316 | 483.2286 | 10.78 | 58.76%
[5 empty] | 10.79 | 246000 | 396 | 100% | 100% | 6.429% | 0.50397 | 1910.8108 | 5474.8509 | 122171.07 | 129556.7318 | 31.2691 | 504.8214 | 10.79 | 59.01%
[5 empty] | 10.8 | 246000 | 396 | 100% | 100% | 7.004% | 0.50701 | 1910.8108 | 5474.8509 | 122723.3986 | 130109.0604 | 32.6123 | 526.5062 | 10.8 | 59.26%
[5 empty] | 10.81 | 246000 | 396 | 100% | 100% | 7.578% | 0.51006 | 1910.8108 | 5474.8509 | 123275.7272 | 130661.389 | 33.9611 | 548.2831 | 10.81 | 59.51%
[5 empty] | 10.82 | 246000 | 396 | 100% | 100% | 8.152% | 0.5131 | 1910.8108 | 5474.8509 | 123828.0559 | 131213.7176 | 35.3157 | 570.1521 | 10.82 | 59.77%
[5 empty] | 10.83 | 246000 | 396 | 100% | 100% | 8.727% | 0.51614 | 1910.8108 | 5474.8509 | 124380.3845 | 131766.0462 | 36.676 | 592.1131 | 10.83 | 60.02%
[5 empty] | 10.84 | 246000 | 396 | 100% | 100% | 9.301% | 0.51919 | 1910.8108 | 5474.8509 | 124932.7131 | 132318.3748 | 38.042 | 614.1662 | 10.84 | 60.27%
[5 empty] | 10.85 | 246000 | 396 | 100% | 100% | 9.875% | 0.52223 | 1910.8108 | 5474.8509 | 125485.0417 | 132870.7035 | 39.4137 | 636.3113 | 10.85 | 60.52%
[5 empty] | 10.86 | 246000 | 396 | 100% | 100% | 10.45% | 0.52528 | 1910.8108 | 5474.8509 | 126037.3703 | 133423.0321 | 40.7911 | 658.5485 | 10.86 | 60.77%
[5 empty] | 10.87 | 246000 | 396 | 100% | 100% | 11.02% | 0.52832 | 1910.8108 | 5474.8509 | 126589.6989 | 133975.3607 | 42.1742 | 680.8777 | 10.87 | 61.02%
[5 empty] | 10.88 | 246000 | 396 | 100% | 100% | 11.6% | 0.53137 | 1910.8108 | 5474.8509 | 127142.0276 | 134527.6893 | 43.563 | 703.299 | 10.88 | 61.28%
[5 empty] | 10.89 | 246000 | 396 | 100% | 100% | 12.17% | 0.53441 | 1910.8108 | 5474.8509 | 127694.3562 | 135080.0179 | 44.9575 | 725.8123 | 10.89 | 61.53%
[5 empty] | 10.9 | 246000 | 396 | 100% | 100% | 12.75% | 0.53746 | 1910.8108 | 5474.8509 | 128246.6848 | 135632.3465 | 46.3576 | 748.4177 | 10.9 | 61.78%
[5 empty] | 10.91 | 246000 | 396 | 100% | 100% | 13.32% | 0.5405 | 1910.8108 | 5474.8509 | 128799.0134 | 136184.6752 | 47.7635 | 771.1151 | 10.91 | 62.03%
[5 empty] | 10.92 | 246000 | 396 | 100% | 100% | 13.9% | 0.54355 | 1910.8108 | 5474.8509 | 129351.342 | 136737.0038 | 49.1752 | 793.9046 | 10.92 | 62.28%
[5 empty] | 10.93 | 246000 | 396 | 100% | 100% | 14.47% | 0.54659 | 1910.8108 | 5474.8509 | 129903.6706 | 137289.3324 | 50.5925 | 816.7862 | 10.93 | 62.53%
[5 empty] | 10.94 | 246000 | 396 | 100% | 100% | 15.04% | 0.54963 | 1910.8108 | 5474.8509 | 130455.9992 | 137841.661 | 52.0155 | 839.7598 | 10.94 | 62.78%
[5 empty] | 10.95 | 246000 | 396 | 100% | 100% | 15.62% | 0.55268 | 1910.8108 | 5474.8509 | 131008.3279 | 138393.9896 | 53.4442 | 862.8255 | 10.95 | 63.04%
[5 empty] | 10.96 | 246000 | 396 | 100% | 100% | 16.19% | 0.55572 | 1910.8108 | 5474.8509 | 131560.6565 | 138946.3182 | 54.8786 | 885.9832 | 10.96 | 63.29%
[5 empty] | 10.97 | 246000 | 396 | 100% | 100% | 16.77% | 0.55877 | 1910.8108 | 5474.8509 | 132112.9851 | 139498.6468 | 56.3187 | 909.233 | 10.97 | 63.54%
[5 empty] | 10.98 | 246000 | 396 | 100% | 100% | 17.34% | 0.56181 | 1910.8108 | 5474.8509 | 132665.3137 | 140050.9755 | 57.7645 | 932.5748 | 10.98 | 63.79%
[5 empty] | 10.99 | 246000 | 396 | 100% | 100% | 17.92% | 0.56486 | 1910.8108 | 5474.8509 | 133217.6423 | 140603.3041 | 59.216 | 956.0087 | 10.99 | 64.04%
[5 empty] | 11 | 246000 | 396 | 100% | 100% | 18.49% | 0.5679 | 1910.8108 | 5474.8509 | 133769.9709 | 141155.6327 | 60.6732 | 979.5346 | 11 | 64.29%
[5 empty] | 11.01 | 246000 | 396 | 100% | 100% | 19.06% | 0.57095 | 1910.8108 | 5474.8509 | 134322.2996 | 141707.9613 | 62.1362 | 1003.1526 | 11.01 | 64.55%
[5 empty] | 11.02 | 246000 | 396 | 100% | 100% | 19.64% | 0.57399 | 1910.8108 | 5474.8509 | 134874.6282 | 142260.2899 | 63.6048 | 1026.8627 | 11.02 | 64.8%
[5 empty] | 11.03 | 246000 | 396 | 100% | 100% | 20.21% | 0.57703 | 1910.8108 | 5474.8509 | 135426.9568 | 142812.6185 | 65.0791 | 1050.6648 | 11.03 | 65.05%
[5 empty] | 11.04 | 246000 | 396 | 100% | 100% | 20.79% | 0.58008 | 1910.8108 | 5474.8509 | 135979.2854 | 143364.9472 | 66.5591 | 1074.5589 | 11.04 | 65.3%
[5 empty] | 11.05 | 246000 | 396 | 100% | 100% | 21.36% | 0.58312 | 1910.8108 | 5474.8509 | 136531.614 | 143917.2758 | 68.0449 | 1098.5451 | 11.05 | 65.55%
[5 empty] | 11.06 | 246000 | 396 | 100% | 100% | 21.94% | 0.58617 | 1910.8108 | 5474.8509 | 137083.9426 | 144469.6044 | 69.5363 | 1122.6234 | 11.06 | 65.8%
[5 empty] | 11.07 | 246000 | 396 | 100% | 100% | 22.51% | 0.58921 | 1910.8108 | 5474.8509 | 137636.2712 | 145021.933 | 71.0334 | 1146.7937 | 11.07 | 66.06%
[5 empty] | 11.08 | 246000 | 396 | 100% | 100% | 23.08% | 0.59226 | 1910.8108 | 5474.8509 | 138188.5999 | 145574.2616 | 72.5362 | 1171.0561 | 11.08 | 66.31%
[5 empty] | 11.09 | 246000 | 396 | 100% | 100% | 23.66% | 0.5953 | 1910.8108 | 5474.8509 | 138740.9285 | 146126.5902 | 74.0448 | 1195.4105 | 11.09 | 66.56%
[5 empty] | 11.1 | 246000 | 396 | 100% | 100% | 24.23% | 0.59835 | 1910.8108 | 5474.8509 | 139293.2571 | 146678.9188 | 75.559 | 1219.857 | 11.1 | 66.81%
[5 empty] | 11.11 | 246000 | 396 | 100% | 100% | 24.81% | 0.60139 | 1910.8108 | 5474.8509 | 139845.5857 | 147231.2475 | 77.079 | 1244.3956 | 11.11 | 67.06%
[5 empty] | 11.12 | 246000 | 396 | 100% | 100% | 25.38% | 0.60444 | 1910.8108 | 5474.8509 | 140397.9143 | 147783.5761 | 78.6046 | 1269.0262 | 11.12 | 67.31%
[5 empty] | 11.13 | 246000 | 396 | 100% | 100% | 25.96% | 0.60748 | 1910.8108 | 5474.8509 | 140950.2429 | 148335.9047 | 80.1359 | 1293.7488 | 11.13 | 67.56%
[5 empty] | 11.14 | 246000 | 396 | 100% | 100% | 26.53% | 0.61052 | 1910.8108 | 5474.8509 | 141502.5716 | 148888.2333 | 81.673 | 1318.5635 | 11.14 | 67.82%
[5 empty] | 11.15 | 246000 | 396 | 100% | 100% | 27.1% | 0.61357 | 1910.8108 | 5474.8509 | 142054.9002 | 149440.5619 | 83.2157 | 1343.4703 | 11.15 | 68.07%
[5 empty] | 11.16 | 246000 | 396 | 100% | 100% | 27.68% | 0.61661 | 1910.8108 | 5474.8509 | 142607.2288 | 149992.8905 | 84.7642 | 1368.4691 | 11.16 | 68.32%
[5 empty] | 11.17 | 246000 | 396 | 100% | 100% | 28.25% | 0.61966 | 1910.8108 | 5474.8509 | 143159.5574 | 150545.2192 | 86.3183 | 1393.56 | 11.17 | 68.57%
[5 empty] | 11.18 | 246000 | 396 | 100% | 100% | 28.83% | 0.6227 | 1910.8108 | 5474.8509 | 143711.886 | 151097.5478 | 87.8782 | 1418.7429 | 11.18 | 68.82%
[5 empty] | 11.19 | 246000 | 396 | 100% | 100% | 29.4% | 0.62575 | 1910.8108 | 5474.8509 | 144264.2146 | 151649.8764 | 89.4437 | 1444.0179 | 11.19 | 69.07%
[5 empty] | 11.2 | 246000 | 396 | 100% | 100% | 29.98% | 0.62879 | 1910.8108 | 5474.8509 | 144816.5432 | 152202.205 | 91.015 | 1469.3849 | 11.2 | 69.33%
[5 empty] | 11.21 | 246000 | 396 | 100% | 100% | 30.55% | 0.63184 | 1910.8108 | 5474.8509 | 145368.8719 | 152754.5336 | 92.5919 | 1494.844 | 11.21 | 69.58%
[5 empty] | 11.22 | 246000 | 396 | 100% | 100% | 31.12% | 0.63488 | 1910.8108 | 5474.8509 | 145921.2005 | 153306.8622 | 94.1746 | 1520.3951 | 11.22 | 69.83%
[5 empty] | 11.23 | 246000 | 396 | 100% | 100% | 31.7% | 0.63793 | 1910.8108 | 5474.8509 | 146473.5291 | 153859.1908 | 95.763 | 1546.0383 | 11.23 | 70.08%
[5 empty] | 11.24 | 246000 | 396 | 100% | 100% | 32.27% | 0.64097 | 1910.8108 | 5474.8509 | 147025.8577 | 154411.5195 | 97.357 | 1571.7736 | 11.24 | 70.33%
[5 empty] | 11.25 | 246000 | 396 | 100% | 100% | 32.85% | 0.64401 | 1910.8108 | 5474.8509 | 147578.1863 | 154963.8481 | 98.9568 | 1597.6009 | 11.25 | 70.58%
[5 empty] | 11.26 | 246000 | 396 | 100% | 100% | 33.42% | 0.64706 | 1910.8108 | 5474.8509 | 148130.5149 | 155516.1767 | 100.5623 | 1623.5202 | 11.26 | 70.84%
[5 empty] | 11.27 | 246000 | 396 | 100% | 100% | 34% | 0.6501 | 1910.8108 | 5474.8509 | 148682.8436 | 156068.5053 | 102.1734 | 1649.5317 | 11.27 | 71.09%
[5 empty] | 11.28 | 246000 | 396 | 100% | 100% | 34.57% | 0.65315 | 1910.8108 | 5474.8509 | 149235.1722 | 156620.8339 | 103.7903 | 1675.6351 | 11.28 | 71.34%
[5 empty] | 11.29 | 246000 | 396 | 100% | 100% | 35.14% | 0.65619 | 1910.8108 | 5474.8509 | 149787.5008 | 157173.1625 | 105.4129 | 1701.8307 | 11.29 | 71.59%
[5 empty] | 11.3 | 246000 | 396 | 100% | 100% | 35.72% | 0.65924 | 1910.8108 | 5474.8509 | 150339.8294 | 157725.4912 | 107.0412 | 1728.1182 | 11.3 | 71.84%
[5 empty] | 11.31 | 246000 | 396 | 100% | 100% | 36.29% | 0.66228 | 1910.8108 | 5474.8509 | 150892.158 | 158277.8198 | 108.6751 | 1754.4979 | 11.31 | 72.09%
[5 empty] | 11.32 | 246000 | 396 | 100% | 100% | 36.87% | 0.66533 | 1910.8108 | 5474.8509 | 151444.4866 | 158830.1484 | 110.3148 | 1780.9696 | 11.32 | 72.34%
[5 empty] | 11.33 | 246000 | 396 | 100% | 100% | 37.44% | 0.66837 | 1910.8108 | 5474.8509 | 151996.8152 | 159382.477 | 111.9602 | 1807.5333 | 11.33 | 72.6%
[5 empty] | 11.34 | 246000 | 396 | 100% | 100% | 38.02% | 0.67142 | 1910.8108 | 5474.8509 | 152549.1439 | 159934.8056 | 113.6113 | 1834.1891 | 11.34 | 72.85%
[5 empty] | 11.35 | 246000 | 396 | 100% | 100% | 38.59% | 0.67446 | 1910.8108 | 5474.8509 | 153101.4725 | 160487.1342 | 115.2681 | 1860.937 | 11.35 | 73.1%
[5 empty] | 11.36 | 246000 | 396 | 100% | 100% | 39.17% | 0.6775 | 1910.8108 | 5474.8509 | 153653.8011 | 161039.4628 | 116.9306 | 1887.7769 | 11.36 | 73.35%
[5 empty] | 11.37 | 246000 | 396 | 100% | 100% | 39.74% | 0.68055 | 1910.8108 | 5474.8509 | 154206.1297 | 161591.7915 | 118.5987 | 1914.7089 | 11.37 | 73.6%
[5 empty] | 11.38 | 246000 | 396 | 100% | 100% | 40.31% | 0.68359 | 1910.8108 | 5474.8509 | 154758.4583 | 162144.1201 | 120.2726 | 1941.7329 | 11.38 | 73.85%
[5 empty] | 11.39 | 246000 | 396 | 100% | 100% | 40.89% | 0.68664 | 1910.8108 | 5474.8509 | 155310.7869 | 162696.4487 | 121.9522 | 1968.8489 | 11.39 | 74.11%
[5 empty] | 11.4 | 246000 | 396 | 100% | 100% | 41.46% | 0.68968 | 1910.8108 | 5474.8509 | 155863.1156 | 163248.7773 | 123.6375 | 1996.0571 | 11.4 | 74.36%
[5 empty] | 11.41 | 246000 | 396 | 100% | 100% | 42.04% | 0.69273 | 1910.8108 | 5474.8509 | 156415.4442 | 163801.1059 | 125.3285 | 2023.3573 | 11.41 | 74.61%
[5 empty] | 11.42 | 246000 | 396 | 100% | 100% | 42.61% | 0.69577 | 1910.8108 | 5474.8509 | 156967.7728 | 164353.4345 | 127.0252 | 2050.7495 | 11.42 | 74.86%
[5 empty] | 11.43 | 246000 | 396 | 100% | 100% | 43.19% | 0.69882 | 1910.8108 | 5474.8509 | 157520.1014 | 164905.7632 | 128.7276 | 2078.2338 | 11.43 | 75.11%
[5 empty] | 11.44 | 246000 | 396 | 100% | 100% | 43.76% | 0.70186 | 1910.8108 | 5474.8509 | 158072.43 | 165458.0918 | 130.4357 | 2105.8101 | 11.44 | 75.36%
[5 empty] | 11.45 | 246000 | 396 | 100% | 100% | 44.33% | 0.7049 | 1910.8108 | 5474.8509 | 158624.7586 | 166010.4204 | 132.1495 | 2133.4785 | 11.45 | 75.62%
[5 empty] | 11.46 | 246000 | 396 | 100% | 100% | 44.91% | 0.70795 | 1910.8108 | 5474.8509 | 159177.0872 | 166562.749 | 133.869 | 2161.239 | 11.46 | 75.87%
[5 empty] | 11.47 | 246000 | 396 | 100% | 100% | 45.48% | 0.71099 | 1910.8108 | 5474.8509 | 159729.4159 | 167115.0776 | 135.5943 | 2189.0915 | 11.47 | 76.12%
[5 empty] | 11.48 | 246000 | 396 | 100% | 100% | 46.06% | 0.71404 | 1910.8108 | 5474.8509 | 160281.7445 | 167667.4062 | 137.3252 | 2217.0361 | 11.48 | 76.37%
[5 empty] | 11.49 | 246000 | 396 | 100% | 100% | 46.63% | 0.71708 | 1910.8108 | 5474.8509 | 160834.0731 | 168219.7348 | 139.0618 | 2245.0727 | 11.49 | 76.62%
[5 empty] | 11.5 | 246000 | 396 | 100% | 100% | 47.21% | 0.72013 | 1910.8108 | 5474.8509 | 161386.4017 | 168772.0635 | 140.8041 | 2273.2014 | 11.5 | 76.87%
[5 empty] | 11.51 | 246000 | 396 | 100% | 100% | 47.78% | 0.72317 | 1910.8108 | 5474.8509 | 161938.7303 | 169324.3921 | 142.5521 | 2301.4221 | 11.51 | 77.12%
[5 empty] | 11.52 | 246000 | 396 | 100% | 100% | 48.35% | 0.72622 | 1910.8108 | 5474.8509 | 162491.0589 | 169876.7207 | 144.3058 | 2329.7349 | 11.52 | 77.38%
[5 empty] | 11.53 | 246000 | 396 | 100% | 100% | 48.93% | 0.72926 | 1910.8108 | 5474.8509 | 163043.3876 | 170429.0493 | 146.0652 | 2358.1397 | 11.53 | 77.63%
[5 empty] | 11.54 | 246000 | 396 | 100% | 100% | 49.5% | 0.73231 | 1910.8108 | 5474.8509 | 163595.7162 | 170981.3779 | 147.8304 | 2386.6366 | 11.54 | 77.88%
[5 empty] | 11.55 | 246000 | 396 | 100% | 100% | 50.08% | 0.73535 | 1910.8108 | 5474.8509 | 164148.0448 | 171533.7065 | 149.6012 | 2415.2256 | 11.55 | 78.13%
[5 empty] | 11.56 | 246000 | 396 | 100% | 100% | 50.65% | 0.73839 | 1910.8108 | 5474.8509 | 164700.3734 | 172086.0352 | 151.3777 | 2443.9066 | 11.56 | 78.38%
[5 empty] | 11.57 | 246000 | 396 | 100% | 100% | 51.23% | 0.74144 | 1910.8108 | 5474.8509 | 165252.702 | 172638.3638 | 153.16 | 2472.6797 | 11.57 | 78.63%
[5 empty] | 11.58 | 246000 | 396 | 100% | 100% | 51.8% | 0.74448 | 1910.8108 | 5474.8509 | 165805.0306 | 173190.6924 | 154.9479 | 2501.5448 | 11.58 | 78.89%
[5 empty] | 11.59 | 246000 | 396 | 100% | 100% | 52.37% | 0.74753 | 1910.8108 | 5474.8509 | 166357.3592 | 173743.021 | 156.7415 | 2530.5019 | 11.59 | 79.14%
[5 empty] | 11.6 | 246000 | 396 | 100% | 100% | 52.95% | 0.75057 | 1910.8108 | 5474.8509 | 166909.6879 | 174295.3496 | 158.5408 | 2559.5512 | 11.6 | 79.39%
[5 empty] | 11.61 | 246000 | 396 | 100% | 100% | 53.52% | 0.75362 | 1910.8108 | 5474.8509 | 167462.0165 | 174847.6782 | 160.3459 | 2588.6924 | 11.61 | 79.64%
[5 empty] | 11.62 | 246000 | 396 | 100% | 100% | 54.1% | 0.75666 | 1910.8108 | 5474.8509 | 168014.3451 | 175400.0068 | 162.1566 | 2617.9258 | 11.62 | 79.89%
[5 empty] | 11.63 | 246000 | 396 | 100% | 100% | 54.67% | 0.75971 | 1910.8108 | 5474.8509 | 168566.6737 | 175952.3355 | 163.9731 | 2647.2512 | 11.63 | 80.14%
[5 empty] | 11.64 | 246000 | 396 | 100% | 100% | 55.25% | 0.76275 | 1910.8108 | 5474.8509 | 169119.0023 | 176504.6641 | 165.7952 | 2676.6686 | 11.64 | 80.4%
[5 empty] | 11.65 | 246000 | 396 | 100% | 100% | 55.82% | 0.7658 | 1910.8108 | 5474.8509 | 169671.3309 | 177056.9927 | 167.6231 | 2706.1781 | 11.65 | 80.65%
[5 empty] | 11.66 | 246000 | 396 | 100% | 100% | 56.39% | 0.76884 | 1910.8108 | 5474.8509 | 170223.6596 | 177609.3213 | 169.4566 | 2735.7797 | 11.66 | 80.9%
[5 empty] | 11.67 | 246000 | 396 | 100% | 100% | 56.97% | 0.77188 | 1910.8108 | 5474.8509 | 170775.9882 | 178161.6499 | 171.2958 | 2765.4733 | 11.67 | 81.15%
[5 empty] | 11.68 | 246000 | 396 | 100% | 100% | 57.54% | 0.77493 | 1910.8108 | 5474.8509 | 171328.3168 | 178713.9785 | 173.1408 | 2795.2589 | 11.68 | 81.4%
[5 empty] | 11.69 | 246000 | 396 | 100% | 100% | 58.12% | 0.77797 | 1910.8108 | 5474.8509 | 171880.6454 | 179266.3072 | 174.9914 | 2825.1367 | 11.69 | 81.65%
[5 empty] | 11.7 | 246000 | 396 | 100% | 100% | 58.69% | 0.78102 | 1910.8108 | 5474.8509 | 172432.974 | 179818.6358 | 176.8478 | 2855.1064 | 11.7 | 81.9%
[5 empty] | 11.71 | 246000 | 396 | 100% | 100% | 59.27% | 0.78406 | 1910.8108 | 5474.8509 | 172985.3026 | 180370.9644 | 178.7099 | 2885.1683 | 11.71 | 82.16%
[5 empty] | 11.72 | 246000 | 396 | 100% | 100% | 59.84% | 0.78711 | 1910.8108 | 5474.8509 | 173537.6312 | 180923.293 | 180.5776 | 2915.3221 | 11.72 | 82.41%
[5 empty] | 11.73 | 246000 | 396 | 100% | 100% | 60.41% | 0.79015 | 1910.8108 | 5474.8509 | 174089.9599 | 181475.6216 | 182.4511 | 2945.5681 | 11.73 | 82.66%
[5 empty] | 11.74 | 246000 | 396 | 100% | 100% | 60.99% | 0.7932 | 1910.8108 | 5474.8509 | 174642.2885 | 182027.9502 | 184.3302 | 2975.9061 | 11.74 | 82.91%
[5 empty] | 11.75 | 246000 | 396 | 100% | 100% | 61.56% | 0.79624 | 1910.8108 | 5474.8509 | 175194.6171 | 182580.2788 | 186.2151 | 3006.3361 | 11.75 | 83.16%
[5 empty] | 11.76 | 246000 | 396 | 100% | 100% | 62.14% | 0.79929 | 1910.8108 | 5474.8509 | 175746.9457 | 183132.6075 | 188.1057 | 3036.8582 | 11.76 | 83.41%
[5 empty] | 11.77 | 246000 | 396 | 100% | 100% | 62.71% | 0.80233 | 1910.8108 | 5474.8509 | 176299.2743 | 183684.9361 | 190.0019 | 3067.4724 | 11.77 | 83.67%
[5 empty] | 11.78 | 246000 | 396 | 100% | 100% | 63.29% | 0.80537 | 1910.8108 | 5474.8509 | 176851.6029 | 184237.2647 | 191.9039 | 3098.1786 | 11.78 | 83.92%
[5 empty] | 11.79 | 246000 | 396 | 100% | 100% | 63.86% | 0.80842 | 1910.8108 | 5474.8509 | 177403.9316 | 184789.5933 | 193.8116 | 3128.9768 | 11.79 | 84.17%
[5 empty] | 11.8 | 246000 | 396 | 100% | 100% | 64.43% | 0.81146 | 1910.8108 | 5474.8509 | 177956.2602 | 185341.9219 | 195.7249 | 3159.8672 | 11.8 | 84.42%
[5 empty] | 11.81 | 246000 | 396 | 100% | 100% | 65.01% | 0.81451 | 1910.8108 | 5474.8509 | 178508.5888 | 185894.2505 | 197.644 | 3190.8495 | 11.81 | 84.67%
[5 empty] | 11.82 | 246000 | 396 | 100% | 100% | 65.58% | 0.81755 | 1910.8108 | 5474.8509 | 179060.9174 | 186446.5792 | 199.5688 | 3221.924 | 11.82 | 84.92%
[5 empty] | 11.83 | 246000 | 396 | 100% | 100% | 66.16% | 0.8206 | 1910.8108 | 5474.8509 | 179613.246 | 186998.9078 | 201.4993 | 3253.0905 | 11.83 | 85.18%
[5 empty] | 11.84 | 246000 | 396 | 100% | 100% | 66.73% | 0.82364 | 1910.8108 | 5474.8509 | 180165.5746 | 187551.2364 | 203.4355 | 3284.349 | 11.84 | 85.43%
[5 empty] | 11.85 | 246000 | 396 | 100% | 100% | 67.31% | 0.82669 | 1910.8108 | 5474.8509 | 180717.9032 | 188103.565 | 205.3773 | 3315.6996 | 11.85 | 85.68%
[5 empty] | 11.86 | 246000 | 396 | 100% | 100% | 67.88% | 0.82973 | 1910.8108 | 5474.8509 | 181270.2319 | 188655.8936 | 207.3249 | 3347.1422 | 11.86 | 85.93%
[5 empty] | 11.87 | 246000 | 396 | 100% | 100% | 68.46% | 0.83278 | 1910.8108 | 5474.8509 | 181822.5605 | 189208.2222 | 209.2782 | 3378.6769 | 11.87 | 86.18%
[5 empty] | 11.88 | 246000 | 396 | 100% | 100% | 69.03% | 0.83582 | 1910.8108 | 5474.8509 | 182374.8891 | 189760.5508 | 211.2372 | 3410.3037 | 11.88 | 86.43%
[5 empty] | 11.89 | 246000 | 396 | 100% | 100% | 69.6% | 0.83886 | 1910.8108 | 5474.8509 | 182927.2177 | 190312.8795 | 213.2019 | 3442.0225 | 11.89 | 86.68%
[5 empty] | 11.9 | 246000 | 396 | 100% | 100% | 70.18% | 0.84191 | 1910.8108 | 5474.8509 | 183479.5463 | 190865.2081 | 215.1723 | 3473.8334 | 11.9 | 86.94%
[5 empty] | 11.91 | 246000 | 396 | 100% | 100% | 70.75% | 0.84495 | 1910.8108 | 5474.8509 | 184031.8749 | 191417.5367 | 217.1484 | 3505.7363 | 11.91 | 87.19%
[5 empty] | 11.92 | 246000 | 396 | 100% | 100% | 71.33% | 0.848 | 1910.8108 | 5474.8509 | 184584.2036 | 191969.8653 | 219.1302 | 3537.7313 | 11.92 | 87.44%
[5 empty] | 11.93 | 246000 | 396 | 100% | 100% | 71.9% | 0.85104 | 1910.8108 | 5474.8509 | 185136.5322 | 192522.1939 | 221.1177 | 3569.8183 | 11.93 | 87.69%
[5 empty] | 11.94 | 246000 | 396 | 100% | 100% | 72.48% | 0.85409 | 1910.8108 | 5474.8509 | 185688.8608 | 193074.5225 | 223.1109 | 3601.9974 | 11.94 | 87.94%
[5 empty] | 11.95 | 246000 | 396 | 100% | 100% | 73.05% | 0.85713 | 1910.8108 | 5474.8509 | 186241.1894 | 193626.8512 | 225.1098 | 3634.2685 | 11.95 | 88.19%
[5 empty] | 11.96 | 246000 | 396 | 100% | 100% | 73.62% | 0.86018 | 1910.8108 | 5474.8509 | 186793.518 | 194179.1798 | 227.1144 | 3666.6317 | 11.96 | 88.45%
[5 empty] | 11.97 | 246000 | 396 | 100% | 100% | 74.2% | 0.86322 | 1910.8108 | 5474.8509 | 187345.8466 | 194731.5084 | 229.1247 | 3699.087 | 11.97 | 88.7%
[5 empty] | 11.98 | 246000 | 396 | 100% | 100% | 74.77% | 0.86626 | 1910.8108 | 5474.8509 | 187898.1752 | 195283.837 | 231.1407 | 3731.6343 | 11.98 | 88.95%
[5 empty] | 11.99 | 246000 | 396 | 100% | 100% | 75.35% | 0.86931 | 1910.8108 | 5474.8509 | 188450.5039 | 195836.1656 | 233.1624 | 3764.2737 | 11.99 | 89.2%
[5 empty] | 12 | 246000 | 396 | 100% | 100% | 75.92% | 0.87235 | 1910.8108 | 5474.8509 | 189002.8325 | 196388.4942 | 235.1898 | 3797.0051 | 12 | 89.45%
[5 empty] | 12.01 | 246000 | 396 | 100% | 100% | 76.5% | 0.8754 | 1910.8108 | 5474.8509 | 189555.1611 | 196940.8228 | 237.2229 | 3829.8285 | 12.01 | 89.7%
[5 empty] | 12.02 | 246000 | 396 | 100% | 100% | 77.07% | 0.87844 | 1910.8108 | 5474.8509 | 190107.4897 | 197493.1515 | 239.2618 | 3862.7441 | 12.02 | 89.96%
[5 empty] | 12.03 | 246000 | 396 | 100% | 100% | 77.64% | 0.88149 | 1910.8108 | 5474.8509 | 190659.8183 | 198045.4801 | 241.3063 | 3895.7517 | 12.03 | 90.21%
[5 empty] | 12.04 | 246000 | 396 | 100% | 100% | 78.22% | 0.88453 | 1910.8108 | 5474.8509 | 191212.1469 | 198597.8087 | 243.3565 | 3928.8513 | 12.04 | 90.46%
[5 empty] | 12.05 | 246000 | 396 | 100% | 100% | 78.79% | 0.88758 | 1910.8108 | 5474.8509 | 191764.4756 | 199150.1373 | 245.4124 | 3962.043 | 12.05 | 90.71%
[5 empty] | 12.06 | 246000 | 396 | 100% | 100% | 79.37% | 0.89062 | 1910.8108 | 5474.8509 | 192316.8042 | 199702.4659 | 247.474 | 3995.3267 | 12.06 | 90.96%
[5 empty] | 12.07 | 246000 | 396 | 100% | 100% | 79.94% | 0.89367 | 1910.8108 | 5474.8509 | 192869.1328 | 200254.7945 | 249.5414 | 4028.7025 | 12.07 | 91.21%
[5 empty] | 12.08 | 246000 | 396 | 100% | 100% | 80.52% | 0.89671 | 1910.8108 | 5474.8509 | 193421.4614 | 200807.1232 | 251.6144 | 4062.1704 | 12.08 | 91.46%
[5 empty] | 12.09 | 246000 | 396 | 100% | 100% | 81.09% | 0.89975 | 1910.8108 | 5474.8509 | 193973.79 | 201359.4518 | 253.6931 | 4095.7303 | 12.09 | 91.72%
[5 empty] | 12.1 | 246000 | 396 | 100% | 100% | 81.66% | 0.9028 | 1910.8108 | 5474.8509 | 194526.1186 | 201911.7804 | 255.7776 | 4129.3822 | 12.1 | 91.97%
[5 empty] | 12.11 | 246000 | 396 | 100% | 100% | 82.24% | 0.90584 | 1910.8108 | 5474.8509 | 195078.4472 | 202464.109 | 257.8677 | 4163.1263 | 12.11 | 92.22%
[5 empty] | 12.12 | 246000 | 396 | 100% | 100% | 82.81% | 0.90889 | 1910.8108 | 5474.8509 | 195630.7759 | 203016.4376 | 259.9635 | 4196.9623 | 12.12 | 92.47%
[5 empty] | 12.13 | 246000 | 396 | 100% | 100% | 83.39% | 0.91193 | 1910.8108 | 5474.8509 | 196183.1045 | 203568.7662 | 262.0651 | 4230.8905 | 12.13 | 92.72%
[5 empty] | 12.14 | 246000 | 396 | 100% | 100% | 83.96% | 0.91498 | 1910.8108 | 5474.8509 | 196735.4331 | 204121.0948 | 264.1723 | 4264.9106 | 12.14 | 92.97%
[5 empty] | 12.15 | 246000 | 396 | 100% | 100% | 84.54% | 0.91802 | 1910.8108 | 5474.8509 | 197287.7617 | 204673.4235 | 266.2853 | 4299.0229 | 12.15 | 93.23%
[5 empty] | 12.16 | 246000 | 396 | 100% | 100% | 85.11% | 0.92107 | 1910.8108 | 5474.8509 | 197840.0903 | 205225.7521 | 268.4039 | 4333.2272 | 12.16 | 93.48%
[5 empty] | 12.17 | 246000 | 396 | 100% | 100% | 85.68% | 0.92411 | 1910.8108 | 5474.8509 | 198392.4189 | 205778.0807 | 270.5282 | 4367.5235 | 12.17 | 93.73%
[5 empty] | 12.18 | 246000 | 396 | 100% | 100% | 86.26% | 0.92716 | 1910.8108 | 5474.8509 | 198944.7476 | 206330.4093 | 272.6583 | 4401.9119 | 12.18 | 93.98%
[5 empty] | 12.19 | 246000 | 396 | 100% | 100% | 86.83% | 0.9302 | 1910.8108 | 5474.8509 | 199497.0762 | 206882.7379 | 274.794 | 4436.3924 | 12.19 | 94.23%
[5 empty] | 12.2 | 246000 | 396 | 100% | 100% | 87.41% | 0.93324 | 1910.8108 | 5474.8509 | 200049.4048 | 207435.0665 | 276.9355 | 4470.9649 | 12.2 | 94.48%
[5 empty] | 12.21 | 246000 | 396 | 100% | 100% | 87.98% | 0.93629 | 1910.8108 | 5474.8509 | 200601.7334 | 207987.3952 | 279.0826 | 4505.6295 | 12.21 | 94.74%
[5 empty] | 12.22 | 246000 | 396 | 100% | 100% | 88.56% | 0.93933 | 1910.8108 | 5474.8509 | 201154.062 | 208539.7238 | 281.2355 | 4540.3861 | 12.22 | 94.99%
[5 empty] | 12.23 | 246000 | 396 | 100% | 100% | 89.13% | 0.94238 | 1910.8108 | 5474.8509 | 201706.3906 | 209092.0524 | 283.3941 | 4575.2348 | 12.23 | 95.24%
[5 empty] | 12.24 | 246000 | 396 | 100% | 100% | 89.7% | 0.94542 | 1910.8108 | 5474.8509 | 202258.7192 | 209644.381 | 285.5583 | 4610.1755 | 12.24 | 95.49%
[5 empty] | 12.25 | 246000 | 396 | 100% | 100% | 90.28% | 0.94847 | 1910.8108 | 5474.8509 | 202811.0479 | 210196.7096 | 287.7283 | 4645.2083 | 12.25 | 95.74%
[5 empty] | 12.26 | 246000 | 396 | 100% | 100% | 90.85% | 0.95151 | 1910.8108 | 5474.8509 | 203363.3765 | 210749.0382 | 289.9039 | 4680.3331 | 12.26 | 95.99%
[5 empty] | 12.27 | 246000 | 396 | 100% | 100% | 91.43% | 0.95456 | 1910.8108 | 5474.8509 | 203915.7051 | 211301.3668 | 292.0853 | 4715.55 | 12.27 | 96.24%
[5 empty] | 12.28 | 246000 | 396 | 100% | 100% | 92% | 0.9576 | 1910.8108 | 5474.8509 | 204468.0337 | 211853.6955 | 294.2724 | 4750.859 | 12.28 | 96.5%
[5 empty] | 12.29 | 246000 | 396 | 100% | 100% | 92.58% | 0.96065 | 1910.8108 | 5474.8509 | 205020.3623 | 212406.0241 | 296.4651 | 4786.26 | 12.29 | 96.75%
[5 empty] | 12.3 | 246000 | 396 | 100% | 100% | 93.15% | 0.96369 | 1910.8108 | 5474.8509 | 205572.6909 | 212958.3527 | 298.6636 | 4821.753 | 12.3 | 97%
[5 empty] | 12.31 | 246000 | 396 | 100% | 100% | 93.72% | 0.96673 | 1910.8108 | 5474.8509 | 206125.0196 | 213510.6813 | 300.8678 | 4857.3381 | 12.31 | 97.25%
[5 empty] | 12.32 | 246000 | 396 | 100% | 100% | 94.3% | 0.96978 | 1910.8108 | 5474.8509 | 206677.3482 | 214063.0099 | 303.0777 | 4893.0153 | 12.32 | 97.5%
[5 empty] | 12.33 | 246000 | 396 | 100% | 100% | 94.87% | 0.97282 | 1910.8108 | 5474.8509 | 207229.6768 | 214615.3385 | 305.2932 | 4928.7845 | 12.33 | 97.75%
[5 empty] | 12.34 | 246000 | 396 | 100% | 100% | 95.45% | 0.97587 | 1910.8108 | 5474.8509 | 207782.0054 | 215167.6672 | 307.5145 | 4964.6458 | 12.34 | 98.01%
[5 empty] | 12.35 | 246000 | 396 | 100% | 100% | 96.02% | 0.97891 | 1910.8108 | 5474.8509 | 208334.334 | 215719.9958 | 309.7415 | 5000.5991 | 12.35 | 98.26%
[5 empty] | 12.36 | 246000 | 396 | 100% | 100% | 96.6% | 0.98196 | 1910.8108 | 5474.8509 | 208886.6626 | 216272.3244 | 311.9742 | 5036.6445 | 12.36 | 98.51%
[5 empty] | 12.37 | 246000 | 396 | 100% | 100% | 97.17% | 0.985 | 1910.8108 | 5474.8509 | 209438.9912 | 216824.653 | 314.2126 | 5072.782 | 12.37 | 98.76%
[5 empty] | 12.38 | 246000 | 396 | 100% | 100% | 97.75% | 0.98805 | 1910.8108 | 5474.8509 | 209991.3199 | 217376.9816 | 316.4567 | 5109.0115 | 12.38 | 99.01%
[5 empty] | 12.39 | 246000 | 396 | 100% | 100% | 98.32% | 0.99109 | 1910.8108 | 5474.8509 | 210543.6485 | 217929.3102 | 318.7064 | 5145.333 | 12.39 | 99.26%
[5 empty] | 12.4 | 246000 | 396 | 100% | 100% | 98.89% | 0.99413 | 1910.8108 | 5474.8509 | 211095.9771 | 218481.6388 | 320.9619 | 5181.7466 | 12.4 | 99.52%
[5 empty] | 12.41 | 246000 | 396 | 100% | 100% | 99.47% | 0.99718 | 1910.8108 | 5474.8509 | 211648.3057 | 219033.9675 | 323.2231 | 5218.2523 | 12.41 | 99.77%
[5 empty] | 12.42 | 246000 | 396 | 100% | 100% | 100% | 1.0002 | 1910.8108 | 5474.8509 | 212200.6343 | 219586.2961 | 325.49 | 5254.85 | 12.42 | 100%
[5 empty] | 12.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 327.7565 | 5291.4409 | 12.43 | 100%
[5 empty] | 12.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 330.023 | 5328.0319 | 12.44 | 100%
[5 empty] | 12.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 332.2895 | 5364.6228 | 12.45 | 100%
[5 empty] | 12.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 334.5559 | 5401.2138 | 12.46 | 100%
[5 empty] | 12.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 336.8224 | 5437.8047 | 12.47 | 100%
[5 empty] | 12.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 339.0889 | 5474.3957 | 12.48 | 100%
[5 empty] | 12.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 341.3554 | 5510.9866 | 12.49 | 100%
[5 empty] | 12.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 343.6218 | 5547.5775 | 12.5 | 100%
[5 empty] | 12.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 345.8883 | 5584.1685 | 12.51 | 100%
[5 empty] | 12.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 348.1548 | 5620.7594 | 12.52 | 100%
[5 empty] | 12.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 350.4213 | 5657.3504 | 12.53 | 100%
[5 empty] | 12.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 352.6877 | 5693.9413 | 12.54 | 100%
[5 empty] | 12.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 354.9542 | 5730.5323 | 12.55 | 100%
[5 empty] | 12.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 357.2207 | 5767.1232 | 12.56 | 100%
[5 empty] | 12.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 359.4872 | 5803.7141 | 12.57 | 100%
[5 empty] | 12.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 361.7536 | 5840.3051 | 12.58 | 100%
[5 empty] | 12.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 364.0201 | 5876.896 | 12.59 | 100%
[5 empty] | 12.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 366.2866 | 5913.487 | 12.6 | 100%
[5 empty] | 12.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 368.5531 | 5950.0779 | 12.61 | 100%
[5 empty] | 12.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 370.8195 | 5986.6689 | 12.62 | 100%
[5 empty] | 12.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 373.086 | 6023.2598 | 12.63 | 100%
[5 empty] | 12.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 375.3525 | 6059.8508 | 12.64 | 100%
[5 empty] | 12.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 377.619 | 6096.4417 | 12.65 | 100%
[5 empty] | 12.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 379.8854 | 6133.0326 | 12.66 | 100%
[5 empty] | 12.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 382.1519 | 6169.6236 | 12.67 | 100%
[5 empty] | 12.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 384.4184 | 6206.2145 | 12.68 | 100%
[5 empty] | 12.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 386.6849 | 6242.8055 | 12.69 | 100%
[5 empty] | 12.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 388.9513 | 6279.3964 | 12.7 | 100%
[5 empty] | 12.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 391.2178 | 6315.9874 | 12.71 | 100%
[5 empty] | 12.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 393.4843 | 6352.5783 | 12.72 | 100%
[5 empty] | 12.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 395.7508 | 6389.1692 | 12.73 | 100%
[5 empty] | 12.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 398.0172 | 6425.7602 | 12.74 | 100%
[5 empty] | 12.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 400.2837 | 6462.3511 | 12.75 | 100%
[5 empty] | 12.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 402.5502 | 6498.9421 | 12.76 | 100%
[5 empty] | 12.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 404.8167 | 6535.533 | 12.77 | 100%
[5 empty] | 12.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 407.0831 | 6572.124 | 12.78 | 100%
[5 empty] | 12.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 409.3496 | 6608.7149 | 12.79 | 100%
[5 empty] | 12.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 411.6161 | 6645.3058 | 12.8 | 100%
[5 empty] | 12.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 413.8826 | 6681.8968 | 12.81 | 100%
[5 empty] | 12.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 416.149 | 6718.4877 | 12.82 | 100%
[5 empty] | 12.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 418.4155 | 6755.0787 | 12.83 | 100%
[5 empty] | 12.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 420.682 | 6791.6696 | 12.84 | 100%
[5 empty] | 12.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 422.9485 | 6828.2606 | 12.85 | 100%
[5 empty] | 12.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 425.2149 | 6864.8515 | 12.86 | 100%
[5 empty] | 12.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 427.4814 | 6901.4425 | 12.87 | 100%
[5 empty] | 12.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 429.7479 | 6938.0334 | 12.88 | 100%
[5 empty] | 12.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 432.0144 | 6974.6243 | 12.89 | 100%
[5 empty] | 12.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 434.2808 | 7011.2153 | 12.9 | 100%
[5 empty] | 12.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 436.5473 | 7047.8062 | 12.91 | 100%
[5 empty] | 12.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 438.8138 | 7084.3972 | 12.92 | 100%
[5 empty] | 12.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 441.0803 | 7120.9881 | 12.93 | 100%
[5 empty] | 12.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 443.3467 | 7157.5791 | 12.94 | 100%
[5 empty] | 12.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 445.6132 | 7194.17 | 12.95 | 100%
[5 empty] | 12.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 447.8797 | 7230.7609 | 12.96 | 100%
[5 empty] | 12.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 450.1462 | 7267.3519 | 12.97 | 100%
[5 empty] | 12.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 452.4126 | 7303.9428 | 12.98 | 100%
[5 empty] | 12.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 454.6791 | 7340.5338 | 12.99 | 100%
[5 empty] | 13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 456.9456 | 7377.1247 | 13 | 100%
[5 empty] | 13.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 459.2121 | 7413.7157 | 13.01 | 100%
[5 empty] | 13.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 461.4785 | 7450.3066 | 13.02 | 100%
[5 empty] | 13.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 463.745 | 7486.8976 | 13.03 | 100%
[5 empty] | 13.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 466.0115 | 7523.4885 | 13.04 | 100%
[5 empty] | 13.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 468.278 | 7560.0794 | 13.05 | 100%
[5 empty] | 13.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 470.5444 | 7596.6704 | 13.06 | 100%
[5 empty] | 13.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 472.8109 | 7633.2613 | 13.07 | 100%
[5 empty] | 13.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 475.0774 | 7669.8523 | 13.08 | 100%
[5 empty] | 13.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 477.3439 | 7706.4432 | 13.09 | 100%
[5 empty] | 13.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 479.6103 | 7743.0342 | 13.1 | 100%
[5 empty] | 13.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 481.8768 | 7779.6251 | 13.11 | 100%
[5 empty] | 13.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 484.1433 | 7816.216 | 13.12 | 100%
[5 empty] | 13.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 486.4098 | 7852.807 | 13.13 | 100%
[5 empty] | 13.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 488.6762 | 7889.3979 | 13.14 | 100%
[5 empty] | 13.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 490.9427 | 7925.9889 | 13.15 | 100%
[5 empty] | 13.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 493.2092 | 7962.5798 | 13.16 | 100%
[5 empty] | 13.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 495.4757 | 7999.1708 | 13.17 | 100%
[5 empty] | 13.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 497.7421 | 8035.7617 | 13.18 | 100%
[5 empty] | 13.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 500.0086 | 8072.3527 | 13.19 | 100%
[5 empty] | 13.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 502.2751 | 8108.9436 | 13.2 | 100%
[5 empty] | 13.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 504.5416 | 8145.5345 | 13.21 | 100%
[5 empty] | 13.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 506.808 | 8182.1255 | 13.22 | 100%
[5 empty] | 13.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 509.0745 | 8218.7164 | 13.23 | 100%
[5 empty] | 13.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 511.341 | 8255.3074 | 13.24 | 100%
[5 empty] | 13.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 513.6075 | 8291.8983 | 13.25 | 100%
[5 empty] | 13.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 515.8739 | 8328.4893 | 13.26 | 100%
[5 empty] | 13.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 518.1404 | 8365.0802 | 13.27 | 100%
[5 empty] | 13.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 520.4069 | 8401.6711 | 13.28 | 100%
[5 empty] | 13.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 522.6734 | 8438.2621 | 13.29 | 100%
[5 empty] | 13.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 524.9398 | 8474.853 | 13.3 | 100%
[5 empty] | 13.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 527.2063 | 8511.444 | 13.31 | 100%
[5 empty] | 13.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 529.4728 | 8548.0349 | 13.32 | 100%
[5 empty] | 13.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 531.7393 | 8584.6259 | 13.33 | 100%
[5 empty] | 13.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 534.0057 | 8621.2168 | 13.34 | 100%
[5 empty] | 13.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 536.2722 | 8657.8077 | 13.35 | 100%
[5 empty] | 13.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 538.5387 | 8694.3987 | 13.36 | 100%
[5 empty] | 13.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 540.8052 | 8730.9896 | 13.37 | 100%
[5 empty] | 13.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 543.0716 | 8767.5806 | 13.38 | 100%
[5 empty] | 13.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 545.3381 | 8804.1715 | 13.39 | 100%
[5 empty] | 13.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 547.6046 | 8840.7625 | 13.4 | 100%
[5 empty] | 13.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 549.8711 | 8877.3534 | 13.41 | 100%
[5 empty] | 13.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 552.1375 | 8913.9444 | 13.42 | 100%
[5 empty] | 13.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 554.404 | 8950.5353 | 13.43 | 100%
[5 empty] | 13.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 556.6705 | 8987.1262 | 13.44 | 100%
[5 empty] | 13.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 558.937 | 9023.7172 | 13.45 | 100%
[5 empty] | 13.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 561.2034 | 9060.3081 | 13.46 | 100%
[5 empty] | 13.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 563.4699 | 9096.8991 | 13.47 | 100%
[5 empty] | 13.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 565.7364 | 9133.49 | 13.48 | 100%
[5 empty] | 13.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 568.0029 | 9170.081 | 13.49 | 100%
[5 empty] | 13.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 570.2693 | 9206.6719 | 13.5 | 100%
[5 empty] | 13.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 572.5358 | 9243.2628 | 13.51 | 100%
[5 empty] | 13.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 574.8023 | 9279.8538 | 13.52 | 100%
[5 empty] | 13.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 577.0688 | 9316.4447 | 13.53 | 100%
[5 empty] | 13.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 579.3353 | 9353.0357 | 13.54 | 100%
[5 empty] | 13.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 581.6017 | 9389.6266 | 13.55 | 100%
[5 empty] | 13.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 583.8682 | 9426.2176 | 13.56 | 100%
[5 empty] | 13.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 586.1347 | 9462.8085 | 13.57 | 100%
[5 empty] | 13.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 588.4012 | 9499.3995 | 13.58 | 100%
[5 empty] | 13.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 590.6676 | 9535.9904 | 13.59 | 100%
[5 empty] | 13.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 592.9341 | 9572.5813 | 13.6 | 100%
[5 empty] | 13.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 595.2006 | 9609.1723 | 13.61 | 100%
[5 empty] | 13.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 597.4671 | 9645.7632 | 13.62 | 100%
[5 empty] | 13.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 599.7335 | 9682.3542 | 13.63 | 100%
[5 empty] | 13.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 602 | 9718.9451 | 13.64 | 100%
[5 empty] | 13.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 604.2665 | 9755.5361 | 13.65 | 100%
[5 empty] | 13.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 606.533 | 9792.127 | 13.66 | 100%
[5 empty] | 13.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 608.7994 | 9828.7179 | 13.67 | 100%
[5 empty] | 13.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 611.0659 | 9865.3089 | 13.68 | 100%
[5 empty] | 13.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 613.3324 | 9901.8998 | 13.69 | 100%
[5 empty] | 13.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 615.5989 | 9938.4908 | 13.7 | 100%
[5 empty] | 13.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 617.8653 | 9975.0817 | 13.71 | 100%
[5 empty] | 13.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 620.1318 | 10011.6727 | 13.72 | 100%
[5 empty] | 13.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 622.3983 | 10048.2636 | 13.73 | 100%
[5 empty] | 13.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 624.6648 | 10084.8546 | 13.74 | 100%
[5 empty] | 13.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 626.9312 | 10121.4455 | 13.75 | 100%
[5 empty] | 13.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 629.1977 | 10158.0364 | 13.76 | 100%
[5 empty] | 13.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 631.4642 | 10194.6274 | 13.77 | 100%
[5 empty] | 13.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 633.7307 | 10231.2183 | 13.78 | 100%
[5 empty] | 13.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 635.9971 | 10267.8093 | 13.79 | 100%
[5 empty] | 13.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 638.2636 | 10304.4002 | 13.8 | 100%
[5 empty] | 13.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 640.5301 | 10340.9912 | 13.81 | 100%
[5 empty] | 13.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 642.7966 | 10377.5821 | 13.82 | 100%
[5 empty] | 13.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 645.063 | 10414.173 | 13.83 | 100%
[5 empty] | 13.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 647.3295 | 10450.764 | 13.84 | 100%
[5 empty] | 13.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 649.596 | 10487.3549 | 13.85 | 100%
[5 empty] | 13.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 651.8625 | 10523.9459 | 13.86 | 100%
[5 empty] | 13.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 654.1289 | 10560.5368 | 13.87 | 100%
[5 empty] | 13.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 656.3954 | 10597.1278 | 13.88 | 100%
[5 empty] | 13.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 658.6619 | 10633.7187 | 13.89 | 100%
[5 empty] | 13.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 660.9284 | 10670.3096 | 13.9 | 100%
[5 empty] | 13.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 663.1948 | 10706.9006 | 13.91 | 100%
[5 empty] | 13.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 665.4613 | 10743.4915 | 13.92 | 100%
[5 empty] | 13.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 667.7278 | 10780.0825 | 13.93 | 100%
[5 empty] | 13.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 669.9943 | 10816.6734 | 13.94 | 100%
[5 empty] | 13.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 672.2607 | 10853.2644 | 13.95 | 100%
[5 empty] | 13.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 674.5272 | 10889.8553 | 13.96 | 100%
[5 empty] | 13.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 676.7937 | 10926.4463 | 13.97 | 100%
[5 empty] | 13.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 679.0602 | 10963.0372 | 13.98 | 100%
[5 empty] | 13.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 681.3266 | 10999.6281 | 13.99 | 100%
[5 empty] | 14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 683.5931 | 11036.2191 | 14 | 100%
[5 empty] | 14.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 685.8596 | 11072.81 | 14.01 | 100%
[5 empty] | 14.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 688.1261 | 11109.401 | 14.02 | 100%
[5 empty] | 14.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 690.3925 | 11145.9919 | 14.03 | 100%
[5 empty] | 14.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 692.659 | 11182.5829 | 14.04 | 100%
[5 empty] | 14.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 694.9255 | 11219.1738 | 14.05 | 100%
[5 empty] | 14.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 697.192 | 11255.7647 | 14.06 | 100%
[5 empty] | 14.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 699.4584 | 11292.3557 | 14.07 | 100%
[5 empty] | 14.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 701.7249 | 11328.9466 | 14.08 | 100%
[5 empty] | 14.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 703.9914 | 11365.5376 | 14.09 | 100%
[5 empty] | 14.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 706.2579 | 11402.1285 | 14.1 | 100%
[5 empty] | 14.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 708.5243 | 11438.7195 | 14.11 | 100%
[5 empty] | 14.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 710.7908 | 11475.3104 | 14.12 | 100%
[5 empty] | 14.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 713.0573 | 11511.9014 | 14.13 | 100%
[5 empty] | 14.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 715.3238 | 11548.4923 | 14.14 | 100%
[5 empty] | 14.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 717.5902 | 11585.0832 | 14.15 | 100%
[5 empty] | 14.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 719.8567 | 11621.6742 | 14.16 | 100%
[5 empty] | 14.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 722.1232 | 11658.2651 | 14.17 | 100%
[5 empty] | 14.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 724.3897 | 11694.8561 | 14.18 | 100%
[5 empty] | 14.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 726.6561 | 11731.447 | 14.19 | 100%
[5 empty] | 14.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 728.9226 | 11768.038 | 14.2 | 100%
[5 empty] | 14.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 731.1891 | 11804.6289 | 14.21 | 100%
[5 empty] | 14.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 733.4556 | 11841.2198 | 14.22 | 100%
[5 empty] | 14.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 735.722 | 11877.8108 | 14.23 | 100%
[5 empty] | 14.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 737.9885 | 11914.4017 | 14.24 | 100%
[5 empty] | 14.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 740.255 | 11950.9927 | 14.25 | 100%
[5 empty] | 14.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 742.5215 | 11987.5836 | 14.26 | 100%
[5 empty] | 14.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 744.7879 | 12024.1746 | 14.27 | 100%
[5 empty] | 14.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 747.0544 | 12060.7655 | 14.28 | 100%
[5 empty] | 14.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 749.3209 | 12097.3564 | 14.29 | 100%
[5 empty] | 14.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 751.5874 | 12133.9474 | 14.3 | 100%
[5 empty] | 14.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 753.8538 | 12170.5383 | 14.31 | 100%
[5 empty] | 14.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 756.1203 | 12207.1293 | 14.32 | 100%
[5 empty] | 14.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 758.3868 | 12243.7202 | 14.33 | 100%
[5 empty] | 14.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 760.6533 | 12280.3112 | 14.34 | 100%
[5 empty] | 14.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 762.9197 | 12316.9021 | 14.35 | 100%
[5 empty] | 14.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 765.1862 | 12353.4931 | 14.36 | 100%
[5 empty] | 14.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 767.4527 | 12390.084 | 14.37 | 100%
[5 empty] | 14.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 769.7192 | 12426.6749 | 14.38 | 100%
[5 empty] | 14.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 771.9856 | 12463.2659 | 14.39 | 100%
[5 empty] | 14.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 774.2521 | 12499.8568 | 14.4 | 100%
[5 empty] | 14.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 776.5186 | 12536.4478 | 14.41 | 100%
[5 empty] | 14.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 778.7851 | 12573.0387 | 14.42 | 100%
[5 empty] | 14.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 781.0515 | 12609.6297 | 14.43 | 100%
[5 empty] | 14.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 783.318 | 12646.2206 | 14.44 | 100%
[5 empty] | 14.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 785.5845 | 12682.8115 | 14.45 | 100%
[5 empty] | 14.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 787.851 | 12719.4025 | 14.46 | 100%
[5 empty] | 14.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 790.1174 | 12755.9934 | 14.47 | 100%
[5 empty] | 14.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 792.3839 | 12792.5844 | 14.48 | 100%
[5 empty] | 14.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 794.6504 | 12829.1753 | 14.49 | 100%
[5 empty] | 14.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 796.9169 | 12865.7663 | 14.5 | 100%
[5 empty] | 14.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 799.1833 | 12902.3572 | 14.51 | 100%
[5 empty] | 14.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 801.4498 | 12938.9482 | 14.52 | 100%
[5 empty] | 14.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 803.7163 | 12975.5391 | 14.53 | 100%
[5 empty] | 14.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 805.9828 | 13012.13 | 14.54 | 100%
[5 empty] | 14.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 808.2492 | 13048.721 | 14.55 | 100%
[5 empty] | 14.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 810.5157 | 13085.3119 | 14.56 | 100%
[5 empty] | 14.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 812.7822 | 13121.9029 | 14.57 | 100%
[5 empty] | 14.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 815.0487 | 13158.4938 | 14.58 | 100%
[5 empty] | 14.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 817.3151 | 13195.0848 | 14.59 | 100%
[5 empty] | 14.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 819.5816 | 13231.6757 | 14.6 | 100%
[5 empty] | 14.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 821.8481 | 13268.2666 | 14.61 | 100%
[5 empty] | 14.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 824.1146 | 13304.8576 | 14.62 | 100%
[5 empty] | 14.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 826.381 | 13341.4485 | 14.63 | 100%
[5 empty] | 14.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 828.6475 | 13378.0395 | 14.64 | 100%
[5 empty] | 14.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 830.914 | 13414.6304 | 14.65 | 100%
[5 empty] | 14.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 833.1805 | 13451.2214 | 14.66 | 100%
[5 empty] | 14.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 835.4469 | 13487.8123 | 14.67 | 100%
[5 empty] | 14.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 837.7134 | 13524.4033 | 14.68 | 100%
[5 empty] | 14.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 839.9799 | 13560.9942 | 14.69 | 100%
[5 empty] | 14.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 842.2464 | 13597.5851 | 14.7 | 100%
[5 empty] | 14.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 844.5129 | 13634.1761 | 14.71 | 100%
[5 empty] | 14.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 846.7793 | 13670.767 | 14.72 | 100%
[5 empty] | 14.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 849.0458 | 13707.358 | 14.73 | 100%
[5 empty] | 14.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 851.3123 | 13743.9489 | 14.74 | 100%
[5 empty] | 14.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 853.5788 | 13780.5399 | 14.75 | 100%
[5 empty] | 14.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 855.8452 | 13817.1308 | 14.76 | 100%
[5 empty] | 14.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 858.1117 | 13853.7217 | 14.77 | 100%
[5 empty] | 14.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 860.3782 | 13890.3127 | 14.78 | 100%
[5 empty] | 14.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 862.6447 | 13926.9036 | 14.79 | 100%
[5 empty] | 14.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 864.9111 | 13963.4946 | 14.8 | 100%
[5 empty] | 14.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 867.1776 | 14000.0855 | 14.81 | 100%
[5 empty] | 14.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 869.4441 | 14036.6765 | 14.82 | 100%
[5 empty] | 14.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 871.7106 | 14073.2674 | 14.83 | 100%
[5 empty] | 14.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 873.977 | 14109.8583 | 14.84 | 100%
[5 empty] | 14.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 876.2435 | 14146.4493 | 14.85 | 100%
[5 empty] | 14.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 878.51 | 14183.0402 | 14.86 | 100%
[5 empty] | 14.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 880.7765 | 14219.6312 | 14.87 | 100%
[5 empty] | 14.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 883.0429 | 14256.2221 | 14.88 | 100%
[5 empty] | 14.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 885.3094 | 14292.8131 | 14.89 | 100%
[5 empty] | 14.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 887.5759 | 14329.404 | 14.9 | 100%
[5 empty] | 14.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 889.8424 | 14365.995 | 14.91 | 100%
[5 empty] | 14.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 892.1088 | 14402.5859 | 14.92 | 100%
[5 empty] | 14.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 894.3753 | 14439.1768 | 14.93 | 100%
[5 empty] | 14.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 896.6418 | 14475.7678 | 14.94 | 100%
[5 empty] | 14.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 898.9083 | 14512.3587 | 14.95 | 100%
[5 empty] | 14.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 901.1747 | 14548.9497 | 14.96 | 100%
[5 empty] | 14.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 903.4412 | 14585.5406 | 14.97 | 100%
[5 empty] | 14.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 905.7077 | 14622.1316 | 14.98 | 100%
[5 empty] | 14.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 907.9742 | 14658.7225 | 14.99 | 100%
[5 empty] | 15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 910.2406 | 14695.3134 | 15 | 100%
[5 empty] | 15.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 912.5071 | 14731.9044 | 15.01 | 100%
[5 empty] | 15.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 914.7736 | 14768.4953 | 15.02 | 100%
[5 empty] | 15.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 917.0401 | 14805.0863 | 15.03 | 100%
[5 empty] | 15.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 919.3065 | 14841.6772 | 15.04 | 100%
[5 empty] | 15.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 921.573 | 14878.2682 | 15.05 | 100%
[5 empty] | 15.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 923.8395 | 14914.8591 | 15.06 | 100%
[5 empty] | 15.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 926.106 | 14951.4501 | 15.07 | 100%
[5 empty] | 15.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 928.3724 | 14988.041 | 15.08 | 100%
[5 empty] | 15.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 930.6389 | 15024.6319 | 15.09 | 100%
[5 empty] | 15.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 932.9054 | 15061.2229 | 15.1 | 100%
[5 empty] | 15.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 935.1719 | 15097.8138 | 15.11 | 100%
[5 empty] | 15.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 937.4383 | 15134.4048 | 15.12 | 100%
[5 empty] | 15.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 939.7048 | 15170.9957 | 15.13 | 100%
[5 empty] | 15.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 941.9713 | 15207.5867 | 15.14 | 100%
[5 empty] | 15.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 944.2378 | 15244.1776 | 15.15 | 100%
[5 empty] | 15.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 946.5042 | 15280.7685 | 15.16 | 100%
[5 empty] | 15.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 948.7707 | 15317.3595 | 15.17 | 100%
[5 empty] | 15.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 951.0372 | 15353.9504 | 15.18 | 100%
[5 empty] | 15.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 953.3037 | 15390.5414 | 15.19 | 100%
[5 empty] | 15.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 955.5701 | 15427.1323 | 15.2 | 100%
[5 empty] | 15.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 957.8366 | 15463.7233 | 15.21 | 100%
[5 empty] | 15.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 960.1031 | 15500.3142 | 15.22 | 100%
[5 empty] | 15.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 962.3696 | 15536.9052 | 15.23 | 100%
[5 empty] | 15.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 964.636 | 15573.4961 | 15.24 | 100%
[5 empty] | 15.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 966.9025 | 15610.087 | 15.25 | 100%
[5 empty] | 15.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 969.169 | 15646.678 | 15.26 | 100%
[5 empty] | 15.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 971.4355 | 15683.2689 | 15.27 | 100%
[5 empty] | 15.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 973.7019 | 15719.8599 | 15.28 | 100%
[5 empty] | 15.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 975.9684 | 15756.4508 | 15.29 | 100%
[5 empty] | 15.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 978.2349 | 15793.0418 | 15.3 | 100%
[5 empty] | 15.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 980.5014 | 15829.6327 | 15.31 | 100%
[5 empty] | 15.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 982.7678 | 15866.2236 | 15.32 | 100%
[5 empty] | 15.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 985.0343 | 15902.8146 | 15.33 | 100%
[5 empty] | 15.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 987.3008 | 15939.4055 | 15.34 | 100%
[5 empty] | 15.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 989.5673 | 15975.9965 | 15.35 | 100%
[5 empty] | 15.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 991.8337 | 16012.5874 | 15.36 | 100%
[5 empty] | 15.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 994.1002 | 16049.1784 | 15.37 | 100%
[5 empty] | 15.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 996.3667 | 16085.7693 | 15.38 | 100%
[5 empty] | 15.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 998.6332 | 16122.3602 | 15.39 | 100%
[5 empty] | 15.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1000.8996 | 16158.9512 | 15.4 | 100%
[5 empty] | 15.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1003.1661 | 16195.5421 | 15.41 | 100%
[5 empty] | 15.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1005.4326 | 16232.1331 | 15.42 | 100%
[5 empty] | 15.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1007.6991 | 16268.724 | 15.43 | 100%
[5 empty] | 15.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1009.9655 | 16305.315 | 15.44 | 100%
[5 empty] | 15.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1012.232 | 16341.9059 | 15.45 | 100%
[5 empty] | 15.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1014.4985 | 16378.4969 | 15.46 | 100%
[5 empty] | 15.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1016.765 | 16415.0878 | 15.47 | 100%
[5 empty] | 15.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1019.0314 | 16451.6787 | 15.48 | 100%
[5 empty] | 15.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1021.2979 | 16488.2697 | 15.49 | 100%
[5 empty] | 15.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1023.5644 | 16524.8606 | 15.5 | 100%
[5 empty] | 15.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1025.8309 | 16561.4516 | 15.51 | 100%
[5 empty] | 15.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1028.0973 | 16598.0425 | 15.52 | 100%
[5 empty] | 15.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1030.3638 | 16634.6335 | 15.53 | 100%
[5 empty] | 15.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1032.6303 | 16671.2244 | 15.54 | 100%
[5 empty] | 15.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1034.8968 | 16707.8153 | 15.55 | 100%
[5 empty] | 15.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1037.1632 | 16744.4063 | 15.56 | 100%
[5 empty] | 15.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1039.4297 | 16780.9972 | 15.57 | 100%
[5 empty] | 15.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1041.6962 | 16817.5882 | 15.58 | 100%
[5 empty] | 15.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1043.9627 | 16854.1791 | 15.59 | 100%
[5 empty] | 15.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1046.2291 | 16890.7701 | 15.6 | 100%
[5 empty] | 15.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1048.4956 | 16927.361 | 15.61 | 100%
[5 empty] | 15.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1050.7621 | 16963.952 | 15.62 | 100%
[5 empty] | 15.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1053.0286 | 17000.5429 | 15.63 | 100%
[5 empty] | 15.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1055.295 | 17037.1338 | 15.64 | 100%
[5 empty] | 15.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1057.5615 | 17073.7248 | 15.65 | 100%
[5 empty] | 15.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1059.828 | 17110.3157 | 15.66 | 100%
[5 empty] | 15.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1062.0945 | 17146.9067 | 15.67 | 100%
[5 empty] | 15.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1064.3609 | 17183.4976 | 15.68 | 100%
[5 empty] | 15.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1066.6274 | 17220.0886 | 15.69 | 100%
[5 empty] | 15.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1068.8939 | 17256.6795 | 15.7 | 100%
[5 empty] | 15.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1071.1604 | 17293.2704 | 15.71 | 100%
[5 empty] | 15.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1073.4268 | 17329.8614 | 15.72 | 100%
[5 empty] | 15.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1075.6933 | 17366.4523 | 15.73 | 100%
[5 empty] | 15.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1077.9598 | 17403.0433 | 15.74 | 100%
[5 empty] | 15.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1080.2263 | 17439.6342 | 15.75 | 100%
[5 empty] | 15.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1082.4927 | 17476.2252 | 15.76 | 100%
[5 empty] | 15.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1084.7592 | 17512.8161 | 15.77 | 100%
[5 empty] | 15.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1087.0257 | 17549.4071 | 15.78 | 100%
[5 empty] | 15.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1089.2922 | 17585.998 | 15.79 | 100%
[5 empty] | 15.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1091.5586 | 17622.5889 | 15.8 | 100%
[5 empty] | 15.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1093.8251 | 17659.1799 | 15.81 | 100%
[5 empty] | 15.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1096.0916 | 17695.7708 | 15.82 | 100%
[5 empty] | 15.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1098.3581 | 17732.3618 | 15.83 | 100%
[5 empty] | 15.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1100.6245 | 17768.9527 | 15.84 | 100%
[5 empty] | 15.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1102.891 | 17805.5437 | 15.85 | 100%
[5 empty] | 15.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1105.1575 | 17842.1346 | 15.86 | 100%
[5 empty] | 15.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1107.424 | 17878.7255 | 15.87 | 100%
[5 empty] | 15.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1109.6904 | 17915.3165 | 15.88 | 100%
[5 empty] | 15.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1111.9569 | 17951.9074 | 15.89 | 100%
[5 empty] | 15.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1114.2234 | 17988.4984 | 15.9 | 100%
[5 empty] | 15.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1116.4899 | 18025.0893 | 15.91 | 100%
[5 empty] | 15.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1118.7564 | 18061.6803 | 15.92 | 100%
[5 empty] | 15.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1121.0228 | 18098.2712 | 15.93 | 100%
[5 empty] | 15.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1123.2893 | 18134.8621 | 15.94 | 100%
[5 empty] | 15.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1125.5558 | 18171.4531 | 15.95 | 100%
[5 empty] | 15.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1127.8223 | 18208.044 | 15.96 | 100%
[5 empty] | 15.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1130.0887 | 18244.635 | 15.97 | 100%
[5 empty] | 15.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1132.3552 | 18281.2259 | 15.98 | 100%
[5 empty] | 15.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1134.6217 | 18317.8169 | 15.99 | 100%
[5 empty] | 16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1136.8882 | 18354.4078 | 16 | 100%
[5 empty] | 16.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1139.1546 | 18390.9988 | 16.01 | 100%
[5 empty] | 16.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1141.4211 | 18427.5897 | 16.02 | 100%
[5 empty] | 16.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1143.6876 | 18464.1806 | 16.03 | 100%
[5 empty] | 16.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1145.9541 | 18500.7716 | 16.04 | 100%
[5 empty] | 16.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1148.2205 | 18537.3625 | 16.05 | 100%
[5 empty] | 16.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1150.487 | 18573.9535 | 16.06 | 100%
[5 empty] | 16.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1152.7535 | 18610.5444 | 16.07 | 100%
[5 empty] | 16.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1155.02 | 18647.1354 | 16.08 | 100%
[5 empty] | 16.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1157.2864 | 18683.7263 | 16.09 | 100%
[5 empty] | 16.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1159.5529 | 18720.3172 | 16.1 | 100%
[5 empty] | 16.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1161.8194 | 18756.9082 | 16.11 | 100%
[5 empty] | 16.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1164.0859 | 18793.4991 | 16.12 | 100%
[5 empty] | 16.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1166.3523 | 18830.0901 | 16.13 | 100%
[5 empty] | 16.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1168.6188 | 18866.681 | 16.14 | 100%
[5 empty] | 16.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1170.8853 | 18903.272 | 16.15 | 100%
[5 empty] | 16.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1173.1518 | 18939.8629 | 16.16 | 100%
[5 empty] | 16.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1175.4182 | 18976.4539 | 16.17 | 100%
[5 empty] | 16.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1177.6847 | 19013.0448 | 16.18 | 100%
[5 empty] | 16.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1179.9512 | 19049.6357 | 16.19 | 100%
[5 empty] | 16.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1182.2177 | 19086.2267 | 16.2 | 100%
[5 empty] | 16.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1184.4841 | 19122.8176 | 16.21 | 100%
[5 empty] | 16.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1186.7506 | 19159.4086 | 16.22 | 100%
[5 empty] | 16.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1189.0171 | 19195.9995 | 16.23 | 100%
[5 empty] | 16.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1191.2836 | 19232.5905 | 16.24 | 100%
[5 empty] | 16.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1193.55 | 19269.1814 | 16.25 | 100%
[5 empty] | 16.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1195.8165 | 19305.7723 | 16.26 | 100%
[5 empty] | 16.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1198.083 | 19342.3633 | 16.27 | 100%
[5 empty] | 16.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1200.3495 | 19378.9542 | 16.28 | 100%
[5 empty] | 16.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1202.6159 | 19415.5452 | 16.29 | 100%
[5 empty] | 16.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1204.8824 | 19452.1361 | 16.3 | 100%
[5 empty] | 16.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1207.1489 | 19488.7271 | 16.31 | 100%
[5 empty] | 16.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1209.4154 | 19525.318 | 16.32 | 100%
[5 empty] | 16.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1211.6818 | 19561.9089 | 16.33 | 100%
[5 empty] | 16.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1213.9483 | 19598.4999 | 16.34 | 100%
[5 empty] | 16.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1216.2148 | 19635.0908 | 16.35 | 100%
[5 empty] | 16.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1218.4813 | 19671.6818 | 16.36 | 100%
[5 empty] | 16.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1220.7477 | 19708.2727 | 16.37 | 100%
[5 empty] | 16.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1223.0142 | 19744.8637 | 16.38 | 100%
[5 empty] | 16.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1225.2807 | 19781.4546 | 16.39 | 100%
[5 empty] | 16.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1227.5472 | 19818.0456 | 16.4 | 100%
[5 empty] | 16.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1229.8136 | 19854.6365 | 16.41 | 100%
[5 empty] | 16.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1232.0801 | 19891.2274 | 16.42 | 100%
[5 empty] | 16.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1234.3466 | 19927.8184 | 16.43 | 100%
[5 empty] | 16.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1236.6131 | 19964.4093 | 16.44 | 100%
[5 empty] | 16.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1238.8795 | 20001.0003 | 16.45 | 100%
[5 empty] | 16.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1241.146 | 20037.5912 | 16.46 | 100%
[5 empty] | 16.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1243.4125 | 20074.1822 | 16.47 | 100%
[5 empty] | 16.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1245.679 | 20110.7731 | 16.48 | 100%
[5 empty] | 16.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1247.9454 | 20147.364 | 16.49 | 100%
[5 empty] | 16.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1250.2119 | 20183.955 | 16.5 | 100%
[5 empty] | 16.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1252.4784 | 20220.5459 | 16.51 | 100%
[5 empty] | 16.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1254.7449 | 20257.1369 | 16.52 | 100%
[5 empty] | 16.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1257.0113 | 20293.7278 | 16.53 | 100%
[5 empty] | 16.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1259.2778 | 20330.3188 | 16.54 | 100%
[5 empty] | 16.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1261.5443 | 20366.9097 | 16.55 | 100%
[5 empty] | 16.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1263.8108 | 20403.5007 | 16.56 | 100%
[5 empty] | 16.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1266.0772 | 20440.0916 | 16.57 | 100%
[5 empty] | 16.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1268.3437 | 20476.6825 | 16.58 | 100%
[5 empty] | 16.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1270.6102 | 20513.2735 | 16.59 | 100%
[5 empty] | 16.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1272.8767 | 20549.8644 | 16.6 | 100%
[5 empty] | 16.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1275.1431 | 20586.4554 | 16.61 | 100%
[5 empty] | 16.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1277.4096 | 20623.0463 | 16.62 | 100%
[5 empty] | 16.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1279.6761 | 20659.6373 | 16.63 | 100%
[5 empty] | 16.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1281.9426 | 20696.2282 | 16.64 | 100%
[5 empty] | 16.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1284.209 | 20732.8191 | 16.65 | 100%
[5 empty] | 16.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1286.4755 | 20769.4101 | 16.66 | 100%
[5 empty] | 16.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1288.742 | 20806.001 | 16.67 | 100%
[5 empty] | 16.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1291.0085 | 20842.592 | 16.68 | 100%
[5 empty] | 16.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1293.2749 | 20879.1829 | 16.69 | 100%
[5 empty] | 16.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1295.5414 | 20915.7739 | 16.7 | 100%
[5 empty] | 16.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1297.8079 | 20952.3648 | 16.71 | 100%
[5 empty] | 16.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1300.0744 | 20988.9558 | 16.72 | 100%
[5 empty] | 16.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1302.3408 | 21025.5467 | 16.73 | 100%
[5 empty] | 16.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1304.6073 | 21062.1376 | 16.74 | 100%
[5 empty] | 16.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1306.8738 | 21098.7286 | 16.75 | 100%
[5 empty] | 16.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1309.1403 | 21135.3195 | 16.76 | 100%
[5 empty] | 16.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1311.4067 | 21171.9105 | 16.77 | 100%
[5 empty] | 16.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1313.6732 | 21208.5014 | 16.78 | 100%
[5 empty] | 16.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1315.9397 | 21245.0924 | 16.79 | 100%
[5 empty] | 16.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1318.2062 | 21281.6833 | 16.8 | 100%
[5 empty] | 16.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1320.4726 | 21318.2742 | 16.81 | 100%
[5 empty] | 16.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1322.7391 | 21354.8652 | 16.82 | 100%
[5 empty] | 16.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1325.0056 | 21391.4561 | 16.83 | 100%
[5 empty] | 16.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1327.2721 | 21428.0471 | 16.84 | 100%
[5 empty] | 16.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1329.5385 | 21464.638 | 16.85 | 100%
[5 empty] | 16.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1331.805 | 21501.229 | 16.86 | 100%
[5 empty] | 16.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1334.0715 | 21537.8199 | 16.87 | 100%
[5 empty] | 16.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1336.338 | 21574.4108 | 16.88 | 100%
[5 empty] | 16.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1338.6044 | 21611.0018 | 16.89 | 100%
[5 empty] | 16.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1340.8709 | 21647.5927 | 16.9 | 100%
[5 empty] | 16.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1343.1374 | 21684.1837 | 16.91 | 100%
[5 empty] | 16.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1345.4039 | 21720.7746 | 16.92 | 100%
[5 empty] | 16.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1347.6703 | 21757.3656 | 16.93 | 100%
[5 empty] | 16.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1349.9368 | 21793.9565 | 16.94 | 100%
[5 empty] | 16.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1352.2033 | 21830.5475 | 16.95 | 100%
[5 empty] | 16.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1354.4698 | 21867.1384 | 16.96 | 100%
[5 empty] | 16.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1356.7362 | 21903.7293 | 16.97 | 100%
[5 empty] | 16.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1359.0027 | 21940.3203 | 16.98 | 100%
[5 empty] | 16.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1361.2692 | 21976.9112 | 16.99 | 100%
[5 empty] | 17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1363.5357 | 22013.5022 | 17 | 100%
[5 empty] | 17.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1365.8021 | 22050.0931 | 17.01 | 100%
[5 empty] | 17.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1368.0686 | 22086.6841 | 17.02 | 100%
[5 empty] | 17.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1370.3351 | 22123.275 | 17.03 | 100%
[5 empty] | 17.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1372.6016 | 22159.8659 | 17.04 | 100%
[5 empty] | 17.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1374.868 | 22196.4569 | 17.05 | 100%
[5 empty] | 17.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1377.1345 | 22233.0478 | 17.06 | 100%
[5 empty] | 17.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1379.401 | 22269.6388 | 17.07 | 100%
[5 empty] | 17.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1381.6675 | 22306.2297 | 17.08 | 100%
[5 empty] | 17.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1383.934 | 22342.8207 | 17.09 | 100%
[5 empty] | 17.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1386.2004 | 22379.4116 | 17.1 | 100%
[5 empty] | 17.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1388.4669 | 22416.0026 | 17.11 | 100%
[5 empty] | 17.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1390.7334 | 22452.5935 | 17.12 | 100%
[5 empty] | 17.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1392.9999 | 22489.1844 | 17.13 | 100%
[5 empty] | 17.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1395.2663 | 22525.7754 | 17.14 | 100%
[5 empty] | 17.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1397.5328 | 22562.3663 | 17.15 | 100%
[5 empty] | 17.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1399.7993 | 22598.9573 | 17.16 | 100%
[5 empty] | 17.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1402.0658 | 22635.5482 | 17.17 | 100%
[5 empty] | 17.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1404.3322 | 22672.1392 | 17.18 | 100%
[5 empty] | 17.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1406.5987 | 22708.7301 | 17.19 | 100%
[5 empty] | 17.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1408.8652 | 22745.321 | 17.2 | 100%
[5 empty] | 17.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1411.1317 | 22781.912 | 17.21 | 100%
[5 empty] | 17.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1413.3981 | 22818.5029 | 17.22 | 100%
[5 empty] | 17.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1415.6646 | 22855.0939 | 17.23 | 100%
[5 empty] | 17.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1417.9311 | 22891.6848 | 17.24 | 100%
[5 empty] | 17.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1420.1976 | 22928.2758 | 17.25 | 100%
[5 empty] | 17.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1422.464 | 22964.8667 | 17.26 | 100%
[5 empty] | 17.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1424.7305 | 23001.4577 | 17.27 | 100%
[5 empty] | 17.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1426.997 | 23038.0486 | 17.28 | 100%
[5 empty] | 17.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1429.2635 | 23074.6395 | 17.29 | 100%
[5 empty] | 17.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1431.5299 | 23111.2305 | 17.3 | 100%
[5 empty] | 17.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1433.7964 | 23147.8214 | 17.31 | 100%
[5 empty] | 17.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1436.0629 | 23184.4124 | 17.32 | 100%
[5 empty] | 17.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1438.3294 | 23221.0033 | 17.33 | 100%
[5 empty] | 17.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1440.5958 | 23257.5943 | 17.34 | 100%
[5 empty] | 17.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1442.8623 | 23294.1852 | 17.35 | 100%
[5 empty] | 17.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1445.1288 | 23330.7761 | 17.36 | 100%
[5 empty] | 17.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1447.3953 | 23367.3671 | 17.37 | 100%
[5 empty] | 17.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1449.6617 | 23403.958 | 17.38 | 100%
[5 empty] | 17.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1451.9282 | 23440.549 | 17.39 | 100%
[5 empty] | 17.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1454.1947 | 23477.1399 | 17.4 | 100%
[5 empty] | 17.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1456.4612 | 23513.7309 | 17.41 | 100%
[5 empty] | 17.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1458.7276 | 23550.3218 | 17.42 | 100%
[5 empty] | 17.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1460.9941 | 23586.9127 | 17.43 | 100%
[5 empty] | 17.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1463.2606 | 23623.5037 | 17.44 | 100%
[5 empty] | 17.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1465.5271 | 23660.0946 | 17.45 | 100%
[5 empty] | 17.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1467.7935 | 23696.6856 | 17.46 | 100%
[5 empty] | 17.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1470.06 | 23733.2765 | 17.47 | 100%
[5 empty] | 17.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1472.3265 | 23769.8675 | 17.48 | 100%
[5 empty] | 17.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1474.593 | 23806.4584 | 17.49 | 100%
[5 empty] | 17.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1476.8594 | 23843.0494 | 17.5 | 100%
[5 empty] | 17.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1479.1259 | 23879.6403 | 17.51 | 100%
[5 empty] | 17.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1481.3924 | 23916.2312 | 17.52 | 100%
[5 empty] | 17.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1483.6589 | 23952.8222 | 17.53 | 100%
[5 empty] | 17.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1485.9253 | 23989.4131 | 17.54 | 100%
[5 empty] | 17.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1488.1918 | 24026.0041 | 17.55 | 100%
[5 empty] | 17.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1490.4583 | 24062.595 | 17.56 | 100%
[5 empty] | 17.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1492.7248 | 24099.186 | 17.57 | 100%
[5 empty] | 17.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1494.9912 | 24135.7769 | 17.58 | 100%
[5 empty] | 17.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1497.2577 | 24172.3678 | 17.59 | 100%
[5 empty] | 17.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1499.5242 | 24208.9588 | 17.6 | 100%
[5 empty] | 17.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1501.7907 | 24245.5497 | 17.61 | 100%
[5 empty] | 17.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1504.0571 | 24282.1407 | 17.62 | 100%
[5 empty] | 17.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1506.3236 | 24318.7316 | 17.63 | 100%
[5 empty] | 17.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1508.5901 | 24355.3226 | 17.64 | 100%
[5 empty] | 17.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1510.8566 | 24391.9135 | 17.65 | 100%
[5 empty] | 17.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1513.123 | 24428.5045 | 17.66 | 100%
[5 empty] | 17.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1515.3895 | 24465.0954 | 17.67 | 100%
[5 empty] | 17.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1517.656 | 24501.6863 | 17.68 | 100%
[5 empty] | 17.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1519.9225 | 24538.2773 | 17.69 | 100%
[5 empty] | 17.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1522.1889 | 24574.8682 | 17.7 | 100%
[5 empty] | 17.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1524.4554 | 24611.4592 | 17.71 | 100%
[5 empty] | 17.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1526.7219 | 24648.0501 | 17.72 | 100%
[5 empty] | 17.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1528.9884 | 24684.6411 | 17.73 | 100%
[5 empty] | 17.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1531.2548 | 24721.232 | 17.74 | 100%
[5 empty] | 17.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1533.5213 | 24757.8229 | 17.75 | 100%
[5 empty] | 17.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1535.7878 | 24794.4139 | 17.76 | 100%
[5 empty] | 17.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1538.0543 | 24831.0048 | 17.77 | 100%
[5 empty] | 17.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1540.3207 | 24867.5958 | 17.78 | 100%
[5 empty] | 17.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1542.5872 | 24904.1867 | 17.79 | 100%
[5 empty] | 17.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1544.8537 | 24940.7777 | 17.8 | 100%
[5 empty] | 17.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1547.1202 | 24977.3686 | 17.81 | 100%
[5 empty] | 17.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1549.3866 | 25013.9595 | 17.82 | 100%
[5 empty] | 17.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1551.6531 | 25050.5505 | 17.83 | 100%
[5 empty] | 17.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1553.9196 | 25087.1414 | 17.84 | 100%
[5 empty] | 17.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1556.1861 | 25123.7324 | 17.85 | 100%
[5 empty] | 17.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1558.4525 | 25160.3233 | 17.86 | 100%
[5 empty] | 17.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1560.719 | 25196.9143 | 17.87 | 100%
[5 empty] | 17.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1562.9855 | 25233.5052 | 17.88 | 100%
[5 empty] | 17.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1565.252 | 25270.0962 | 17.89 | 100%
[5 empty] | 17.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1567.5184 | 25306.6871 | 17.9 | 100%
[5 empty] | 17.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1569.7849 | 25343.278 | 17.91 | 100%
[5 empty] | 17.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1572.0514 | 25379.869 | 17.92 | 100%
[5 empty] | 17.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1574.3179 | 25416.4599 | 17.93 | 100%
[5 empty] | 17.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1576.5843 | 25453.0509 | 17.94 | 100%
[5 empty] | 17.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1578.8508 | 25489.6418 | 17.95 | 100%
[5 empty] | 17.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1581.1173 | 25526.2328 | 17.96 | 100%
[5 empty] | 17.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1583.3838 | 25562.8237 | 17.97 | 100%
[5 empty] | 17.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1585.6502 | 25599.4146 | 17.98 | 100%
[5 empty] | 17.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1587.9167 | 25636.0056 | 17.99 | 100%
[5 empty] | 18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1590.1832 | 25672.5965 | 18 | 100%
[5 empty] | 18.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1592.4497 | 25709.1875 | 18.01 | 100%
[5 empty] | 18.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1594.7161 | 25745.7784 | 18.02 | 100%
[5 empty] | 18.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1596.9826 | 25782.3694 | 18.03 | 100%
[5 empty] | 18.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1599.2491 | 25818.9603 | 18.04 | 100%
[5 empty] | 18.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1601.5156 | 25855.5513 | 18.05 | 100%
[5 empty] | 18.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1603.782 | 25892.1422 | 18.06 | 100%
[5 empty] | 18.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1606.0485 | 25928.7331 | 18.07 | 100%
[5 empty] | 18.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1608.315 | 25965.3241 | 18.08 | 100%
[5 empty] | 18.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1610.5815 | 26001.915 | 18.09 | 100%
[5 empty] | 18.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1612.8479 | 26038.506 | 18.1 | 100%
[5 empty] | 18.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1615.1144 | 26075.0969 | 18.11 | 100%
[5 empty] | 18.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1617.3809 | 26111.6879 | 18.12 | 100%
[5 empty] | 18.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1619.6474 | 26148.2788 | 18.13 | 100%
[5 empty] | 18.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1621.9138 | 26184.8697 | 18.14 | 100%
[5 empty] | 18.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1624.1803 | 26221.4607 | 18.15 | 100%
[5 empty] | 18.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1626.4468 | 26258.0516 | 18.16 | 100%
[5 empty] | 18.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1628.7133 | 26294.6426 | 18.17 | 100%
[5 empty] | 18.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1630.9797 | 26331.2335 | 18.18 | 100%
[5 empty] | 18.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1633.2462 | 26367.8245 | 18.19 | 100%
[5 empty] | 18.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1635.5127 | 26404.4154 | 18.2 | 100%
[5 empty] | 18.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1637.7792 | 26441.0064 | 18.21 | 100%
[5 empty] | 18.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1640.0456 | 26477.5973 | 18.22 | 100%
[5 empty] | 18.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1642.3121 | 26514.1882 | 18.23 | 100%
[5 empty] | 18.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1644.5786 | 26550.7792 | 18.24 | 100%
[5 empty] | 18.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1646.8451 | 26587.3701 | 18.25 | 100%
[5 empty] | 18.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1649.1115 | 26623.9611 | 18.26 | 100%
[5 empty] | 18.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1651.378 | 26660.552 | 18.27 | 100%
[5 empty] | 18.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1653.6445 | 26697.143 | 18.28 | 100%
[5 empty] | 18.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1655.911 | 26733.7339 | 18.29 | 100%
[5 empty] | 18.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1658.1775 | 26770.3248 | 18.3 | 100%
[5 empty] | 18.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1660.4439 | 26806.9158 | 18.31 | 100%
[5 empty] | 18.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1662.7104 | 26843.5067 | 18.32 | 100%
[5 empty] | 18.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1664.9769 | 26880.0977 | 18.33 | 100%
[5 empty] | 18.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1667.2434 | 26916.6886 | 18.34 | 100%
[5 empty] | 18.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1669.5098 | 26953.2796 | 18.35 | 100%
[5 empty] | 18.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1671.7763 | 26989.8705 | 18.36 | 100%
[5 empty] | 18.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1674.0428 | 27026.4614 | 18.37 | 100%
[5 empty] | 18.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1676.3093 | 27063.0524 | 18.38 | 100%
[5 empty] | 18.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1678.5757 | 27099.6433 | 18.39 | 100%
[5 empty] | 18.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1680.8422 | 27136.2343 | 18.4 | 100%
[5 empty] | 18.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1683.1087 | 27172.8252 | 18.41 | 100%
[5 empty] | 18.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1685.3752 | 27209.4162 | 18.42 | 100%
[5 empty] | 18.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1687.6416 | 27246.0071 | 18.43 | 100%
[5 empty] | 18.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1689.9081 | 27282.5981 | 18.44 | 100%
[5 empty] | 18.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1692.1746 | 27319.189 | 18.45 | 100%
[5 empty] | 18.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1694.4411 | 27355.7799 | 18.46 | 100%
[5 empty] | 18.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1696.7075 | 27392.3709 | 18.47 | 100%
[5 empty] | 18.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1698.974 | 27428.9618 | 18.48 | 100%
[5 empty] | 18.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1701.2405 | 27465.5528 | 18.49 | 100%
[5 empty] | 18.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1703.507 | 27502.1437 | 18.5 | 100%
[5 empty] | 18.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1705.7734 | 27538.7347 | 18.51 | 100%
[5 empty] | 18.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1708.0399 | 27575.3256 | 18.52 | 100%
[5 empty] | 18.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1710.3064 | 27611.9165 | 18.53 | 100%
[5 empty] | 18.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1712.5729 | 27648.5075 | 18.54 | 100%
[5 empty] | 18.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1714.8393 | 27685.0984 | 18.55 | 100%
[5 empty] | 18.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1717.1058 | 27721.6894 | 18.56 | 100%
[5 empty] | 18.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1719.3723 | 27758.2803 | 18.57 | 100%
[5 empty] | 18.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1721.6388 | 27794.8713 | 18.58 | 100%
[5 empty] | 18.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1723.9052 | 27831.4622 | 18.59 | 100%
[5 empty] | 18.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1726.1717 | 27868.0532 | 18.6 | 100%
[5 empty] | 18.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1728.4382 | 27904.6441 | 18.61 | 100%
[5 empty] | 18.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1730.7047 | 27941.235 | 18.62 | 100%
[5 empty] | 18.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1732.9711 | 27977.826 | 18.63 | 100%
[5 empty] | 18.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1735.2376 | 28014.4169 | 18.64 | 100%
[5 empty] | 18.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1737.5041 | 28051.0079 | 18.65 | 100%
[5 empty] | 18.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1739.7706 | 28087.5988 | 18.66 | 100%
[5 empty] | 18.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1742.037 | 28124.1898 | 18.67 | 100%
[5 empty] | 18.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1744.3035 | 28160.7807 | 18.68 | 100%
[5 empty] | 18.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1746.57 | 28197.3716 | 18.69 | 100%
[5 empty] | 18.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1748.8365 | 28233.9626 | 18.7 | 100%
[5 empty] | 18.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1751.1029 | 28270.5535 | 18.71 | 100%
[5 empty] | 18.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1753.3694 | 28307.1445 | 18.72 | 100%
[5 empty] | 18.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1755.6359 | 28343.7354 | 18.73 | 100%
[5 empty] | 18.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1757.9024 | 28380.3264 | 18.74 | 100%
[5 empty] | 18.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1760.1688 | 28416.9173 | 18.75 | 100%
[5 empty] | 18.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1762.4353 | 28453.5083 | 18.76 | 100%
[5 empty] | 18.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1764.7018 | 28490.0992 | 18.77 | 100%
[5 empty] | 18.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1766.9683 | 28526.6901 | 18.78 | 100%
[5 empty] | 18.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1769.2347 | 28563.2811 | 18.79 | 100%
[5 empty] | 18.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1771.5012 | 28599.872 | 18.8 | 100%
[5 empty] | 18.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1773.7677 | 28636.463 | 18.81 | 100%
[5 empty] | 18.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1776.0342 | 28673.0539 | 18.82 | 100%
[5 empty] | 18.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1778.3006 | 28709.6449 | 18.83 | 100%
[5 empty] | 18.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1780.5671 | 28746.2358 | 18.84 | 100%
[5 empty] | 18.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1782.8336 | 28782.8267 | 18.85 | 100%
[5 empty] | 18.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1785.1001 | 28819.4177 | 18.86 | 100%
[5 empty] | 18.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1787.3665 | 28856.0086 | 18.87 | 100%
[5 empty] | 18.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1789.633 | 28892.5996 | 18.88 | 100%
[5 empty] | 18.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1791.8995 | 28929.1905 | 18.89 | 100%
[5 empty] | 18.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1794.166 | 28965.7815 | 18.9 | 100%
[5 empty] | 18.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1796.4324 | 29002.3724 | 18.91 | 100%
[5 empty] | 18.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1798.6989 | 29038.9633 | 18.92 | 100%
[5 empty] | 18.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1800.9654 | 29075.5543 | 18.93 | 100%
[5 empty] | 18.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1803.2319 | 29112.1452 | 18.94 | 100%
[5 empty] | 18.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1805.4983 | 29148.7362 | 18.95 | 100%
[5 empty] | 18.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1807.7648 | 29185.3271 | 18.96 | 100%
[5 empty] | 18.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1810.0313 | 29221.9181 | 18.97 | 100%
[5 empty] | 18.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1812.2978 | 29258.509 | 18.98 | 100%
[5 empty] | 18.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1814.5642 | 29295.1 | 18.99 | 100%
[5 empty] | 19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1816.8307 | 29331.6909 | 19 | 100%
[5 empty] | 19.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1819.0972 | 29368.2818 | 19.01 | 100%
[5 empty] | 19.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1821.3637 | 29404.8728 | 19.02 | 100%
[5 empty] | 19.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1823.6301 | 29441.4637 | 19.03 | 100%
[5 empty] | 19.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1825.8966 | 29478.0547 | 19.04 | 100%
[5 empty] | 19.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1828.1631 | 29514.6456 | 19.05 | 100%
[5 empty] | 19.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1830.4296 | 29551.2366 | 19.06 | 100%
[5 empty] | 19.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1832.696 | 29587.8275 | 19.07 | 100%
[5 empty] | 19.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1834.9625 | 29624.4184 | 19.08 | 100%
[5 empty] | 19.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1837.229 | 29661.0094 | 19.09 | 100%
[5 empty] | 19.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1839.4955 | 29697.6003 | 19.1 | 100%
[5 empty] | 19.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1841.7619 | 29734.1913 | 19.11 | 100%
[5 empty] | 19.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1844.0284 | 29770.7822 | 19.12 | 100%
[5 empty] | 19.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1846.2949 | 29807.3732 | 19.13 | 100%
[5 empty] | 19.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1848.5614 | 29843.9641 | 19.14 | 100%
[5 empty] | 19.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1850.8278 | 29880.5551 | 19.15 | 100%
[5 empty] | 19.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1853.0943 | 29917.146 | 19.16 | 100%
[5 empty] | 19.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1855.3608 | 29953.7369 | 19.17 | 100%
[5 empty] | 19.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1857.6273 | 29990.3279 | 19.18 | 100%
[5 empty] | 19.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1859.8937 | 30026.9188 | 19.19 | 100%
[5 empty] | 19.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1862.1602 | 30063.5098 | 19.2 | 100%
[5 empty] | 19.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1864.4267 | 30100.1007 | 19.21 | 100%
[5 empty] | 19.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1866.6932 | 30136.6917 | 19.22 | 100%
[5 empty] | 19.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1868.9596 | 30173.2826 | 19.23 | 100%
[5 empty] | 19.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1871.2261 | 30209.8735 | 19.24 | 100%
[5 empty] | 19.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1873.4926 | 30246.4645 | 19.25 | 100%
[5 empty] | 19.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1875.7591 | 30283.0554 | 19.26 | 100%
[5 empty] | 19.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1878.0255 | 30319.6464 | 19.27 | 100%
[5 empty] | 19.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1880.292 | 30356.2373 | 19.28 | 100%
[5 empty] | 19.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1882.5585 | 30392.8283 | 19.29 | 100%
[5 empty] | 19.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1884.825 | 30429.4192 | 19.3 | 100%
[5 empty] | 19.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1887.0914 | 30466.0102 | 19.31 | 100%
[5 empty] | 19.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1889.3579 | 30502.6011 | 19.32 | 100%
[5 empty] | 19.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1891.6244 | 30539.192 | 19.33 | 100%
[5 empty] | 19.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1893.8909 | 30575.783 | 19.34 | 100%
[5 empty] | 19.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1896.1573 | 30612.3739 | 19.35 | 100%
[5 empty] | 19.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1898.4238 | 30648.9649 | 19.36 | 100%
[5 empty] | 19.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1900.6903 | 30685.5558 | 19.37 | 100%
[5 empty] | 19.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1902.9568 | 30722.1468 | 19.38 | 100%
[5 empty] | 19.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1905.2232 | 30758.7377 | 19.39 | 100%
[5 empty] | 19.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1907.4897 | 30795.3286 | 19.4 | 100%
[5 empty] | 19.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1909.7562 | 30831.9196 | 19.41 | 100%
[5 empty] | 19.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1912.0227 | 30868.5105 | 19.42 | 100%
[5 empty] | 19.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1914.2891 | 30905.1015 | 19.43 | 100%
[5 empty] | 19.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1916.5556 | 30941.6924 | 19.44 | 100%
[5 empty] | 19.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1918.8221 | 30978.2834 | 19.45 | 100%
[5 empty] | 19.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1921.0886 | 31014.8743 | 19.46 | 100%
[5 empty] | 19.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1923.3551 | 31051.4652 | 19.47 | 100%
[5 empty] | 19.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1925.6215 | 31088.0562 | 19.48 | 100%
[5 empty] | 19.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1927.888 | 31124.6471 | 19.49 | 100%
[5 empty] | 19.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1930.1545 | 31161.2381 | 19.5 | 100%
[5 empty] | 19.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1932.421 | 31197.829 | 19.51 | 100%
[5 empty] | 19.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1934.6874 | 31234.42 | 19.52 | 100%
[5 empty] | 19.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1936.9539 | 31271.0109 | 19.53 | 100%
[5 empty] | 19.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1939.2204 | 31307.6019 | 19.54 | 100%
[5 empty] | 19.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1941.4869 | 31344.1928 | 19.55 | 100%
[5 empty] | 19.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1943.7533 | 31380.7837 | 19.56 | 100%
[5 empty] | 19.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1946.0198 | 31417.3747 | 19.57 | 100%
[5 empty] | 19.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1948.2863 | 31453.9656 | 19.58 | 100%
[5 empty] | 19.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1950.5528 | 31490.5566 | 19.59 | 100%
[5 empty] | 19.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1952.8192 | 31527.1475 | 19.6 | 100%
[5 empty] | 19.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1955.0857 | 31563.7385 | 19.61 | 100%
[5 empty] | 19.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1957.3522 | 31600.3294 | 19.62 | 100%
[5 empty] | 19.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1959.6187 | 31636.9203 | 19.63 | 100%
[5 empty] | 19.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1961.8851 | 31673.5113 | 19.64 | 100%
[5 empty] | 19.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1964.1516 | 31710.1022 | 19.65 | 100%
[5 empty] | 19.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1966.4181 | 31746.6932 | 19.66 | 100%
[5 empty] | 19.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1968.6846 | 31783.2841 | 19.67 | 100%
[5 empty] | 19.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1970.951 | 31819.8751 | 19.68 | 100%
[5 empty] | 19.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1973.2175 | 31856.466 | 19.69 | 100%
[5 empty] | 19.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1975.484 | 31893.057 | 19.7 | 100%
[5 empty] | 19.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1977.7505 | 31929.6479 | 19.71 | 100%
[5 empty] | 19.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1980.0169 | 31966.2388 | 19.72 | 100%
[5 empty] | 19.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1982.2834 | 32002.8298 | 19.73 | 100%
[5 empty] | 19.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1984.5499 | 32039.4207 | 19.74 | 100%
[5 empty] | 19.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1986.8164 | 32076.0117 | 19.75 | 100%
[5 empty] | 19.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1989.0828 | 32112.6026 | 19.76 | 100%
[5 empty] | 19.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1991.3493 | 32149.1936 | 19.77 | 100%
[5 empty] | 19.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1993.6158 | 32185.7845 | 19.78 | 100%
[5 empty] | 19.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1995.8823 | 32222.3754 | 19.79 | 100%
[5 empty] | 19.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 1998.1487 | 32258.9664 | 19.8 | 100%
[5 empty] | 19.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2000.4152 | 32295.5573 | 19.81 | 100%
[5 empty] | 19.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2002.6817 | 32332.1483 | 19.82 | 100%
[5 empty] | 19.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2004.9482 | 32368.7392 | 19.83 | 100%
[5 empty] | 19.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2007.2146 | 32405.3302 | 19.84 | 100%
[5 empty] | 19.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2009.4811 | 32441.9211 | 19.85 | 100%
[5 empty] | 19.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2011.7476 | 32478.512 | 19.86 | 100%
[5 empty] | 19.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2014.0141 | 32515.103 | 19.87 | 100%
[5 empty] | 19.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2016.2805 | 32551.6939 | 19.88 | 100%
[5 empty] | 19.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2018.547 | 32588.2849 | 19.89 | 100%
[5 empty] | 19.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2020.8135 | 32624.8758 | 19.9 | 100%
[5 empty] | 19.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2023.08 | 32661.4668 | 19.91 | 100%
[5 empty] | 19.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2025.3464 | 32698.0577 | 19.92 | 100%
[5 empty] | 19.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2027.6129 | 32734.6487 | 19.93 | 100%
[5 empty] | 19.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2029.8794 | 32771.2396 | 19.94 | 100%
[5 empty] | 19.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2032.1459 | 32807.8305 | 19.95 | 100%
[5 empty] | 19.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2034.4123 | 32844.4215 | 19.96 | 100%
[5 empty] | 19.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2036.6788 | 32881.0124 | 19.97 | 100%
[5 empty] | 19.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2038.9453 | 32917.6034 | 19.98 | 100%
[5 empty] | 19.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2041.2118 | 32954.1943 | 19.99 | 100%
[5 empty] | 20 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2043.4782 | 32990.7853 | 20 | 100%
[5 empty] | 20.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2045.7447 | 33027.3762 | 20.01 | 100%
[5 empty] | 20.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2048.0112 | 33063.9671 | 20.02 | 100%
[5 empty] | 20.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2050.2777 | 33100.5581 | 20.03 | 100%
[5 empty] | 20.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2052.5441 | 33137.149 | 20.04 | 100%
[5 empty] | 20.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2054.8106 | 33173.74 | 20.05 | 100%
[5 empty] | 20.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2057.0771 | 33210.3309 | 20.06 | 100%
[5 empty] | 20.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2059.3436 | 33246.9219 | 20.07 | 100%
[5 empty] | 20.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2061.61 | 33283.5128 | 20.08 | 100%
[5 empty] | 20.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2063.8765 | 33320.1038 | 20.09 | 100%
[5 empty] | 20.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2066.143 | 33356.6947 | 20.1 | 100%
[5 empty] | 20.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2068.4095 | 33393.2856 | 20.11 | 100%
[5 empty] | 20.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2070.6759 | 33429.8766 | 20.12 | 100%
[5 empty] | 20.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2072.9424 | 33466.4675 | 20.13 | 100%
[5 empty] | 20.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2075.2089 | 33503.0585 | 20.14 | 100%
[5 empty] | 20.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2077.4754 | 33539.6494 | 20.15 | 100%
[5 empty] | 20.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2079.7418 | 33576.2404 | 20.16 | 100%
[5 empty] | 20.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2082.0083 | 33612.8313 | 20.17 | 100%
[5 empty] | 20.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2084.2748 | 33649.4222 | 20.18 | 100%
[5 empty] | 20.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2086.5413 | 33686.0132 | 20.19 | 100%
[5 empty] | 20.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2088.8077 | 33722.6041 | 20.2 | 100%
[5 empty] | 20.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2091.0742 | 33759.1951 | 20.21 | 100%
[5 empty] | 20.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2093.3407 | 33795.786 | 20.22 | 100%
[5 empty] | 20.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2095.6072 | 33832.377 | 20.23 | 100%
[5 empty] | 20.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2097.8736 | 33868.9679 | 20.24 | 100%
[5 empty] | 20.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2100.1401 | 33905.5589 | 20.25 | 100%
[5 empty] | 20.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2102.4066 | 33942.1498 | 20.26 | 100%
[5 empty] | 20.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2104.6731 | 33978.7407 | 20.27 | 100%
[5 empty] | 20.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2106.9395 | 34015.3317 | 20.28 | 100%
[5 empty] | 20.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2109.206 | 34051.9226 | 20.29 | 100%
[5 empty] | 20.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2111.4725 | 34088.5136 | 20.3 | 100%
[5 empty] | 20.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2113.739 | 34125.1045 | 20.31 | 100%
[5 empty] | 20.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2116.0054 | 34161.6955 | 20.32 | 100%
[5 empty] | 20.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2118.2719 | 34198.2864 | 20.33 | 100%
[5 empty] | 20.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2120.5384 | 34234.8773 | 20.34 | 100%
[5 empty] | 20.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2122.8049 | 34271.4683 | 20.35 | 100%
[5 empty] | 20.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2125.0713 | 34308.0592 | 20.36 | 100%
[5 empty] | 20.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2127.3378 | 34344.6502 | 20.37 | 100%
[5 empty] | 20.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2129.6043 | 34381.2411 | 20.38 | 100%
[5 empty] | 20.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2131.8708 | 34417.8321 | 20.39 | 100%
[5 empty] | 20.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2134.1372 | 34454.423 | 20.4 | 100%
[5 empty] | 20.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2136.4037 | 34491.0139 | 20.41 | 100%
[5 empty] | 20.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2138.6702 | 34527.6049 | 20.42 | 100%
[5 empty] | 20.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2140.9367 | 34564.1958 | 20.43 | 100%
[5 empty] | 20.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2143.2031 | 34600.7868 | 20.44 | 100%
[5 empty] | 20.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2145.4696 | 34637.3777 | 20.45 | 100%
[5 empty] | 20.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2147.7361 | 34673.9687 | 20.46 | 100%
[5 empty] | 20.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2150.0026 | 34710.5596 | 20.47 | 100%
[5 empty] | 20.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2152.269 | 34747.1506 | 20.48 | 100%
[5 empty] | 20.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2154.5355 | 34783.7415 | 20.49 | 100%
[5 empty] | 20.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2156.802 | 34820.3324 | 20.5 | 100%
[5 empty] | 20.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2159.0685 | 34856.9234 | 20.51 | 100%
[5 empty] | 20.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2161.3349 | 34893.5143 | 20.52 | 100%
[5 empty] | 20.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2163.6014 | 34930.1053 | 20.53 | 100%
[5 empty] | 20.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2165.8679 | 34966.6962 | 20.54 | 100%
[5 empty] | 20.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2168.1344 | 35003.2872 | 20.55 | 100%
[5 empty] | 20.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2170.4008 | 35039.8781 | 20.56 | 100%
[5 empty] | 20.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2172.6673 | 35076.469 | 20.57 | 100%
[5 empty] | 20.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2174.9338 | 35113.06 | 20.58 | 100%
[5 empty] | 20.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2177.2003 | 35149.6509 | 20.59 | 100%
[5 empty] | 20.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2179.4667 | 35186.2419 | 20.6 | 100%
[5 empty] | 20.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2181.7332 | 35222.8328 | 20.61 | 100%
[5 empty] | 20.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2183.9997 | 35259.4238 | 20.62 | 100%
[5 empty] | 20.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2186.2662 | 35296.0147 | 20.63 | 100%
[5 empty] | 20.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2188.5326 | 35332.6057 | 20.64 | 100%
[5 empty] | 20.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2190.7991 | 35369.1966 | 20.65 | 100%
[5 empty] | 20.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2193.0656 | 35405.7875 | 20.66 | 100%
[5 empty] | 20.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2195.3321 | 35442.3785 | 20.67 | 100%
[5 empty] | 20.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2197.5986 | 35478.9694 | 20.68 | 100%
[5 empty] | 20.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2199.865 | 35515.5604 | 20.69 | 100%
[5 empty] | 20.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2202.1315 | 35552.1513 | 20.7 | 100%
[5 empty] | 20.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2204.398 | 35588.7423 | 20.71 | 100%
[5 empty] | 20.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2206.6645 | 35625.3332 | 20.72 | 100%
[5 empty] | 20.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2208.9309 | 35661.9241 | 20.73 | 100%
[5 empty] | 20.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2211.1974 | 35698.5151 | 20.74 | 100%
[5 empty] | 20.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2213.4639 | 35735.106 | 20.75 | 100%
[5 empty] | 20.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2215.7304 | 35771.697 | 20.76 | 100%
[5 empty] | 20.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2217.9968 | 35808.2879 | 20.77 | 100%
[5 empty] | 20.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2220.2633 | 35844.8789 | 20.78 | 100%
[5 empty] | 20.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2222.5298 | 35881.4698 | 20.79 | 100%
[5 empty] | 20.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2224.7963 | 35918.0608 | 20.8 | 100%
[5 empty] | 20.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2227.0627 | 35954.6517 | 20.81 | 100%
[5 empty] | 20.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2229.3292 | 35991.2426 | 20.82 | 100%
[5 empty] | 20.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2231.5957 | 36027.8336 | 20.83 | 100%
[5 empty] | 20.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2233.8622 | 36064.4245 | 20.84 | 100%
[5 empty] | 20.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2236.1286 | 36101.0155 | 20.85 | 100%
[5 empty] | 20.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2238.3951 | 36137.6064 | 20.86 | 100%
[5 empty] | 20.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2240.6616 | 36174.1974 | 20.87 | 100%
[5 empty] | 20.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2242.9281 | 36210.7883 | 20.88 | 100%
[5 empty] | 20.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2245.1945 | 36247.3792 | 20.89 | 100%
[5 empty] | 20.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2247.461 | 36283.9702 | 20.9 | 100%
[5 empty] | 20.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2249.7275 | 36320.5611 | 20.91 | 100%
[5 empty] | 20.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2251.994 | 36357.1521 | 20.92 | 100%
[5 empty] | 20.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2254.2604 | 36393.743 | 20.93 | 100%
[5 empty] | 20.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2256.5269 | 36430.334 | 20.94 | 100%
[5 empty] | 20.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2258.7934 | 36466.9249 | 20.95 | 100%
[5 empty] | 20.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2261.0599 | 36503.5158 | 20.96 | 100%
[5 empty] | 20.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2263.3263 | 36540.1068 | 20.97 | 100%
[5 empty] | 20.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2265.5928 | 36576.6977 | 20.98 | 100%
[5 empty] | 20.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2267.8593 | 36613.2887 | 20.99 | 100%
[5 empty] | 21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2270.1258 | 36649.8796 | 21 | 100%
[5 empty] | 21.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2272.3922 | 36686.4706 | 21.01 | 100%
[5 empty] | 21.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2274.6587 | 36723.0615 | 21.02 | 100%
[5 empty] | 21.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2276.9252 | 36759.6525 | 21.03 | 100%
[5 empty] | 21.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2279.1917 | 36796.2434 | 21.04 | 100%
[5 empty] | 21.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2281.4581 | 36832.8343 | 21.05 | 100%
[5 empty] | 21.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2283.7246 | 36869.4253 | 21.06 | 100%
[5 empty] | 21.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2285.9911 | 36906.0162 | 21.07 | 100%
[5 empty] | 21.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2288.2576 | 36942.6072 | 21.08 | 100%
[5 empty] | 21.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2290.524 | 36979.1981 | 21.09 | 100%
[5 empty] | 21.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2292.7905 | 37015.7891 | 21.1 | 100%
[5 empty] | 21.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2295.057 | 37052.38 | 21.11 | 100%
[5 empty] | 21.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2297.3235 | 37088.9709 | 21.12 | 100%
[5 empty] | 21.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2299.5899 | 37125.5619 | 21.13 | 100%
[5 empty] | 21.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2301.8564 | 37162.1528 | 21.14 | 100%
[5 empty] | 21.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2304.1229 | 37198.7438 | 21.15 | 100%
[5 empty] | 21.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2306.3894 | 37235.3347 | 21.16 | 100%
[5 empty] | 21.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2308.6558 | 37271.9257 | 21.17 | 100%
[5 empty] | 21.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2310.9223 | 37308.5166 | 21.18 | 100%
[5 empty] | 21.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2313.1888 | 37345.1076 | 21.19 | 100%
[5 empty] | 21.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2315.4553 | 37381.6985 | 21.2 | 100%
[5 empty] | 21.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2317.7217 | 37418.2894 | 21.21 | 100%
[5 empty] | 21.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2319.9882 | 37454.8804 | 21.22 | 100%
[5 empty] | 21.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2322.2547 | 37491.4713 | 21.23 | 100%
[5 empty] | 21.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2324.5212 | 37528.0623 | 21.24 | 100%
[5 empty] | 21.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2326.7876 | 37564.6532 | 21.25 | 100%
[5 empty] | 21.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2329.0541 | 37601.2442 | 21.26 | 100%
[5 empty] | 21.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2331.3206 | 37637.8351 | 21.27 | 100%
[5 empty] | 21.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2333.5871 | 37674.426 | 21.28 | 100%
[5 empty] | 21.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2335.8535 | 37711.017 | 21.29 | 100%
[5 empty] | 21.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2338.12 | 37747.6079 | 21.3 | 100%
[5 empty] | 21.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2340.3865 | 37784.1989 | 21.31 | 100%
[5 empty] | 21.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2342.653 | 37820.7898 | 21.32 | 100%
[5 empty] | 21.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2344.9194 | 37857.3808 | 21.33 | 100%
[5 empty] | 21.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2347.1859 | 37893.9717 | 21.34 | 100%
[5 empty] | 21.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2349.4524 | 37930.5626 | 21.35 | 100%
[5 empty] | 21.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2351.7189 | 37967.1536 | 21.36 | 100%
[5 empty] | 21.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2353.9853 | 38003.7445 | 21.37 | 100%
[5 empty] | 21.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2356.2518 | 38040.3355 | 21.38 | 100%
[5 empty] | 21.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2358.5183 | 38076.9264 | 21.39 | 100%
[5 empty] | 21.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2360.7848 | 38113.5174 | 21.4 | 100%
[5 empty] | 21.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2363.0512 | 38150.1083 | 21.41 | 100%
[5 empty] | 21.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2365.3177 | 38186.6993 | 21.42 | 100%
[5 empty] | 21.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2367.5842 | 38223.2902 | 21.43 | 100%
[5 empty] | 21.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2369.8507 | 38259.8811 | 21.44 | 100%
[5 empty] | 21.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2372.1171 | 38296.4721 | 21.45 | 100%
[5 empty] | 21.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2374.3836 | 38333.063 | 21.46 | 100%
[5 empty] | 21.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2376.6501 | 38369.654 | 21.47 | 100%
[5 empty] | 21.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2378.9166 | 38406.2449 | 21.48 | 100%
[5 empty] | 21.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2381.183 | 38442.8359 | 21.49 | 100%
[5 empty] | 21.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2383.4495 | 38479.4268 | 21.5 | 100%
[5 empty] | 21.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2385.716 | 38516.0177 | 21.51 | 100%
[5 empty] | 21.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2387.9825 | 38552.6087 | 21.52 | 100%
[5 empty] | 21.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2390.2489 | 38589.1996 | 21.53 | 100%
[5 empty] | 21.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2392.5154 | 38625.7906 | 21.54 | 100%
[5 empty] | 21.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2394.7819 | 38662.3815 | 21.55 | 100%
[5 empty] | 21.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2397.0484 | 38698.9725 | 21.56 | 100%
[5 empty] | 21.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2399.3148 | 38735.5634 | 21.57 | 100%
[5 empty] | 21.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2401.5813 | 38772.1544 | 21.58 | 100%
[5 empty] | 21.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2403.8478 | 38808.7453 | 21.59 | 100%
[5 empty] | 21.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2406.1143 | 38845.3362 | 21.6 | 100%
[5 empty] | 21.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2408.3807 | 38881.9272 | 21.61 | 100%
[5 empty] | 21.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2410.6472 | 38918.5181 | 21.62 | 100%
[5 empty] | 21.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2412.9137 | 38955.1091 | 21.63 | 100%
[5 empty] | 21.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2415.1802 | 38991.7 | 21.64 | 100%
[5 empty] | 21.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2417.4466 | 39028.291 | 21.65 | 100%
[5 empty] | 21.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2419.7131 | 39064.8819 | 21.66 | 100%
[5 empty] | 21.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2421.9796 | 39101.4728 | 21.67 | 100%
[5 empty] | 21.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2424.2461 | 39138.0638 | 21.68 | 100%
[5 empty] | 21.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2426.5125 | 39174.6547 | 21.69 | 100%
[5 empty] | 21.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2428.779 | 39211.2457 | 21.7 | 100%
[5 empty] | 21.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2431.0455 | 39247.8366 | 21.71 | 100%
[5 empty] | 21.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2433.312 | 39284.4276 | 21.72 | 100%
[5 empty] | 21.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2435.5784 | 39321.0185 | 21.73 | 100%
[5 empty] | 21.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2437.8449 | 39357.6095 | 21.74 | 100%
[5 empty] | 21.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2440.1114 | 39394.2004 | 21.75 | 100%
[5 empty] | 21.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2442.3779 | 39430.7913 | 21.76 | 100%
[5 empty] | 21.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2444.6443 | 39467.3823 | 21.77 | 100%
[5 empty] | 21.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2446.9108 | 39503.9732 | 21.78 | 100%
[5 empty] | 21.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2449.1773 | 39540.5642 | 21.79 | 100%
[5 empty] | 21.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2451.4438 | 39577.1551 | 21.8 | 100%
[5 empty] | 21.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2453.7102 | 39613.7461 | 21.81 | 100%
[5 empty] | 21.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2455.9767 | 39650.337 | 21.82 | 100%
[5 empty] | 21.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2458.2432 | 39686.9279 | 21.83 | 100%
[5 empty] | 21.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2460.5097 | 39723.5189 | 21.84 | 100%
[5 empty] | 21.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2462.7761 | 39760.1098 | 21.85 | 100%
[5 empty] | 21.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2465.0426 | 39796.7008 | 21.86 | 100%
[5 empty] | 21.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2467.3091 | 39833.2917 | 21.87 | 100%
[5 empty] | 21.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2469.5756 | 39869.8827 | 21.88 | 100%
[5 empty] | 21.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2471.8421 | 39906.4736 | 21.89 | 100%
[5 empty] | 21.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2474.1085 | 39943.0645 | 21.9 | 100%
[5 empty] | 21.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2476.375 | 39979.6555 | 21.91 | 100%
[5 empty] | 21.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2478.6415 | 40016.2464 | 21.92 | 100%
[5 empty] | 21.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2480.908 | 40052.8374 | 21.93 | 100%
[5 empty] | 21.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2483.1744 | 40089.4283 | 21.94 | 100%
[5 empty] | 21.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2485.4409 | 40126.0193 | 21.95 | 100%
[5 empty] | 21.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2487.7074 | 40162.6102 | 21.96 | 100%
[5 empty] | 21.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2489.9739 | 40199.2012 | 21.97 | 100%
[5 empty] | 21.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2492.2403 | 40235.7921 | 21.98 | 100%
[5 empty] | 21.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2494.5068 | 40272.383 | 21.99 | 100%
[5 empty] | 22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2496.7733 | 40308.974 | 22 | 100%
[5 empty] | 22.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2499.0398 | 40345.5649 | 22.01 | 100%
[5 empty] | 22.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2501.3062 | 40382.1559 | 22.02 | 100%
[5 empty] | 22.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2503.5727 | 40418.7468 | 22.03 | 100%
[5 empty] | 22.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2505.8392 | 40455.3378 | 22.04 | 100%
[5 empty] | 22.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2508.1057 | 40491.9287 | 22.05 | 100%
[5 empty] | 22.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2510.3721 | 40528.5196 | 22.06 | 100%
[5 empty] | 22.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2512.6386 | 40565.1106 | 22.07 | 100%
[5 empty] | 22.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2514.9051 | 40601.7015 | 22.08 | 100%
[5 empty] | 22.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2517.1716 | 40638.2925 | 22.09 | 100%
[5 empty] | 22.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2519.438 | 40674.8834 | 22.1 | 100%
[5 empty] | 22.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2521.7045 | 40711.4744 | 22.11 | 100%
[5 empty] | 22.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2523.971 | 40748.0653 | 22.12 | 100%
[5 empty] | 22.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2526.2375 | 40784.6563 | 22.13 | 100%
[5 empty] | 22.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2528.5039 | 40821.2472 | 22.14 | 100%
[5 empty] | 22.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2530.7704 | 40857.8381 | 22.15 | 100%
[5 empty] | 22.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2533.0369 | 40894.4291 | 22.16 | 100%
[5 empty] | 22.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2535.3034 | 40931.02 | 22.17 | 100%
[5 empty] | 22.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2537.5698 | 40967.611 | 22.18 | 100%
[5 empty] | 22.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2539.8363 | 41004.2019 | 22.19 | 100%
[5 empty] | 22.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2542.1028 | 41040.7929 | 22.2 | 100%
[5 empty] | 22.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2544.3693 | 41077.3838 | 22.21 | 100%
[5 empty] | 22.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2546.6357 | 41113.9747 | 22.22 | 100%
[5 empty] | 22.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2548.9022 | 41150.5657 | 22.23 | 100%
[5 empty] | 22.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2551.1687 | 41187.1566 | 22.24 | 100%
[5 empty] | 22.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2553.4352 | 41223.7476 | 22.25 | 100%
[5 empty] | 22.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2555.7016 | 41260.3385 | 22.26 | 100%
[5 empty] | 22.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2557.9681 | 41296.9295 | 22.27 | 100%
[5 empty] | 22.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2560.2346 | 41333.5204 | 22.28 | 100%
[5 empty] | 22.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2562.5011 | 41370.1114 | 22.29 | 100%
[5 empty] | 22.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2564.7675 | 41406.7023 | 22.3 | 100%
[5 empty] | 22.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2567.034 | 41443.2932 | 22.31 | 100%
[5 empty] | 22.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2569.3005 | 41479.8842 | 22.32 | 100%
[5 empty] | 22.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2571.567 | 41516.4751 | 22.33 | 100%
[5 empty] | 22.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2573.8334 | 41553.0661 | 22.34 | 100%
[5 empty] | 22.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2576.0999 | 41589.657 | 22.35 | 100%
[5 empty] | 22.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2578.3664 | 41626.248 | 22.36 | 100%
[5 empty] | 22.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2580.6329 | 41662.8389 | 22.37 | 100%
[5 empty] | 22.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2582.8993 | 41699.4298 | 22.38 | 100%
[5 empty] | 22.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2585.1658 | 41736.0208 | 22.39 | 100%
[5 empty] | 22.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2587.4323 | 41772.6117 | 22.4 | 100%
[5 empty] | 22.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2589.6988 | 41809.2027 | 22.41 | 100%
[5 empty] | 22.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2591.9652 | 41845.7936 | 22.42 | 100%
[5 empty] | 22.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2594.2317 | 41882.3846 | 22.43 | 100%
[5 empty] | 22.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2596.4982 | 41918.9755 | 22.44 | 100%
[5 empty] | 22.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2598.7647 | 41955.5664 | 22.45 | 100%
[5 empty] | 22.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2601.0311 | 41992.1574 | 22.46 | 100%
[5 empty] | 22.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2603.2976 | 42028.7483 | 22.47 | 100%
[5 empty] | 22.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2605.5641 | 42065.3393 | 22.48 | 100%
[5 empty] | 22.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2607.8306 | 42101.9302 | 22.49 | 100%
[5 empty] | 22.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2610.097 | 42138.5212 | 22.5 | 100%
[5 empty] | 22.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2612.3635 | 42175.1121 | 22.51 | 100%
[5 empty] | 22.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2614.63 | 42211.7031 | 22.52 | 100%
[5 empty] | 22.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2616.8965 | 42248.294 | 22.53 | 100%
[5 empty] | 22.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2619.1629 | 42284.8849 | 22.54 | 100%
[5 empty] | 22.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2621.4294 | 42321.4759 | 22.55 | 100%
[5 empty] | 22.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2623.6959 | 42358.0668 | 22.56 | 100%
[5 empty] | 22.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2625.9624 | 42394.6578 | 22.57 | 100%
[5 empty] | 22.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2628.2288 | 42431.2487 | 22.58 | 100%
[5 empty] | 22.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2630.4953 | 42467.8397 | 22.59 | 100%
[5 empty] | 22.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2632.7618 | 42504.4306 | 22.6 | 100%
[5 empty] | 22.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2635.0283 | 42541.0215 | 22.61 | 100%
[5 empty] | 22.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2637.2947 | 42577.6125 | 22.62 | 100%
[5 empty] | 22.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2639.5612 | 42614.2034 | 22.63 | 100%
[5 empty] | 22.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2641.8277 | 42650.7944 | 22.64 | 100%
[5 empty] | 22.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2644.0942 | 42687.3853 | 22.65 | 100%
[5 empty] | 22.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2646.3606 | 42723.9763 | 22.66 | 100%
[5 empty] | 22.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2648.6271 | 42760.5672 | 22.67 | 100%
[5 empty] | 22.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2650.8936 | 42797.1582 | 22.68 | 100%
[5 empty] | 22.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2653.1601 | 42833.7491 | 22.69 | 100%
[5 empty] | 22.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2655.4265 | 42870.34 | 22.7 | 100%
[5 empty] | 22.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2657.693 | 42906.931 | 22.71 | 100%
[5 empty] | 22.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2659.9595 | 42943.5219 | 22.72 | 100%
[5 empty] | 22.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2662.226 | 42980.1129 | 22.73 | 100%
[5 empty] | 22.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2664.4924 | 43016.7038 | 22.74 | 100%
[5 empty] | 22.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2666.7589 | 43053.2948 | 22.75 | 100%
[5 empty] | 22.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2669.0254 | 43089.8857 | 22.76 | 100%
[5 empty] | 22.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2671.2919 | 43126.4766 | 22.77 | 100%
[5 empty] | 22.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2673.5583 | 43163.0676 | 22.78 | 100%
[5 empty] | 22.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2675.8248 | 43199.6585 | 22.79 | 100%
[5 empty] | 22.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2678.0913 | 43236.2495 | 22.8 | 100%
[5 empty] | 22.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2680.3578 | 43272.8404 | 22.81 | 100%
[5 empty] | 22.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2682.6242 | 43309.4314 | 22.82 | 100%
[5 empty] | 22.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2684.8907 | 43346.0223 | 22.83 | 100%
[5 empty] | 22.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2687.1572 | 43382.6133 | 22.84 | 100%
[5 empty] | 22.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2689.4237 | 43419.2042 | 22.85 | 100%
[5 empty] | 22.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2691.6901 | 43455.7951 | 22.86 | 100%
[5 empty] | 22.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2693.9566 | 43492.3861 | 22.87 | 100%
[5 empty] | 22.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2696.2231 | 43528.977 | 22.88 | 100%
[5 empty] | 22.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2698.4896 | 43565.568 | 22.89 | 100%
[5 empty] | 22.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2700.756 | 43602.1589 | 22.9 | 100%
[5 empty] | 22.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2703.0225 | 43638.7499 | 22.91 | 100%
[5 empty] | 22.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2705.289 | 43675.3408 | 22.92 | 100%
[5 empty] | 22.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2707.5555 | 43711.9317 | 22.93 | 100%
[5 empty] | 22.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2709.8219 | 43748.5227 | 22.94 | 100%
[5 empty] | 22.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2712.0884 | 43785.1136 | 22.95 | 100%
[5 empty] | 22.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2714.3549 | 43821.7046 | 22.96 | 100%
[5 empty] | 22.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2716.6214 | 43858.2955 | 22.97 | 100%
[5 empty] | 22.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2718.8878 | 43894.8865 | 22.98 | 100%
[5 empty] | 22.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2721.1543 | 43931.4774 | 22.99 | 100%
[5 empty] | 23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2723.4208 | 43968.0683 | 23 | 100%
[5 empty] | 23.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2725.6873 | 44004.6593 | 23.01 | 100%
[5 empty] | 23.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2727.9537 | 44041.2502 | 23.02 | 100%
[5 empty] | 23.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2730.2202 | 44077.8412 | 23.03 | 100%
[5 empty] | 23.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2732.4867 | 44114.4321 | 23.04 | 100%
[5 empty] | 23.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2734.7532 | 44151.0231 | 23.05 | 100%
[5 empty] | 23.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2737.0197 | 44187.614 | 23.06 | 100%
[5 empty] | 23.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2739.2861 | 44224.205 | 23.07 | 100%
[5 empty] | 23.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2741.5526 | 44260.7959 | 23.08 | 100%
[5 empty] | 23.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2743.8191 | 44297.3868 | 23.09 | 100%
[5 empty] | 23.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2746.0856 | 44333.9778 | 23.1 | 100%
[5 empty] | 23.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2748.352 | 44370.5687 | 23.11 | 100%
[5 empty] | 23.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2750.6185 | 44407.1597 | 23.12 | 100%
[5 empty] | 23.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2752.885 | 44443.7506 | 23.13 | 100%
[5 empty] | 23.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2755.1515 | 44480.3416 | 23.14 | 100%
[5 empty] | 23.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2757.4179 | 44516.9325 | 23.15 | 100%
[5 empty] | 23.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2759.6844 | 44553.5234 | 23.16 | 100%
[5 empty] | 23.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2761.9509 | 44590.1144 | 23.17 | 100%
[5 empty] | 23.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2764.2174 | 44626.7053 | 23.18 | 100%
[5 empty] | 23.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2766.4838 | 44663.2963 | 23.19 | 100%
[5 empty] | 23.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2768.7503 | 44699.8872 | 23.2 | 100%
[5 empty] | 23.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2771.0168 | 44736.4782 | 23.21 | 100%
[5 empty] | 23.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2773.2833 | 44773.0691 | 23.22 | 100%
[5 empty] | 23.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2775.5497 | 44809.6601 | 23.23 | 100%
[5 empty] | 23.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2777.8162 | 44846.251 | 23.24 | 100%
[5 empty] | 23.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2780.0827 | 44882.8419 | 23.25 | 100%
[5 empty] | 23.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2782.3492 | 44919.4329 | 23.26 | 100%
[5 empty] | 23.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2784.6156 | 44956.0238 | 23.27 | 100%
[5 empty] | 23.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2786.8821 | 44992.6148 | 23.28 | 100%
[5 empty] | 23.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2789.1486 | 45029.2057 | 23.29 | 100%
[5 empty] | 23.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2791.4151 | 45065.7967 | 23.3 | 100%
[5 empty] | 23.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2793.6815 | 45102.3876 | 23.31 | 100%
[5 empty] | 23.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2795.948 | 45138.9785 | 23.32 | 100%
[5 empty] | 23.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2798.2145 | 45175.5695 | 23.33 | 100%
[5 empty] | 23.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2800.481 | 45212.1604 | 23.34 | 100%
[5 empty] | 23.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2802.7474 | 45248.7514 | 23.35 | 100%
[5 empty] | 23.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2805.0139 | 45285.3423 | 23.36 | 100%
[5 empty] | 23.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2807.2804 | 45321.9333 | 23.37 | 100%
[5 empty] | 23.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2809.5469 | 45358.5242 | 23.38 | 100%
[5 empty] | 23.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2811.8133 | 45395.1151 | 23.39 | 100%
[5 empty] | 23.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2814.0798 | 45431.7061 | 23.4 | 100%
[5 empty] | 23.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2816.3463 | 45468.297 | 23.41 | 100%
[5 empty] | 23.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2818.6128 | 45504.888 | 23.42 | 100%
[5 empty] | 23.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2820.8792 | 45541.4789 | 23.43 | 100%
[5 empty] | 23.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2823.1457 | 45578.0699 | 23.44 | 100%
[5 empty] | 23.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2825.4122 | 45614.6608 | 23.45 | 100%
[5 empty] | 23.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2827.6787 | 45651.2518 | 23.46 | 100%
[5 empty] | 23.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2829.9451 | 45687.8427 | 23.47 | 100%
[5 empty] | 23.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2832.2116 | 45724.4336 | 23.48 | 100%
[5 empty] | 23.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2834.4781 | 45761.0246 | 23.49 | 100%
[5 empty] | 23.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2836.7446 | 45797.6155 | 23.5 | 100%
[5 empty] | 23.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2839.011 | 45834.2065 | 23.51 | 100%
[5 empty] | 23.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2841.2775 | 45870.7974 | 23.52 | 100%
[5 empty] | 23.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2843.544 | 45907.3884 | 23.53 | 100%
[5 empty] | 23.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2845.8105 | 45943.9793 | 23.54 | 100%
[5 empty] | 23.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2848.0769 | 45980.5702 | 23.55 | 100%
[5 empty] | 23.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2850.3434 | 46017.1612 | 23.56 | 100%
[5 empty] | 23.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2852.6099 | 46053.7521 | 23.57 | 100%
[5 empty] | 23.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2854.8764 | 46090.3431 | 23.58 | 100%
[5 empty] | 23.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2857.1428 | 46126.934 | 23.59 | 100%
[5 empty] | 23.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2859.4093 | 46163.525 | 23.6 | 100%
[5 empty] | 23.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2861.6758 | 46200.1159 | 23.61 | 100%
[5 empty] | 23.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2863.9423 | 46236.7069 | 23.62 | 100%
[5 empty] | 23.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2866.2087 | 46273.2978 | 23.63 | 100%
[5 empty] | 23.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2868.4752 | 46309.8887 | 23.64 | 100%
[5 empty] | 23.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2870.7417 | 46346.4797 | 23.65 | 100%
[5 empty] | 23.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2873.0082 | 46383.0706 | 23.66 | 100%
[5 empty] | 23.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2875.2746 | 46419.6616 | 23.67 | 100%
[5 empty] | 23.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2877.5411 | 46456.2525 | 23.68 | 100%
[5 empty] | 23.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2879.8076 | 46492.8435 | 23.69 | 100%
[5 empty] | 23.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2882.0741 | 46529.4344 | 23.7 | 100%
[5 empty] | 23.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2884.3405 | 46566.0253 | 23.71 | 100%
[5 empty] | 23.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2886.607 | 46602.6163 | 23.72 | 100%
[5 empty] | 23.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2888.8735 | 46639.2072 | 23.73 | 100%
[5 empty] | 23.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2891.14 | 46675.7982 | 23.74 | 100%
[5 empty] | 23.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2893.4064 | 46712.3891 | 23.75 | 100%
[5 empty] | 23.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2895.6729 | 46748.9801 | 23.76 | 100%
[5 empty] | 23.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2897.9394 | 46785.571 | 23.77 | 100%
[5 empty] | 23.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2900.2059 | 46822.162 | 23.78 | 100%
[5 empty] | 23.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2902.4723 | 46858.7529 | 23.79 | 100%
[5 empty] | 23.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2904.7388 | 46895.3438 | 23.8 | 100%
[5 empty] | 23.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2907.0053 | 46931.9348 | 23.81 | 100%
[5 empty] | 23.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2909.2718 | 46968.5257 | 23.82 | 100%
[5 empty] | 23.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2911.5382 | 47005.1167 | 23.83 | 100%
[5 empty] | 23.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2913.8047 | 47041.7076 | 23.84 | 100%
[5 empty] | 23.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2916.0712 | 47078.2986 | 23.85 | 100%
[5 empty] | 23.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2918.3377 | 47114.8895 | 23.86 | 100%
[5 empty] | 23.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2920.6041 | 47151.4804 | 23.87 | 100%
[5 empty] | 23.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2922.8706 | 47188.0714 | 23.88 | 100%
[5 empty] | 23.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2925.1371 | 47224.6623 | 23.89 | 100%
[5 empty] | 23.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2927.4036 | 47261.2533 | 23.9 | 100%
[5 empty] | 23.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2929.67 | 47297.8442 | 23.91 | 100%
[5 empty] | 23.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2931.9365 | 47334.4352 | 23.92 | 100%
[5 empty] | 23.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2934.203 | 47371.0261 | 23.93 | 100%
[5 empty] | 23.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2936.4695 | 47407.617 | 23.94 | 100%
[5 empty] | 23.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2938.7359 | 47444.208 | 23.95 | 100%
[5 empty] | 23.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2941.0024 | 47480.7989 | 23.96 | 100%
[5 empty] | 23.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2943.2689 | 47517.3899 | 23.97 | 100%
[5 empty] | 23.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2945.5354 | 47553.9808 | 23.98 | 100%
[5 empty] | 23.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2947.8018 | 47590.5718 | 23.99 | 100%
[5 empty] | 24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2950.0683 | 47627.1627 | 24 | 100%
[5 empty] | 24.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2952.3348 | 47663.7537 | 24.01 | 100%
[5 empty] | 24.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2954.6013 | 47700.3446 | 24.02 | 100%
[5 empty] | 24.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2956.8677 | 47736.9355 | 24.03 | 100%
[5 empty] | 24.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2959.1342 | 47773.5265 | 24.04 | 100%
[5 empty] | 24.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2961.4007 | 47810.1174 | 24.05 | 100%
[5 empty] | 24.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2963.6672 | 47846.7084 | 24.06 | 100%
[5 empty] | 24.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2965.9336 | 47883.2993 | 24.07 | 100%
[5 empty] | 24.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2968.2001 | 47919.8903 | 24.08 | 100%
[5 empty] | 24.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2970.4666 | 47956.4812 | 24.09 | 100%
[5 empty] | 24.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2972.7331 | 47993.0721 | 24.1 | 100%
[5 empty] | 24.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2974.9995 | 48029.6631 | 24.11 | 100%
[5 empty] | 24.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2977.266 | 48066.254 | 24.12 | 100%
[5 empty] | 24.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2979.5325 | 48102.845 | 24.13 | 100%
[5 empty] | 24.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2981.799 | 48139.4359 | 24.14 | 100%
[5 empty] | 24.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2984.0654 | 48176.0269 | 24.15 | 100%
[5 empty] | 24.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2986.3319 | 48212.6178 | 24.16 | 100%
[5 empty] | 24.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2988.5984 | 48249.2088 | 24.17 | 100%
[5 empty] | 24.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2990.8649 | 48285.7997 | 24.18 | 100%
[5 empty] | 24.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2993.1313 | 48322.3906 | 24.19 | 100%
[5 empty] | 24.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2995.3978 | 48358.9816 | 24.2 | 100%
[5 empty] | 24.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2997.6643 | 48395.5725 | 24.21 | 100%
[5 empty] | 24.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 2999.9308 | 48432.1635 | 24.22 | 100%
[5 empty] | 24.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3002.1972 | 48468.7544 | 24.23 | 100%
[5 empty] | 24.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3004.4637 | 48505.3454 | 24.24 | 100%
[5 empty] | 24.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3006.7302 | 48541.9363 | 24.25 | 100%
[5 empty] | 24.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3008.9967 | 48578.5272 | 24.26 | 100%
[5 empty] | 24.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3011.2632 | 48615.1182 | 24.27 | 100%
[5 empty] | 24.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3013.5296 | 48651.7091 | 24.28 | 100%
[5 empty] | 24.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3015.7961 | 48688.3001 | 24.29 | 100%
[5 empty] | 24.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3018.0626 | 48724.891 | 24.3 | 100%
[5 empty] | 24.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3020.3291 | 48761.482 | 24.31 | 100%
[5 empty] | 24.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3022.5955 | 48798.0729 | 24.32 | 100%
[5 empty] | 24.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3024.862 | 48834.6639 | 24.33 | 100%
[5 empty] | 24.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3027.1285 | 48871.2548 | 24.34 | 100%
[5 empty] | 24.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3029.395 | 48907.8457 | 24.35 | 100%
[5 empty] | 24.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3031.6614 | 48944.4367 | 24.36 | 100%
[5 empty] | 24.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3033.9279 | 48981.0276 | 24.37 | 100%
[5 empty] | 24.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3036.1944 | 49017.6186 | 24.38 | 100%
[5 empty] | 24.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3038.4609 | 49054.2095 | 24.39 | 100%
[5 empty] | 24.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3040.7273 | 49090.8005 | 24.4 | 100%
[5 empty] | 24.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3042.9938 | 49127.3914 | 24.41 | 100%
[5 empty] | 24.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3045.2603 | 49163.9823 | 24.42 | 100%
[5 empty] | 24.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3047.5268 | 49200.5733 | 24.43 | 100%
[5 empty] | 24.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3049.7932 | 49237.1642 | 24.44 | 100%
[5 empty] | 24.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3052.0597 | 49273.7552 | 24.45 | 100%
[5 empty] | 24.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3054.3262 | 49310.3461 | 24.46 | 100%
[5 empty] | 24.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3056.5927 | 49346.9371 | 24.47 | 100%
[5 empty] | 24.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3058.8591 | 49383.528 | 24.48 | 100%
[5 empty] | 24.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3061.1256 | 49420.1189 | 24.49 | 100%
[5 empty] | 24.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3063.3921 | 49456.7099 | 24.5 | 100%
[5 empty] | 24.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3065.6586 | 49493.3008 | 24.51 | 100%
[5 empty] | 24.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3067.925 | 49529.8918 | 24.52 | 100%
[5 empty] | 24.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3070.1915 | 49566.4827 | 24.53 | 100%
[5 empty] | 24.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3072.458 | 49603.0737 | 24.54 | 100%
[5 empty] | 24.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3074.7245 | 49639.6646 | 24.55 | 100%
[5 empty] | 24.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3076.9909 | 49676.2556 | 24.56 | 100%
[5 empty] | 24.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3079.2574 | 49712.8465 | 24.57 | 100%
[5 empty] | 24.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3081.5239 | 49749.4374 | 24.58 | 100%
[5 empty] | 24.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3083.7904 | 49786.0284 | 24.59 | 100%
[5 empty] | 24.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3086.0568 | 49822.6193 | 24.6 | 100%
[5 empty] | 24.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3088.3233 | 49859.2103 | 24.61 | 100%
[5 empty] | 24.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3090.5898 | 49895.8012 | 24.62 | 100%
[5 empty] | 24.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3092.8563 | 49932.3922 | 24.63 | 100%
[5 empty] | 24.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3095.1227 | 49968.9831 | 24.64 | 100%
[5 empty] | 24.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3097.3892 | 50005.574 | 24.65 | 100%
[5 empty] | 24.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3099.6557 | 50042.165 | 24.66 | 100%
[5 empty] | 24.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3101.9222 | 50078.7559 | 24.67 | 100%
[5 empty] | 24.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3104.1886 | 50115.3469 | 24.68 | 100%
[5 empty] | 24.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3106.4551 | 50151.9378 | 24.69 | 100%
[5 empty] | 24.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3108.7216 | 50188.5288 | 24.7 | 100%
[5 empty] | 24.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3110.9881 | 50225.1197 | 24.71 | 100%
[5 empty] | 24.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3113.2545 | 50261.7107 | 24.72 | 100%
[5 empty] | 24.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3115.521 | 50298.3016 | 24.73 | 100%
[5 empty] | 24.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3117.7875 | 50334.8925 | 24.74 | 100%
[5 empty] | 24.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3120.054 | 50371.4835 | 24.75 | 100%
[5 empty] | 24.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3122.3204 | 50408.0744 | 24.76 | 100%
[5 empty] | 24.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3124.5869 | 50444.6654 | 24.77 | 100%
[5 empty] | 24.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3126.8534 | 50481.2563 | 24.78 | 100%
[5 empty] | 24.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3129.1199 | 50517.8473 | 24.79 | 100%
[5 empty] | 24.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3131.3863 | 50554.4382 | 24.8 | 100%
[5 empty] | 24.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3133.6528 | 50591.0291 | 24.81 | 100%
[5 empty] | 24.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3135.9193 | 50627.6201 | 24.82 | 100%
[5 empty] | 24.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3138.1858 | 50664.211 | 24.83 | 100%
[5 empty] | 24.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3140.4522 | 50700.802 | 24.84 | 100%
[5 empty] | 24.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3142.7187 | 50737.3929 | 24.85 | 100%
[5 empty] | 24.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3144.9852 | 50773.9839 | 24.86 | 100%
[5 empty] | 24.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3147.2517 | 50810.5748 | 24.87 | 100%
[5 empty] | 24.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3149.5181 | 50847.1657 | 24.88 | 100%
[5 empty] | 24.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3151.7846 | 50883.7567 | 24.89 | 100%
[5 empty] | 24.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3154.0511 | 50920.3476 | 24.9 | 100%
[5 empty] | 24.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3156.3176 | 50956.9386 | 24.91 | 100%
[5 empty] | 24.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3158.584 | 50993.5295 | 24.92 | 100%
[5 empty] | 24.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3160.8505 | 51030.1205 | 24.93 | 100%
[5 empty] | 24.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3163.117 | 51066.7114 | 24.94 | 100%
[5 empty] | 24.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3165.3835 | 51103.3024 | 24.95 | 100%
[5 empty] | 24.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3167.6499 | 51139.8933 | 24.96 | 100%
[5 empty] | 24.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3169.9164 | 51176.4842 | 24.97 | 100%
[5 empty] | 24.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3172.1829 | 51213.0752 | 24.98 | 100%
[5 empty] | 24.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3174.4494 | 51249.6661 | 24.99 | 100%
[5 empty] | 25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3176.7158 | 51286.2571 | 25 | 100%
[5 empty] | 25.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3178.9823 | 51322.848 | 25.01 | 100%
[5 empty] | 25.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3181.2488 | 51359.439 | 25.02 | 100%
[5 empty] | 25.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3183.5153 | 51396.0299 | 25.03 | 100%
[5 empty] | 25.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3185.7817 | 51432.6208 | 25.04 | 100%
[5 empty] | 25.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3188.0482 | 51469.2118 | 25.05 | 100%
[5 empty] | 25.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3190.3147 | 51505.8027 | 25.06 | 100%
[5 empty] | 25.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3192.5812 | 51542.3937 | 25.07 | 100%
[5 empty] | 25.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3194.8476 | 51578.9846 | 25.08 | 100%
[5 empty] | 25.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3197.1141 | 51615.5756 | 25.09 | 100%
[5 empty] | 25.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3199.3806 | 51652.1665 | 25.1 | 100%
[5 empty] | 25.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3201.6471 | 51688.7575 | 25.11 | 100%
[5 empty] | 25.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3203.9135 | 51725.3484 | 25.12 | 100%
[5 empty] | 25.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3206.18 | 51761.9393 | 25.13 | 100%
[5 empty] | 25.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3208.4465 | 51798.5303 | 25.14 | 100%
[5 empty] | 25.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3210.713 | 51835.1212 | 25.15 | 100%
[5 empty] | 25.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3212.9794 | 51871.7122 | 25.16 | 100%
[5 empty] | 25.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3215.2459 | 51908.3031 | 25.17 | 100%
[5 empty] | 25.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3217.5124 | 51944.8941 | 25.18 | 100%
[5 empty] | 25.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3219.7789 | 51981.485 | 25.19 | 100%
[5 empty] | 25.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3222.0453 | 52018.0759 | 25.2 | 100%
[5 empty] | 25.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3224.3118 | 52054.6669 | 25.21 | 100%
[5 empty] | 25.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3226.5783 | 52091.2578 | 25.22 | 100%
[5 empty] | 25.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3228.8448 | 52127.8488 | 25.23 | 100%
[5 empty] | 25.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3231.1112 | 52164.4397 | 25.24 | 100%
[5 empty] | 25.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3233.3777 | 52201.0307 | 25.25 | 100%
[5 empty] | 25.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3235.6442 | 52237.6216 | 25.26 | 100%
[5 empty] | 25.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3237.9107 | 52274.2126 | 25.27 | 100%
[5 empty] | 25.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3240.1771 | 52310.8035 | 25.28 | 100%
[5 empty] | 25.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3242.4436 | 52347.3944 | 25.29 | 100%
[5 empty] | 25.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3244.7101 | 52383.9854 | 25.3 | 100%
[5 empty] | 25.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3246.9766 | 52420.5763 | 25.31 | 100%
[5 empty] | 25.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3249.243 | 52457.1673 | 25.32 | 100%
[5 empty] | 25.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3251.5095 | 52493.7582 | 25.33 | 100%
[5 empty] | 25.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3253.776 | 52530.3492 | 25.34 | 100%
[5 empty] | 25.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3256.0425 | 52566.9401 | 25.35 | 100%
[5 empty] | 25.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3258.3089 | 52603.531 | 25.36 | 100%
[5 empty] | 25.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3260.5754 | 52640.122 | 25.37 | 100%
[5 empty] | 25.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3262.8419 | 52676.7129 | 25.38 | 100%
[5 empty] | 25.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3265.1084 | 52713.3039 | 25.39 | 100%
[5 empty] | 25.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3267.3748 | 52749.8948 | 25.4 | 100%
[5 empty] | 25.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3269.6413 | 52786.4858 | 25.41 | 100%
[5 empty] | 25.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3271.9078 | 52823.0767 | 25.42 | 100%
[5 empty] | 25.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3274.1743 | 52859.6676 | 25.43 | 100%
[5 empty] | 25.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3276.4408 | 52896.2586 | 25.44 | 100%
[5 empty] | 25.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3278.7072 | 52932.8495 | 25.45 | 100%
[5 empty] | 25.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3280.9737 | 52969.4405 | 25.46 | 100%
[5 empty] | 25.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3283.2402 | 53006.0314 | 25.47 | 100%
[5 empty] | 25.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3285.5067 | 53042.6224 | 25.48 | 100%
[5 empty] | 25.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3287.7731 | 53079.2133 | 25.49 | 100%
[5 empty] | 25.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3290.0396 | 53115.8043 | 25.5 | 100%
[5 empty] | 25.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3292.3061 | 53152.3952 | 25.51 | 100%
[5 empty] | 25.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3294.5726 | 53188.9861 | 25.52 | 100%
[5 empty] | 25.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3296.839 | 53225.5771 | 25.53 | 100%
[5 empty] | 25.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3299.1055 | 53262.168 | 25.54 | 100%
[5 empty] | 25.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3301.372 | 53298.759 | 25.55 | 100%
[5 empty] | 25.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3303.6385 | 53335.3499 | 25.56 | 100%
[5 empty] | 25.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3305.9049 | 53371.9409 | 25.57 | 100%
[5 empty] | 25.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3308.1714 | 53408.5318 | 25.58 | 100%
[5 empty] | 25.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3310.4379 | 53445.1227 | 25.59 | 100%
[5 empty] | 25.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3312.7044 | 53481.7137 | 25.6 | 100%
[5 empty] | 25.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3314.9708 | 53518.3046 | 25.61 | 100%
[5 empty] | 25.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3317.2373 | 53554.8956 | 25.62 | 100%
[5 empty] | 25.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3319.5038 | 53591.4865 | 25.63 | 100%
[5 empty] | 25.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3321.7703 | 53628.0775 | 25.64 | 100%
[5 empty] | 25.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3324.0367 | 53664.6684 | 25.65 | 100%
[5 empty] | 25.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3326.3032 | 53701.2594 | 25.66 | 100%
[5 empty] | 25.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3328.5697 | 53737.8503 | 25.67 | 100%
[5 empty] | 25.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3330.8362 | 53774.4412 | 25.68 | 100%
[5 empty] | 25.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3333.1026 | 53811.0322 | 25.69 | 100%
[5 empty] | 25.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3335.3691 | 53847.6231 | 25.7 | 100%
[5 empty] | 25.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3337.6356 | 53884.2141 | 25.71 | 100%
[5 empty] | 25.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3339.9021 | 53920.805 | 25.72 | 100%
[5 empty] | 25.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3342.1685 | 53957.396 | 25.73 | 100%
[5 empty] | 25.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3344.435 | 53993.9869 | 25.74 | 100%
[5 empty] | 25.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3346.7015 | 54030.5778 | 25.75 | 100%
[5 empty] | 25.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3348.968 | 54067.1688 | 25.76 | 100%
[5 empty] | 25.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3351.2344 | 54103.7597 | 25.77 | 100%
[5 empty] | 25.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3353.5009 | 54140.3507 | 25.78 | 100%
[5 empty] | 25.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3355.7674 | 54176.9416 | 25.79 | 100%
[5 empty] | 25.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3358.0339 | 54213.5326 | 25.8 | 100%
[5 empty] | 25.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3360.3003 | 54250.1235 | 25.81 | 100%
[5 empty] | 25.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3362.5668 | 54286.7145 | 25.82 | 100%
[5 empty] | 25.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3364.8333 | 54323.3054 | 25.83 | 100%
[5 empty] | 25.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3367.0998 | 54359.8963 | 25.84 | 100%
[5 empty] | 25.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3369.3662 | 54396.4873 | 25.85 | 100%
[5 empty] | 25.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3371.6327 | 54433.0782 | 25.86 | 100%
[5 empty] | 25.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3373.8992 | 54469.6692 | 25.87 | 100%
[5 empty] | 25.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3376.1657 | 54506.2601 | 25.88 | 100%
[5 empty] | 25.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3378.4321 | 54542.8511 | 25.89 | 100%
[5 empty] | 25.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3380.6986 | 54579.442 | 25.9 | 100%
[5 empty] | 25.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3382.9651 | 54616.0329 | 25.91 | 100%
[5 empty] | 25.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3385.2316 | 54652.6239 | 25.92 | 100%
[5 empty] | 25.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3387.498 | 54689.2148 | 25.93 | 100%
[5 empty] | 25.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3389.7645 | 54725.8058 | 25.94 | 100%
[5 empty] | 25.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3392.031 | 54762.3967 | 25.95 | 100%
[5 empty] | 25.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3394.2975 | 54798.9877 | 25.96 | 100%
[5 empty] | 25.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3396.5639 | 54835.5786 | 25.97 | 100%
[5 empty] | 25.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3398.8304 | 54872.1695 | 25.98 | 100%
[5 empty] | 25.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3401.0969 | 54908.7605 | 25.99 | 100%
[5 empty] | 26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3403.3634 | 54945.3514 | 26 | 100%
[5 empty] | 26.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3405.6298 | 54981.9424 | 26.01 | 100%
[5 empty] | 26.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3407.8963 | 55018.5333 | 26.02 | 100%
[5 empty] | 26.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3410.1628 | 55055.1243 | 26.03 | 100%
[5 empty] | 26.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3412.4293 | 55091.7152 | 26.04 | 100%
[5 empty] | 26.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3414.6957 | 55128.3062 | 26.05 | 100%
[5 empty] | 26.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3416.9622 | 55164.8971 | 26.06 | 100%
[5 empty] | 26.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3419.2287 | 55201.488 | 26.07 | 100%
[5 empty] | 26.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3421.4952 | 55238.079 | 26.08 | 100%
[5 empty] | 26.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3423.7616 | 55274.6699 | 26.09 | 100%
[5 empty] | 26.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3426.0281 | 55311.2609 | 26.1 | 100%
[5 empty] | 26.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3428.2946 | 55347.8518 | 26.11 | 100%
[5 empty] | 26.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3430.5611 | 55384.4428 | 26.12 | 100%
[5 empty] | 26.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3432.8275 | 55421.0337 | 26.13 | 100%
[5 empty] | 26.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3435.094 | 55457.6246 | 26.14 | 100%
[5 empty] | 26.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3437.3605 | 55494.2156 | 26.15 | 100%
[5 empty] | 26.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3439.627 | 55530.8065 | 26.16 | 100%
[5 empty] | 26.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3441.8934 | 55567.3975 | 26.17 | 100%
[5 empty] | 26.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3444.1599 | 55603.9884 | 26.18 | 100%
[5 empty] | 26.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3446.4264 | 55640.5794 | 26.19 | 100%
[5 empty] | 26.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3448.6929 | 55677.1703 | 26.2 | 100%
[5 empty] | 26.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3450.9593 | 55713.7613 | 26.21 | 100%
[5 empty] | 26.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3453.2258 | 55750.3522 | 26.22 | 100%
[5 empty] | 26.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3455.4923 | 55786.9431 | 26.23 | 100%
[5 empty] | 26.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3457.7588 | 55823.5341 | 26.24 | 100%
[5 empty] | 26.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3460.0252 | 55860.125 | 26.25 | 100%
[5 empty] | 26.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3462.2917 | 55896.716 | 26.26 | 100%
[5 empty] | 26.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3464.5582 | 55933.3069 | 26.27 | 100%
[5 empty] | 26.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3466.8247 | 55969.8979 | 26.28 | 100%
[5 empty] | 26.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3469.0911 | 56006.4888 | 26.29 | 100%
[5 empty] | 26.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3471.3576 | 56043.0797 | 26.3 | 100%
[5 empty] | 26.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3473.6241 | 56079.6707 | 26.31 | 100%
[5 empty] | 26.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3475.8906 | 56116.2616 | 26.32 | 100%
[5 empty] | 26.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3478.157 | 56152.8526 | 26.33 | 100%
[5 empty] | 26.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3480.4235 | 56189.4435 | 26.34 | 100%
[5 empty] | 26.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3482.69 | 56226.0345 | 26.35 | 100%
[5 empty] | 26.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3484.9565 | 56262.6254 | 26.36 | 100%
[5 empty] | 26.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3487.2229 | 56299.2164 | 26.37 | 100%
[5 empty] | 26.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3489.4894 | 56335.8073 | 26.38 | 100%
[5 empty] | 26.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3491.7559 | 56372.3982 | 26.39 | 100%
[5 empty] | 26.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3494.0224 | 56408.9892 | 26.4 | 100%
[5 empty] | 26.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3496.2888 | 56445.5801 | 26.41 | 100%
[5 empty] | 26.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3498.5553 | 56482.1711 | 26.42 | 100%
[5 empty] | 26.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3500.8218 | 56518.762 | 26.43 | 100%
[5 empty] | 26.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3503.0883 | 56555.353 | 26.44 | 100%
[5 empty] | 26.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3505.3547 | 56591.9439 | 26.45 | 100%
[5 empty] | 26.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3507.6212 | 56628.5348 | 26.46 | 100%
[5 empty] | 26.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3509.8877 | 56665.1258 | 26.47 | 100%
[5 empty] | 26.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3512.1542 | 56701.7167 | 26.48 | 100%
[5 empty] | 26.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3514.4206 | 56738.3077 | 26.49 | 100%
[5 empty] | 26.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3516.6871 | 56774.8986 | 26.5 | 100%
[5 empty] | 26.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3518.9536 | 56811.4896 | 26.51 | 100%
[5 empty] | 26.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3521.2201 | 56848.0805 | 26.52 | 100%
[5 empty] | 26.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3523.4865 | 56884.6714 | 26.53 | 100%
[5 empty] | 26.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3525.753 | 56921.2624 | 26.54 | 100%
[5 empty] | 26.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3528.0195 | 56957.8533 | 26.55 | 100%
[5 empty] | 26.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3530.286 | 56994.4443 | 26.56 | 100%
[5 empty] | 26.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3532.5524 | 57031.0352 | 26.57 | 100%
[5 empty] | 26.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3534.8189 | 57067.6262 | 26.58 | 100%
[5 empty] | 26.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3537.0854 | 57104.2171 | 26.59 | 100%
[5 empty] | 26.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3539.3519 | 57140.8081 | 26.6 | 100%
[5 empty] | 26.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3541.6183 | 57177.399 | 26.61 | 100%
[5 empty] | 26.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3543.8848 | 57213.9899 | 26.62 | 100%
[5 empty] | 26.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3546.1513 | 57250.5809 | 26.63 | 100%
[5 empty] | 26.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3548.4178 | 57287.1718 | 26.64 | 100%
[5 empty] | 26.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3550.6843 | 57323.7628 | 26.65 | 100%
[5 empty] | 26.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3552.9507 | 57360.3537 | 26.66 | 100%
[5 empty] | 26.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3555.2172 | 57396.9447 | 26.67 | 100%
[5 empty] | 26.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3557.4837 | 57433.5356 | 26.68 | 100%
[5 empty] | 26.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3559.7502 | 57470.1265 | 26.69 | 100%
[5 empty] | 26.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3562.0166 | 57506.7175 | 26.7 | 100%
[5 empty] | 26.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3564.2831 | 57543.3084 | 26.71 | 100%
[5 empty] | 26.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3566.5496 | 57579.8994 | 26.72 | 100%
[5 empty] | 26.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3568.8161 | 57616.4903 | 26.73 | 100%
[5 empty] | 26.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3571.0825 | 57653.0813 | 26.74 | 100%
[5 empty] | 26.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3573.349 | 57689.6722 | 26.75 | 100%
[5 empty] | 26.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3575.6155 | 57726.2632 | 26.76 | 100%
[5 empty] | 26.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3577.882 | 57762.8541 | 26.77 | 100%
[5 empty] | 26.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3580.1484 | 57799.445 | 26.78 | 100%
[5 empty] | 26.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3582.4149 | 57836.036 | 26.79 | 100%
[5 empty] | 26.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3584.6814 | 57872.6269 | 26.8 | 100%
[5 empty] | 26.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3586.9479 | 57909.2179 | 26.81 | 100%
[5 empty] | 26.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3589.2143 | 57945.8088 | 26.82 | 100%
[5 empty] | 26.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3591.4808 | 57982.3998 | 26.83 | 100%
[5 empty] | 26.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3593.7473 | 58018.9907 | 26.84 | 100%
[5 empty] | 26.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3596.0138 | 58055.5816 | 26.85 | 100%
[5 empty] | 26.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3598.2802 | 58092.1726 | 26.86 | 100%
[5 empty] | 26.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3600.5467 | 58128.7635 | 26.87 | 100%
[5 empty] | 26.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3602.8132 | 58165.3545 | 26.88 | 100%
[5 empty] | 26.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3605.0797 | 58201.9454 | 26.89 | 100%
[5 empty] | 26.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3607.3461 | 58238.5364 | 26.9 | 100%
[5 empty] | 26.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3609.6126 | 58275.1273 | 26.91 | 100%
[5 empty] | 26.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3611.8791 | 58311.7182 | 26.92 | 100%
[5 empty] | 26.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3614.1456 | 58348.3092 | 26.93 | 100%
[5 empty] | 26.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3616.412 | 58384.9001 | 26.94 | 100%
[5 empty] | 26.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3618.6785 | 58421.4911 | 26.95 | 100%
[5 empty] | 26.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3620.945 | 58458.082 | 26.96 | 100%
[5 empty] | 26.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3623.2115 | 58494.673 | 26.97 | 100%
[5 empty] | 26.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3625.4779 | 58531.2639 | 26.98 | 100%
[5 empty] | 26.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3627.7444 | 58567.8549 | 26.99 | 100%
[5 empty] | 27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3630.0109 | 58604.4458 | 27 | 100%
[5 empty] | 27.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3632.2774 | 58641.0367 | 27.01 | 100%
[5 empty] | 27.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3634.5438 | 58677.6277 | 27.02 | 100%
[5 empty] | 27.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3636.8103 | 58714.2186 | 27.03 | 100%
[5 empty] | 27.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3639.0768 | 58750.8096 | 27.04 | 100%
[5 empty] | 27.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3641.3433 | 58787.4005 | 27.05 | 100%
[5 empty] | 27.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3643.6097 | 58823.9915 | 27.06 | 100%
[5 empty] | 27.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3645.8762 | 58860.5824 | 27.07 | 100%
[5 empty] | 27.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3648.1427 | 58897.1733 | 27.08 | 100%
[5 empty] | 27.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3650.4092 | 58933.7643 | 27.09 | 100%
[5 empty] | 27.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3652.6756 | 58970.3552 | 27.1 | 100%
[5 empty] | 27.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3654.9421 | 59006.9462 | 27.11 | 100%
[5 empty] | 27.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3657.2086 | 59043.5371 | 27.12 | 100%
[5 empty] | 27.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3659.4751 | 59080.1281 | 27.13 | 100%
[5 empty] | 27.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3661.7415 | 59116.719 | 27.14 | 100%
[5 empty] | 27.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3664.008 | 59153.31 | 27.15 | 100%
[5 empty] | 27.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3666.2745 | 59189.9009 | 27.16 | 100%
[5 empty] | 27.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3668.541 | 59226.4918 | 27.17 | 100%
[5 empty] | 27.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3670.8074 | 59263.0828 | 27.18 | 100%
[5 empty] | 27.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3673.0739 | 59299.6737 | 27.19 | 100%
[5 empty] | 27.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3675.3404 | 59336.2647 | 27.2 | 100%
[5 empty] | 27.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3677.6069 | 59372.8556 | 27.21 | 100%
[5 empty] | 27.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3679.8733 | 59409.4466 | 27.22 | 100%
[5 empty] | 27.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3682.1398 | 59446.0375 | 27.23 | 100%
[5 empty] | 27.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3684.4063 | 59482.6284 | 27.24 | 100%
[5 empty] | 27.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3686.6728 | 59519.2194 | 27.25 | 100%
[5 empty] | 27.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3688.9392 | 59555.8103 | 27.26 | 100%
[5 empty] | 27.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3691.2057 | 59592.4013 | 27.27 | 100%
[5 empty] | 27.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3693.4722 | 59628.9922 | 27.28 | 100%
[5 empty] | 27.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3695.7387 | 59665.5832 | 27.29 | 100%
[5 empty] | 27.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3698.0051 | 59702.1741 | 27.3 | 100%
[5 empty] | 27.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3700.2716 | 59738.7651 | 27.31 | 100%
[5 empty] | 27.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3702.5381 | 59775.356 | 27.32 | 100%
[5 empty] | 27.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3704.8046 | 59811.9469 | 27.33 | 100%
[5 empty] | 27.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3707.071 | 59848.5379 | 27.34 | 100%
[5 empty] | 27.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3709.3375 | 59885.1288 | 27.35 | 100%
[5 empty] | 27.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3711.604 | 59921.7198 | 27.36 | 100%
[5 empty] | 27.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3713.8705 | 59958.3107 | 27.37 | 100%
[5 empty] | 27.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3716.1369 | 59994.9017 | 27.38 | 100%
[5 empty] | 27.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3718.4034 | 60031.4926 | 27.39 | 100%
[5 empty] | 27.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3720.6699 | 60068.0835 | 27.4 | 100%
[5 empty] | 27.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3722.9364 | 60104.6745 | 27.41 | 100%
[5 empty] | 27.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3725.2028 | 60141.2654 | 27.42 | 100%
[5 empty] | 27.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3727.4693 | 60177.8564 | 27.43 | 100%
[5 empty] | 27.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3729.7358 | 60214.4473 | 27.44 | 100%
[5 empty] | 27.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3732.0023 | 60251.0383 | 27.45 | 100%
[5 empty] | 27.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3734.2687 | 60287.6292 | 27.46 | 100%
[5 empty] | 27.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3736.5352 | 60324.2201 | 27.47 | 100%
[5 empty] | 27.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3738.8017 | 60360.8111 | 27.48 | 100%
[5 empty] | 27.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3741.0682 | 60397.402 | 27.49 | 100%
[5 empty] | 27.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3743.3346 | 60433.993 | 27.5 | 100%
[5 empty] | 27.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3745.6011 | 60470.5839 | 27.51 | 100%
[5 empty] | 27.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3747.8676 | 60507.1749 | 27.52 | 100%
[5 empty] | 27.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3750.1341 | 60543.7658 | 27.53 | 100%
[5 empty] | 27.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3752.4005 | 60580.3568 | 27.54 | 100%
[5 empty] | 27.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3754.667 | 60616.9477 | 27.55 | 100%
[5 empty] | 27.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3756.9335 | 60653.5386 | 27.56 | 100%
[5 empty] | 27.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3759.2 | 60690.1296 | 27.57 | 100%
[5 empty] | 27.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3761.4664 | 60726.7205 | 27.58 | 100%
[5 empty] | 27.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3763.7329 | 60763.3115 | 27.59 | 100%
[5 empty] | 27.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3765.9994 | 60799.9024 | 27.6 | 100%
[5 empty] | 27.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3768.2659 | 60836.4934 | 27.61 | 100%
[5 empty] | 27.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3770.5323 | 60873.0843 | 27.62 | 100%
[5 empty] | 27.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3772.7988 | 60909.6752 | 27.63 | 100%
[5 empty] | 27.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3775.0653 | 60946.2662 | 27.64 | 100%
[5 empty] | 27.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3777.3318 | 60982.8571 | 27.65 | 100%
[5 empty] | 27.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3779.5982 | 61019.4481 | 27.66 | 100%
[5 empty] | 27.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3781.8647 | 61056.039 | 27.67 | 100%
[5 empty] | 27.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3784.1312 | 61092.63 | 27.68 | 100%
[5 empty] | 27.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3786.3977 | 61129.2209 | 27.69 | 100%
[5 empty] | 27.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3788.6641 | 61165.8119 | 27.7 | 100%
[5 empty] | 27.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3790.9306 | 61202.4028 | 27.71 | 100%
[5 empty] | 27.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3793.1971 | 61238.9937 | 27.72 | 100%
[5 empty] | 27.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3795.4636 | 61275.5847 | 27.73 | 100%
[5 empty] | 27.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3797.73 | 61312.1756 | 27.74 | 100%
[5 empty] | 27.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3799.9965 | 61348.7666 | 27.75 | 100%
[5 empty] | 27.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3802.263 | 61385.3575 | 27.76 | 100%
[5 empty] | 27.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3804.5295 | 61421.9485 | 27.77 | 100%
[5 empty] | 27.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3806.7959 | 61458.5394 | 27.78 | 100%
[5 empty] | 27.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3809.0624 | 61495.1303 | 27.79 | 100%
[5 empty] | 27.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3811.3289 | 61531.7213 | 27.8 | 100%
[5 empty] | 27.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3813.5954 | 61568.3122 | 27.81 | 100%
[5 empty] | 27.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3815.8619 | 61604.9032 | 27.82 | 100%
[5 empty] | 27.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3818.1283 | 61641.4941 | 27.83 | 100%
[5 empty] | 27.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3820.3948 | 61678.0851 | 27.84 | 100%
[5 empty] | 27.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3822.6613 | 61714.676 | 27.85 | 100%
[5 empty] | 27.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3824.9278 | 61751.267 | 27.86 | 100%
[5 empty] | 27.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3827.1942 | 61787.8579 | 27.87 | 100%
[5 empty] | 27.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3829.4607 | 61824.4488 | 27.88 | 100%
[5 empty] | 27.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3831.7272 | 61861.0398 | 27.89 | 100%
[5 empty] | 27.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3833.9937 | 61897.6307 | 27.9 | 100%
[5 empty] | 27.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3836.2601 | 61934.2217 | 27.91 | 100%
[5 empty] | 27.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3838.5266 | 61970.8126 | 27.92 | 100%
[5 empty] | 27.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3840.7931 | 62007.4036 | 27.93 | 100%
[5 empty] | 27.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3843.0596 | 62043.9945 | 27.94 | 100%
[5 empty] | 27.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3845.326 | 62080.5854 | 27.95 | 100%
[5 empty] | 27.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3847.5925 | 62117.1764 | 27.96 | 100%
[5 empty] | 27.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3849.859 | 62153.7673 | 27.97 | 100%
[5 empty] | 27.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3852.1255 | 62190.3583 | 27.98 | 100%
[5 empty] | 27.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3854.3919 | 62226.9492 | 27.99 | 100%
[5 empty] | 28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3856.6584 | 62263.5402 | 28 | 100%
[5 empty] | 28.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3858.9249 | 62300.1311 | 28.01 | 100%
[5 empty] | 28.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3861.1914 | 62336.722 | 28.02 | 100%
[5 empty] | 28.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3863.4578 | 62373.313 | 28.03 | 100%
[5 empty] | 28.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3865.7243 | 62409.9039 | 28.04 | 100%
[5 empty] | 28.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3867.9908 | 62446.4949 | 28.05 | 100%
[5 empty] | 28.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3870.2573 | 62483.0858 | 28.06 | 100%
[5 empty] | 28.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3872.5237 | 62519.6768 | 28.07 | 100%
[5 empty] | 28.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3874.7902 | 62556.2677 | 28.08 | 100%
[5 empty] | 28.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3877.0567 | 62592.8587 | 28.09 | 100%
[5 empty] | 28.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3879.3232 | 62629.4496 | 28.1 | 100%
[5 empty] | 28.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3881.5896 | 62666.0405 | 28.11 | 100%
[5 empty] | 28.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3883.8561 | 62702.6315 | 28.12 | 100%
[5 empty] | 28.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3886.1226 | 62739.2224 | 28.13 | 100%
[5 empty] | 28.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3888.3891 | 62775.8134 | 28.14 | 100%
[5 empty] | 28.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3890.6555 | 62812.4043 | 28.15 | 100%
[5 empty] | 28.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3892.922 | 62848.9953 | 28.16 | 100%
[5 empty] | 28.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3895.1885 | 62885.5862 | 28.17 | 100%
[5 empty] | 28.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3897.455 | 62922.1771 | 28.18 | 100%
[5 empty] | 28.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3899.7214 | 62958.7681 | 28.19 | 100%
[5 empty] | 28.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3901.9879 | 62995.359 | 28.2 | 100%
[5 empty] | 28.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3904.2544 | 63031.95 | 28.21 | 100%
[5 empty] | 28.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3906.5209 | 63068.5409 | 28.22 | 100%
[5 empty] | 28.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3908.7873 | 63105.1319 | 28.23 | 100%
[5 empty] | 28.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3911.0538 | 63141.7228 | 28.24 | 100%
[5 empty] | 28.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3913.3203 | 63178.3138 | 28.25 | 100%
[5 empty] | 28.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3915.5868 | 63214.9047 | 28.26 | 100%
[5 empty] | 28.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3917.8532 | 63251.4956 | 28.27 | 100%
[5 empty] | 28.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3920.1197 | 63288.0866 | 28.28 | 100%
[5 empty] | 28.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3922.3862 | 63324.6775 | 28.29 | 100%
[5 empty] | 28.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3924.6527 | 63361.2685 | 28.3 | 100%
[5 empty] | 28.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3926.9191 | 63397.8594 | 28.31 | 100%
[5 empty] | 28.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3929.1856 | 63434.4504 | 28.32 | 100%
[5 empty] | 28.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3931.4521 | 63471.0413 | 28.33 | 100%
[5 empty] | 28.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3933.7186 | 63507.6322 | 28.34 | 100%
[5 empty] | 28.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3935.985 | 63544.2232 | 28.35 | 100%
[5 empty] | 28.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3938.2515 | 63580.8141 | 28.36 | 100%
[5 empty] | 28.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3940.518 | 63617.4051 | 28.37 | 100%
[5 empty] | 28.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3942.7845 | 63653.996 | 28.38 | 100%
[5 empty] | 28.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3945.0509 | 63690.587 | 28.39 | 100%
[5 empty] | 28.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3947.3174 | 63727.1779 | 28.4 | 100%
[5 empty] | 28.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3949.5839 | 63763.7688 | 28.41 | 100%
[5 empty] | 28.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3951.8504 | 63800.3598 | 28.42 | 100%
[5 empty] | 28.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3954.1168 | 63836.9507 | 28.43 | 100%
[5 empty] | 28.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3956.3833 | 63873.5417 | 28.44 | 100%
[5 empty] | 28.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3958.6498 | 63910.1326 | 28.45 | 100%
[5 empty] | 28.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3960.9163 | 63946.7236 | 28.46 | 100%
[5 empty] | 28.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3963.1827 | 63983.3145 | 28.47 | 100%
[5 empty] | 28.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3965.4492 | 64019.9055 | 28.48 | 100%
[5 empty] | 28.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3967.7157 | 64056.4964 | 28.49 | 100%
[5 empty] | 28.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3969.9822 | 64093.0873 | 28.5 | 100%
[5 empty] | 28.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3972.2486 | 64129.6783 | 28.51 | 100%
[5 empty] | 28.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3974.5151 | 64166.2692 | 28.52 | 100%
[5 empty] | 28.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3976.7816 | 64202.8602 | 28.53 | 100%
[5 empty] | 28.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3979.0481 | 64239.4511 | 28.54 | 100%
[5 empty] | 28.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3981.3145 | 64276.0421 | 28.55 | 100%
[5 empty] | 28.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3983.581 | 64312.633 | 28.56 | 100%
[5 empty] | 28.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3985.8475 | 64349.2239 | 28.57 | 100%
[5 empty] | 28.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3988.114 | 64385.8149 | 28.58 | 100%
[5 empty] | 28.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3990.3804 | 64422.4058 | 28.59 | 100%
[5 empty] | 28.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3992.6469 | 64458.9968 | 28.6 | 100%
[5 empty] | 28.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3994.9134 | 64495.5877 | 28.61 | 100%
[5 empty] | 28.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3997.1799 | 64532.1787 | 28.62 | 100%
[5 empty] | 28.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 3999.4463 | 64568.7696 | 28.63 | 100%
[5 empty] | 28.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4001.7128 | 64605.3606 | 28.64 | 100%
[5 empty] | 28.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4003.9793 | 64641.9515 | 28.65 | 100%
[5 empty] | 28.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4006.2458 | 64678.5424 | 28.66 | 100%
[5 empty] | 28.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4008.5122 | 64715.1334 | 28.67 | 100%
[5 empty] | 28.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4010.7787 | 64751.7243 | 28.68 | 100%
[5 empty] | 28.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4013.0452 | 64788.3153 | 28.69 | 100%
[5 empty] | 28.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4015.3117 | 64824.9062 | 28.7 | 100%
[5 empty] | 28.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4017.5781 | 64861.4972 | 28.71 | 100%
[5 empty] | 28.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4019.8446 | 64898.0881 | 28.72 | 100%
[5 empty] | 28.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4022.1111 | 64934.679 | 28.73 | 100%
[5 empty] | 28.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4024.3776 | 64971.27 | 28.74 | 100%
[5 empty] | 28.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4026.644 | 65007.8609 | 28.75 | 100%
[5 empty] | 28.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4028.9105 | 65044.4519 | 28.76 | 100%
[5 empty] | 28.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4031.177 | 65081.0428 | 28.77 | 100%
[5 empty] | 28.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4033.4435 | 65117.6338 | 28.78 | 100%
[5 empty] | 28.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4035.7099 | 65154.2247 | 28.79 | 100%
[5 empty] | 28.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4037.9764 | 65190.8157 | 28.8 | 100%
[5 empty] | 28.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4040.2429 | 65227.4066 | 28.81 | 100%
[5 empty] | 28.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4042.5094 | 65263.9975 | 28.82 | 100%
[5 empty] | 28.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4044.7758 | 65300.5885 | 28.83 | 100%
[5 empty] | 28.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4047.0423 | 65337.1794 | 28.84 | 100%
[5 empty] | 28.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4049.3088 | 65373.7704 | 28.85 | 100%
[5 empty] | 28.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4051.5753 | 65410.3613 | 28.86 | 100%
[5 empty] | 28.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4053.8417 | 65446.9523 | 28.87 | 100%
[5 empty] | 28.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4056.1082 | 65483.5432 | 28.88 | 100%
[5 empty] | 28.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4058.3747 | 65520.1341 | 28.89 | 100%
[5 empty] | 28.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4060.6412 | 65556.7251 | 28.9 | 100%
[5 empty] | 28.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4062.9076 | 65593.316 | 28.91 | 100%
[5 empty] | 28.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4065.1741 | 65629.907 | 28.92 | 100%
[5 empty] | 28.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4067.4406 | 65666.4979 | 28.93 | 100%
[5 empty] | 28.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4069.7071 | 65703.0889 | 28.94 | 100%
[5 empty] | 28.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4071.9735 | 65739.6798 | 28.95 | 100%
[5 empty] | 28.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4074.24 | 65776.2707 | 28.96 | 100%
[5 empty] | 28.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4076.5065 | 65812.8617 | 28.97 | 100%
[5 empty] | 28.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4078.773 | 65849.4526 | 28.98 | 100%
[5 empty] | 28.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4081.0394 | 65886.0436 | 28.99 | 100%
[5 empty] | 29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4083.3059 | 65922.6345 | 29 | 100%
[5 empty] | 29.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4085.5724 | 65959.2255 | 29.01 | 100%
[5 empty] | 29.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4087.8389 | 65995.8164 | 29.02 | 100%
[5 empty] | 29.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4090.1054 | 66032.4074 | 29.03 | 100%
[5 empty] | 29.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4092.3718 | 66068.9983 | 29.04 | 100%
[5 empty] | 29.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4094.6383 | 66105.5892 | 29.05 | 100%
[5 empty] | 29.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4096.9048 | 66142.1802 | 29.06 | 100%
[5 empty] | 29.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4099.1713 | 66178.7711 | 29.07 | 100%
[5 empty] | 29.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4101.4377 | 66215.3621 | 29.08 | 100%
[5 empty] | 29.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4103.7042 | 66251.953 | 29.09 | 100%
[5 empty] | 29.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4105.9707 | 66288.544 | 29.1 | 100%
[5 empty] | 29.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4108.2372 | 66325.1349 | 29.11 | 100%
[5 empty] | 29.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4110.5036 | 66361.7258 | 29.12 | 100%
[5 empty] | 29.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4112.7701 | 66398.3168 | 29.13 | 100%
[5 empty] | 29.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4115.0366 | 66434.9077 | 29.14 | 100%
[5 empty] | 29.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4117.3031 | 66471.4987 | 29.15 | 100%
[5 empty] | 29.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4119.5695 | 66508.0896 | 29.16 | 100%
[5 empty] | 29.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4121.836 | 66544.6806 | 29.17 | 100%
[5 empty] | 29.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4124.1025 | 66581.2715 | 29.18 | 100%
[5 empty] | 29.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4126.369 | 66617.8625 | 29.19 | 100%
[5 empty] | 29.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4128.6354 | 66654.4534 | 29.2 | 100%
[5 empty] | 29.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4130.9019 | 66691.0443 | 29.21 | 100%
[5 empty] | 29.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4133.1684 | 66727.6353 | 29.22 | 100%
[5 empty] | 29.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4135.4349 | 66764.2262 | 29.23 | 100%
[5 empty] | 29.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4137.7013 | 66800.8172 | 29.24 | 100%
[5 empty] | 29.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4139.9678 | 66837.4081 | 29.25 | 100%
[5 empty] | 29.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4142.2343 | 66873.9991 | 29.26 | 100%
[5 empty] | 29.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4144.5008 | 66910.59 | 29.27 | 100%
[5 empty] | 29.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4146.7672 | 66947.1809 | 29.28 | 100%
[5 empty] | 29.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4149.0337 | 66983.7719 | 29.29 | 100%
[5 empty] | 29.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4151.3002 | 67020.3628 | 29.3 | 100%
[5 empty] | 29.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4153.5667 | 67056.9538 | 29.31 | 100%
[5 empty] | 29.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4155.8331 | 67093.5447 | 29.32 | 100%
[5 empty] | 29.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4158.0996 | 67130.1357 | 29.33 | 100%
[5 empty] | 29.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4160.3661 | 67166.7266 | 29.34 | 100%
[5 empty] | 29.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4162.6326 | 67203.3176 | 29.35 | 100%
[5 empty] | 29.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4164.899 | 67239.9085 | 29.36 | 100%
[5 empty] | 29.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4167.1655 | 67276.4994 | 29.37 | 100%
[5 empty] | 29.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4169.432 | 67313.0904 | 29.38 | 100%
[5 empty] | 29.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4171.6985 | 67349.6813 | 29.39 | 100%
[5 empty] | 29.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4173.9649 | 67386.2723 | 29.4 | 100%
[5 empty] | 29.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4176.2314 | 67422.8632 | 29.41 | 100%
[5 empty] | 29.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4178.4979 | 67459.4542 | 29.42 | 100%
[5 empty] | 29.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4180.7644 | 67496.0451 | 29.43 | 100%
[5 empty] | 29.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4183.0308 | 67532.636 | 29.44 | 100%
[5 empty] | 29.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4185.2973 | 67569.227 | 29.45 | 100%
[5 empty] | 29.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4187.5638 | 67605.8179 | 29.46 | 100%
[5 empty] | 29.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4189.8303 | 67642.4089 | 29.47 | 100%
[5 empty] | 29.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4192.0967 | 67678.9998 | 29.48 | 100%
[5 empty] | 29.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4194.3632 | 67715.5908 | 29.49 | 100%
[5 empty] | 29.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4196.6297 | 67752.1817 | 29.5 | 100%
[5 empty] | 29.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4198.8962 | 67788.7726 | 29.51 | 100%
[5 empty] | 29.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4201.1626 | 67825.3636 | 29.52 | 100%
[5 empty] | 29.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4203.4291 | 67861.9545 | 29.53 | 100%
[5 empty] | 29.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4205.6956 | 67898.5455 | 29.54 | 100%
[5 empty] | 29.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4207.9621 | 67935.1364 | 29.55 | 100%
[5 empty] | 29.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4210.2285 | 67971.7274 | 29.56 | 100%
[5 empty] | 29.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4212.495 | 68008.3183 | 29.57 | 100%
[5 empty] | 29.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4214.7615 | 68044.9093 | 29.58 | 100%
[5 empty] | 29.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4217.028 | 68081.5002 | 29.59 | 100%
[5 empty] | 29.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4219.2944 | 68118.0911 | 29.6 | 100%
[5 empty] | 29.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4221.5609 | 68154.6821 | 29.61 | 100%
[5 empty] | 29.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4223.8274 | 68191.273 | 29.62 | 100%
[5 empty] | 29.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4226.0939 | 68227.864 | 29.63 | 100%
[5 empty] | 29.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4228.3603 | 68264.4549 | 29.64 | 100%
[5 empty] | 29.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4230.6268 | 68301.0459 | 29.65 | 100%
[5 empty] | 29.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4232.8933 | 68337.6368 | 29.66 | 100%
[5 empty] | 29.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4235.1598 | 68374.2277 | 29.67 | 100%
[5 empty] | 29.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4237.4262 | 68410.8187 | 29.68 | 100%
[5 empty] | 29.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4239.6927 | 68447.4096 | 29.69 | 100%
[5 empty] | 29.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4241.9592 | 68484.0006 | 29.7 | 100%
[5 empty] | 29.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4244.2257 | 68520.5915 | 29.71 | 100%
[5 empty] | 29.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4246.4921 | 68557.1825 | 29.72 | 100%
[5 empty] | 29.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4248.7586 | 68593.7734 | 29.73 | 100%
[5 empty] | 29.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4251.0251 | 68630.3644 | 29.74 | 100%
[5 empty] | 29.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4253.2916 | 68666.9553 | 29.75 | 100%
[5 empty] | 29.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4255.558 | 68703.5462 | 29.76 | 100%
[5 empty] | 29.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4257.8245 | 68740.1372 | 29.77 | 100%
[5 empty] | 29.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4260.091 | 68776.7281 | 29.78 | 100%
[5 empty] | 29.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4262.3575 | 68813.3191 | 29.79 | 100%
[5 empty] | 29.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4264.6239 | 68849.91 | 29.8 | 100%
[5 empty] | 29.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4266.8904 | 68886.501 | 29.81 | 100%
[5 empty] | 29.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4269.1569 | 68923.0919 | 29.82 | 100%
[5 empty] | 29.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4271.4234 | 68959.6828 | 29.83 | 100%
[5 empty] | 29.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4273.6898 | 68996.2738 | 29.84 | 100%
[5 empty] | 29.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4275.9563 | 69032.8647 | 29.85 | 100%
[5 empty] | 29.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4278.2228 | 69069.4557 | 29.86 | 100%
[5 empty] | 29.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4280.4893 | 69106.0466 | 29.87 | 100%
[5 empty] | 29.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4282.7557 | 69142.6376 | 29.88 | 100%
[5 empty] | 29.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4285.0222 | 69179.2285 | 29.89 | 100%
[5 empty] | 29.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4287.2887 | 69215.8195 | 29.9 | 100%
[5 empty] | 29.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4289.5552 | 69252.4104 | 29.91 | 100%
[5 empty] | 29.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4291.8216 | 69289.0013 | 29.92 | 100%
[5 empty] | 29.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4294.0881 | 69325.5923 | 29.93 | 100%
[5 empty] | 29.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4296.3546 | 69362.1832 | 29.94 | 100%
[5 empty] | 29.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4298.6211 | 69398.7742 | 29.95 | 100%
[5 empty] | 29.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4300.8875 | 69435.3651 | 29.96 | 100%
[5 empty] | 29.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4303.154 | 69471.9561 | 29.97 | 100%
[5 empty] | 29.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4305.4205 | 69508.547 | 29.98 | 100%
[5 empty] | 29.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4307.687 | 69545.1379 | 29.99 | 100%
[5 empty] | 30 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4309.9534 | 69581.7289 | 30 | 100%
[5 empty] | 30.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4312.2199 | 69618.3198 | 30.01 | 100%
[5 empty] | 30.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4314.4864 | 69654.9108 | 30.02 | 100%
[5 empty] | 30.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4316.7529 | 69691.5017 | 30.03 | 100%
[5 empty] | 30.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4319.0193 | 69728.0927 | 30.04 | 100%
[5 empty] | 30.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4321.2858 | 69764.6836 | 30.05 | 100%
[5 empty] | 30.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4323.5523 | 69801.2745 | 30.06 | 100%
[5 empty] | 30.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4325.8188 | 69837.8655 | 30.07 | 100%
[5 empty] | 30.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4328.0852 | 69874.4564 | 30.08 | 100%
[5 empty] | 30.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4330.3517 | 69911.0474 | 30.09 | 100%
[5 empty] | 30.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4332.6182 | 69947.6383 | 30.1 | 100%
[5 empty] | 30.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4334.8847 | 69984.2293 | 30.11 | 100%
[5 empty] | 30.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4337.1511 | 70020.8202 | 30.12 | 100%
[5 empty] | 30.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4339.4176 | 70057.4112 | 30.13 | 100%
[5 empty] | 30.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4341.6841 | 70094.0021 | 30.14 | 100%
[5 empty] | 30.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4343.9506 | 70130.593 | 30.15 | 100%
[5 empty] | 30.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4346.217 | 70167.184 | 30.16 | 100%
[5 empty] | 30.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4348.4835 | 70203.7749 | 30.17 | 100%
[5 empty] | 30.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4350.75 | 70240.3659 | 30.18 | 100%
[5 empty] | 30.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4353.0165 | 70276.9568 | 30.19 | 100%
[5 empty] | 30.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4355.2829 | 70313.5478 | 30.2 | 100%
[5 empty] | 30.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4357.5494 | 70350.1387 | 30.21 | 100%
[5 empty] | 30.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4359.8159 | 70386.7296 | 30.22 | 100%
[5 empty] | 30.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4362.0824 | 70423.3206 | 30.23 | 100%
[5 empty] | 30.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4364.3489 | 70459.9115 | 30.24 | 100%
[5 empty] | 30.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4366.6153 | 70496.5025 | 30.25 | 100%
[5 empty] | 30.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4368.8818 | 70533.0934 | 30.26 | 100%
[5 empty] | 30.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4371.1483 | 70569.6844 | 30.27 | 100%
[5 empty] | 30.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4373.4148 | 70606.2753 | 30.28 | 100%
[5 empty] | 30.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4375.6812 | 70642.8663 | 30.29 | 100%
[5 empty] | 30.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4377.9477 | 70679.4572 | 30.3 | 100%
[5 empty] | 30.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4380.2142 | 70716.0481 | 30.31 | 100%
[5 empty] | 30.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4382.4807 | 70752.6391 | 30.32 | 100%
[5 empty] | 30.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4384.7471 | 70789.23 | 30.33 | 100%
[5 empty] | 30.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4387.0136 | 70825.821 | 30.34 | 100%
[5 empty] | 30.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4389.2801 | 70862.4119 | 30.35 | 100%
[5 empty] | 30.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4391.5466 | 70899.0029 | 30.36 | 100%
[5 empty] | 30.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4393.813 | 70935.5938 | 30.37 | 100%
[5 empty] | 30.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4396.0795 | 70972.1847 | 30.38 | 100%
[5 empty] | 30.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4398.346 | 71008.7757 | 30.39 | 100%
[5 empty] | 30.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4400.6125 | 71045.3666 | 30.4 | 100%
[5 empty] | 30.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4402.8789 | 71081.9576 | 30.41 | 100%
[5 empty] | 30.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4405.1454 | 71118.5485 | 30.42 | 100%
[5 empty] | 30.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4407.4119 | 71155.1395 | 30.43 | 100%
[5 empty] | 30.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4409.6784 | 71191.7304 | 30.44 | 100%
[5 empty] | 30.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4411.9448 | 71228.3213 | 30.45 | 100%
[5 empty] | 30.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4414.2113 | 71264.9123 | 30.46 | 100%
[5 empty] | 30.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4416.4778 | 71301.5032 | 30.47 | 100%
[5 empty] | 30.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4418.7443 | 71338.0942 | 30.48 | 100%
[5 empty] | 30.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4421.0107 | 71374.6851 | 30.49 | 100%
[5 empty] | 30.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4423.2772 | 71411.2761 | 30.5 | 100%
[5 empty] | 30.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4425.5437 | 71447.867 | 30.51 | 100%
[5 empty] | 30.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4427.8102 | 71484.458 | 30.52 | 100%
[5 empty] | 30.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4430.0766 | 71521.0489 | 30.53 | 100%
[5 empty] | 30.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4432.3431 | 71557.6398 | 30.54 | 100%
[5 empty] | 30.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4434.6096 | 71594.2308 | 30.55 | 100%
[5 empty] | 30.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4436.8761 | 71630.8217 | 30.56 | 100%
[5 empty] | 30.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4439.1425 | 71667.4127 | 30.57 | 100%
[5 empty] | 30.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4441.409 | 71704.0036 | 30.58 | 100%
[5 empty] | 30.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4443.6755 | 71740.5946 | 30.59 | 100%
[5 empty] | 30.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4445.942 | 71777.1855 | 30.6 | 100%
[5 empty] | 30.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4448.2084 | 71813.7764 | 30.61 | 100%
[5 empty] | 30.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4450.4749 | 71850.3674 | 30.62 | 100%
[5 empty] | 30.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4452.7414 | 71886.9583 | 30.63 | 100%
[5 empty] | 30.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4455.0079 | 71923.5493 | 30.64 | 100%
[5 empty] | 30.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4457.2743 | 71960.1402 | 30.65 | 100%
[5 empty] | 30.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4459.5408 | 71996.7312 | 30.66 | 100%
[5 empty] | 30.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4461.8073 | 72033.3221 | 30.67 | 100%
[5 empty] | 30.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4464.0738 | 72069.9131 | 30.68 | 100%
[5 empty] | 30.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4466.3402 | 72106.504 | 30.69 | 100%
[5 empty] | 30.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4468.6067 | 72143.0949 | 30.7 | 100%
[5 empty] | 30.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4470.8732 | 72179.6859 | 30.71 | 100%
[5 empty] | 30.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4473.1397 | 72216.2768 | 30.72 | 100%
[5 empty] | 30.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4475.4061 | 72252.8678 | 30.73 | 100%
[5 empty] | 30.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4477.6726 | 72289.4587 | 30.74 | 100%
[5 empty] | 30.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4479.9391 | 72326.0497 | 30.75 | 100%
[5 empty] | 30.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4482.2056 | 72362.6406 | 30.76 | 100%
[5 empty] | 30.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4484.472 | 72399.2315 | 30.77 | 100%
[5 empty] | 30.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4486.7385 | 72435.8225 | 30.78 | 100%
[5 empty] | 30.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4489.005 | 72472.4134 | 30.79 | 100%
[5 empty] | 30.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4491.2715 | 72509.0044 | 30.8 | 100%
[5 empty] | 30.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4493.5379 | 72545.5953 | 30.81 | 100%
[5 empty] | 30.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4495.8044 | 72582.1863 | 30.82 | 100%
[5 empty] | 30.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4498.0709 | 72618.7772 | 30.83 | 100%
[5 empty] | 30.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4500.3374 | 72655.3682 | 30.84 | 100%
[5 empty] | 30.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4502.6038 | 72691.9591 | 30.85 | 100%
[5 empty] | 30.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4504.8703 | 72728.55 | 30.86 | 100%
[5 empty] | 30.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4507.1368 | 72765.141 | 30.87 | 100%
[5 empty] | 30.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4509.4033 | 72801.7319 | 30.88 | 100%
[5 empty] | 30.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4511.6697 | 72838.3229 | 30.89 | 100%
[5 empty] | 30.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4513.9362 | 72874.9138 | 30.9 | 100%
[5 empty] | 30.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4516.2027 | 72911.5048 | 30.91 | 100%
[5 empty] | 30.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4518.4692 | 72948.0957 | 30.92 | 100%
[5 empty] | 30.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4520.7356 | 72984.6866 | 30.93 | 100%
[5 empty] | 30.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4523.0021 | 73021.2776 | 30.94 | 100%
[5 empty] | 30.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4525.2686 | 73057.8685 | 30.95 | 100%
[5 empty] | 30.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4527.5351 | 73094.4595 | 30.96 | 100%
[5 empty] | 30.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4529.8015 | 73131.0504 | 30.97 | 100%
[5 empty] | 30.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4532.068 | 73167.6414 | 30.98 | 100%
[5 empty] | 30.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4534.3345 | 73204.2323 | 30.99 | 100%
[5 empty] | 31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4536.601 | 73240.8232 | 31 | 100%
[5 empty] | 31.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4538.8674 | 73277.4142 | 31.01 | 100%
[5 empty] | 31.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4541.1339 | 73314.0051 | 31.02 | 100%
[5 empty] | 31.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4543.4004 | 73350.5961 | 31.03 | 100%
[5 empty] | 31.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4545.6669 | 73387.187 | 31.04 | 100%
[5 empty] | 31.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4547.9333 | 73423.778 | 31.05 | 100%
[5 empty] | 31.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4550.1998 | 73460.3689 | 31.06 | 100%
[5 empty] | 31.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4552.4663 | 73496.9599 | 31.07 | 100%
[5 empty] | 31.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4554.7328 | 73533.5508 | 31.08 | 100%
[5 empty] | 31.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4556.9992 | 73570.1417 | 31.09 | 100%
[5 empty] | 31.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4559.2657 | 73606.7327 | 31.1 | 100%
[5 empty] | 31.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4561.5322 | 73643.3236 | 31.11 | 100%
[5 empty] | 31.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4563.7987 | 73679.9146 | 31.12 | 100%
[5 empty] | 31.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4566.0651 | 73716.5055 | 31.13 | 100%
[5 empty] | 31.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4568.3316 | 73753.0965 | 31.14 | 100%
[5 empty] | 31.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4570.5981 | 73789.6874 | 31.15 | 100%
[5 empty] | 31.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4572.8646 | 73826.2783 | 31.16 | 100%
[5 empty] | 31.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4575.131 | 73862.8693 | 31.17 | 100%
[5 empty] | 31.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4577.3975 | 73899.4602 | 31.18 | 100%
[5 empty] | 31.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4579.664 | 73936.0512 | 31.19 | 100%
[5 empty] | 31.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4581.9305 | 73972.6421 | 31.2 | 100%
[5 empty] | 31.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4584.1969 | 74009.2331 | 31.21 | 100%
[5 empty] | 31.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4586.4634 | 74045.824 | 31.22 | 100%
[5 empty] | 31.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4588.7299 | 74082.415 | 31.23 | 100%
[5 empty] | 31.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4590.9964 | 74119.0059 | 31.24 | 100%
[5 empty] | 31.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4593.2628 | 74155.5968 | 31.25 | 100%
[5 empty] | 31.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4595.5293 | 74192.1878 | 31.26 | 100%
[5 empty] | 31.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4597.7958 | 74228.7787 | 31.27 | 100%
[5 empty] | 31.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4600.0623 | 74265.3697 | 31.28 | 100%
[5 empty] | 31.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4602.3287 | 74301.9606 | 31.29 | 100%
[5 empty] | 31.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4604.5952 | 74338.5516 | 31.3 | 100%
[5 empty] | 31.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4606.8617 | 74375.1425 | 31.31 | 100%
[5 empty] | 31.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4609.1282 | 74411.7334 | 31.32 | 100%
[5 empty] | 31.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4611.3946 | 74448.3244 | 31.33 | 100%
[5 empty] | 31.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4613.6611 | 74484.9153 | 31.34 | 100%
[5 empty] | 31.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4615.9276 | 74521.5063 | 31.35 | 100%
[5 empty] | 31.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4618.1941 | 74558.0972 | 31.36 | 100%
[5 empty] | 31.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4620.4605 | 74594.6882 | 31.37 | 100%
[5 empty] | 31.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4622.727 | 74631.2791 | 31.38 | 100%
[5 empty] | 31.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4624.9935 | 74667.8701 | 31.39 | 100%
[5 empty] | 31.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4627.26 | 74704.461 | 31.4 | 100%
[5 empty] | 31.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4629.5265 | 74741.0519 | 31.41 | 100%
[5 empty] | 31.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4631.7929 | 74777.6429 | 31.42 | 100%
[5 empty] | 31.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4634.0594 | 74814.2338 | 31.43 | 100%
[5 empty] | 31.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4636.3259 | 74850.8248 | 31.44 | 100%
[5 empty] | 31.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4638.5924 | 74887.4157 | 31.45 | 100%
[5 empty] | 31.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4640.8588 | 74924.0067 | 31.46 | 100%
[5 empty] | 31.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4643.1253 | 74960.5976 | 31.47 | 100%
[5 empty] | 31.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4645.3918 | 74997.1885 | 31.48 | 100%
[5 empty] | 31.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4647.6583 | 75033.7795 | 31.49 | 100%
[5 empty] | 31.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4649.9247 | 75070.3704 | 31.5 | 100%
[5 empty] | 31.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4652.1912 | 75106.9614 | 31.51 | 100%
[5 empty] | 31.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4654.4577 | 75143.5523 | 31.52 | 100%
[5 empty] | 31.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4656.7242 | 75180.1433 | 31.53 | 100%
[5 empty] | 31.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4658.9906 | 75216.7342 | 31.54 | 100%
[5 empty] | 31.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4661.2571 | 75253.3251 | 31.55 | 100%
[5 empty] | 31.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4663.5236 | 75289.9161 | 31.56 | 100%
[5 empty] | 31.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4665.7901 | 75326.507 | 31.57 | 100%
[5 empty] | 31.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4668.0565 | 75363.098 | 31.58 | 100%
[5 empty] | 31.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4670.323 | 75399.6889 | 31.59 | 100%
[5 empty] | 31.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4672.5895 | 75436.2799 | 31.6 | 100%
[5 empty] | 31.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4674.856 | 75472.8708 | 31.61 | 100%
[5 empty] | 31.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4677.1224 | 75509.4618 | 31.62 | 100%
[5 empty] | 31.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4679.3889 | 75546.0527 | 31.63 | 100%
[5 empty] | 31.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4681.6554 | 75582.6436 | 31.64 | 100%
[5 empty] | 31.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4683.9219 | 75619.2346 | 31.65 | 100%
[5 empty] | 31.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4686.1883 | 75655.8255 | 31.66 | 100%
[5 empty] | 31.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4688.4548 | 75692.4165 | 31.67 | 100%
[5 empty] | 31.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4690.7213 | 75729.0074 | 31.68 | 100%
[5 empty] | 31.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4692.9878 | 75765.5984 | 31.69 | 100%
[5 empty] | 31.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4695.2542 | 75802.1893 | 31.7 | 100%
[5 empty] | 31.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4697.5207 | 75838.7802 | 31.71 | 100%
[5 empty] | 31.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4699.7872 | 75875.3712 | 31.72 | 100%
[5 empty] | 31.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4702.0537 | 75911.9621 | 31.73 | 100%
[5 empty] | 31.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4704.3201 | 75948.5531 | 31.74 | 100%
[5 empty] | 31.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4706.5866 | 75985.144 | 31.75 | 100%
[5 empty] | 31.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4708.8531 | 76021.735 | 31.76 | 100%
[5 empty] | 31.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4711.1196 | 76058.3259 | 31.77 | 100%
[5 empty] | 31.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4713.386 | 76094.9169 | 31.78 | 100%
[5 empty] | 31.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4715.6525 | 76131.5078 | 31.79 | 100%
[5 empty] | 31.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4717.919 | 76168.0987 | 31.8 | 100%
[5 empty] | 31.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4720.1855 | 76204.6897 | 31.81 | 100%
[5 empty] | 31.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4722.4519 | 76241.2806 | 31.82 | 100%
[5 empty] | 31.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4724.7184 | 76277.8716 | 31.83 | 100%
[5 empty] | 31.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4726.9849 | 76314.4625 | 31.84 | 100%
[5 empty] | 31.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4729.2514 | 76351.0535 | 31.85 | 100%
[5 empty] | 31.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4731.5178 | 76387.6444 | 31.86 | 100%
[5 empty] | 31.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4733.7843 | 76424.2353 | 31.87 | 100%
[5 empty] | 31.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4736.0508 | 76460.8263 | 31.88 | 100%
[5 empty] | 31.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4738.3173 | 76497.4172 | 31.89 | 100%
[5 empty] | 31.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4740.5837 | 76534.0082 | 31.9 | 100%
[5 empty] | 31.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4742.8502 | 76570.5991 | 31.91 | 100%
[5 empty] | 31.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4745.1167 | 76607.1901 | 31.92 | 100%
[5 empty] | 31.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4747.3832 | 76643.781 | 31.93 | 100%
[5 empty] | 31.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4749.6496 | 76680.3719 | 31.94 | 100%
[5 empty] | 31.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4751.9161 | 76716.9629 | 31.95 | 100%
[5 empty] | 31.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4754.1826 | 76753.5538 | 31.96 | 100%
[5 empty] | 31.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4756.4491 | 76790.1448 | 31.97 | 100%
[5 empty] | 31.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4758.7155 | 76826.7357 | 31.98 | 100%
[5 empty] | 31.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4760.982 | 76863.3267 | 31.99 | 100%
[5 empty] | 32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4763.2485 | 76899.9176 | 32 | 100%
[5 empty] | 32.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4765.515 | 76936.5086 | 32.01 | 100%
[5 empty] | 32.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4767.7814 | 76973.0995 | 32.02 | 100%
[5 empty] | 32.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4770.0479 | 77009.6904 | 32.03 | 100%
[5 empty] | 32.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4772.3144 | 77046.2814 | 32.04 | 100%
[5 empty] | 32.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4774.5809 | 77082.8723 | 32.05 | 100%
[5 empty] | 32.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4776.8473 | 77119.4633 | 32.06 | 100%
[5 empty] | 32.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4779.1138 | 77156.0542 | 32.07 | 100%
[5 empty] | 32.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4781.3803 | 77192.6452 | 32.08 | 100%
[5 empty] | 32.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4783.6468 | 77229.2361 | 32.09 | 100%
[5 empty] | 32.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4785.9132 | 77265.827 | 32.1 | 100%
[5 empty] | 32.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4788.1797 | 77302.418 | 32.11 | 100%
[5 empty] | 32.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4790.4462 | 77339.0089 | 32.12 | 100%
[5 empty] | 32.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4792.7127 | 77375.5999 | 32.13 | 100%
[5 empty] | 32.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4794.9791 | 77412.1908 | 32.14 | 100%
[5 empty] | 32.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4797.2456 | 77448.7818 | 32.15 | 100%
[5 empty] | 32.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4799.5121 | 77485.3727 | 32.16 | 100%
[5 empty] | 32.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4801.7786 | 77521.9637 | 32.17 | 100%
[5 empty] | 32.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4804.045 | 77558.5546 | 32.18 | 100%
[5 empty] | 32.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4806.3115 | 77595.1455 | 32.19 | 100%
[5 empty] | 32.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4808.578 | 77631.7365 | 32.2 | 100%
[5 empty] | 32.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4810.8445 | 77668.3274 | 32.21 | 100%
[5 empty] | 32.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4813.1109 | 77704.9184 | 32.22 | 100%
[5 empty] | 32.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4815.3774 | 77741.5093 | 32.23 | 100%
[5 empty] | 32.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4817.6439 | 77778.1003 | 32.24 | 100%
[5 empty] | 32.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4819.9104 | 77814.6912 | 32.25 | 100%
[5 empty] | 32.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4822.1768 | 77851.2821 | 32.26 | 100%
[5 empty] | 32.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4824.4433 | 77887.8731 | 32.27 | 100%
[5 empty] | 32.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4826.7098 | 77924.464 | 32.28 | 100%
[5 empty] | 32.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4828.9763 | 77961.055 | 32.29 | 100%
[5 empty] | 32.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4831.2427 | 77997.6459 | 32.3 | 100%
[5 empty] | 32.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4833.5092 | 78034.2369 | 32.31 | 100%
[5 empty] | 32.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4835.7757 | 78070.8278 | 32.32 | 100%
[5 empty] | 32.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4838.0422 | 78107.4188 | 32.33 | 100%
[5 empty] | 32.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4840.3086 | 78144.0097 | 32.34 | 100%
[5 empty] | 32.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4842.5751 | 78180.6006 | 32.35 | 100%
[5 empty] | 32.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4844.8416 | 78217.1916 | 32.36 | 100%
[5 empty] | 32.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4847.1081 | 78253.7825 | 32.37 | 100%
[5 empty] | 32.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4849.3745 | 78290.3735 | 32.38 | 100%
[5 empty] | 32.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4851.641 | 78326.9644 | 32.39 | 100%
[5 empty] | 32.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4853.9075 | 78363.5554 | 32.4 | 100%
[5 empty] | 32.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4856.174 | 78400.1463 | 32.41 | 100%
[5 empty] | 32.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4858.4404 | 78436.7372 | 32.42 | 100%
[5 empty] | 32.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4860.7069 | 78473.3282 | 32.43 | 100%
[5 empty] | 32.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4862.9734 | 78509.9191 | 32.44 | 100%
[5 empty] | 32.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4865.2399 | 78546.5101 | 32.45 | 100%
[5 empty] | 32.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4867.5063 | 78583.101 | 32.46 | 100%
[5 empty] | 32.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4869.7728 | 78619.692 | 32.47 | 100%
[5 empty] | 32.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4872.0393 | 78656.2829 | 32.48 | 100%
[5 empty] | 32.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4874.3058 | 78692.8738 | 32.49 | 100%
[5 empty] | 32.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4876.5722 | 78729.4648 | 32.5 | 100%
[5 empty] | 32.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4878.8387 | 78766.0557 | 32.51 | 100%
[5 empty] | 32.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4881.1052 | 78802.6467 | 32.52 | 100%
[5 empty] | 32.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4883.3717 | 78839.2376 | 32.53 | 100%
[5 empty] | 32.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4885.6381 | 78875.8286 | 32.54 | 100%
[5 empty] | 32.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4887.9046 | 78912.4195 | 32.55 | 100%
[5 empty] | 32.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4890.1711 | 78949.0105 | 32.56 | 100%
[5 empty] | 32.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4892.4376 | 78985.6014 | 32.57 | 100%
[5 empty] | 32.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4894.704 | 79022.1923 | 32.58 | 100%
[5 empty] | 32.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4896.9705 | 79058.7833 | 32.59 | 100%
[5 empty] | 32.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4899.237 | 79095.3742 | 32.6 | 100%
[5 empty] | 32.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4901.5035 | 79131.9652 | 32.61 | 100%
[5 empty] | 32.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4903.77 | 79168.5561 | 32.62 | 100%
[5 empty] | 32.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4906.0364 | 79205.1471 | 32.63 | 100%
[5 empty] | 32.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4908.3029 | 79241.738 | 32.64 | 100%
[5 empty] | 32.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4910.5694 | 79278.3289 | 32.65 | 100%
[5 empty] | 32.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4912.8359 | 79314.9199 | 32.66 | 100%
[5 empty] | 32.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4915.1023 | 79351.5108 | 32.67 | 100%
[5 empty] | 32.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4917.3688 | 79388.1018 | 32.68 | 100%
[5 empty] | 32.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4919.6353 | 79424.6927 | 32.69 | 100%
[5 empty] | 32.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4921.9018 | 79461.2837 | 32.7 | 100%
[5 empty] | 32.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4924.1682 | 79497.8746 | 32.71 | 100%
[5 empty] | 32.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4926.4347 | 79534.4656 | 32.72 | 100%
[5 empty] | 32.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4928.7012 | 79571.0565 | 32.73 | 100%
[5 empty] | 32.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4930.9677 | 79607.6474 | 32.74 | 100%
[5 empty] | 32.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4933.2341 | 79644.2384 | 32.75 | 100%
[5 empty] | 32.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4935.5006 | 79680.8293 | 32.76 | 100%
[5 empty] | 32.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4937.7671 | 79717.4203 | 32.77 | 100%
[5 empty] | 32.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4940.0336 | 79754.0112 | 32.78 | 100%
[5 empty] | 32.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4942.3 | 79790.6022 | 32.79 | 100%
[5 empty] | 32.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4944.5665 | 79827.1931 | 32.8 | 100%
[5 empty] | 32.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4946.833 | 79863.784 | 32.81 | 100%
[5 empty] | 32.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4949.0995 | 79900.375 | 32.82 | 100%
[5 empty] | 32.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4951.3659 | 79936.9659 | 32.83 | 100%
[5 empty] | 32.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4953.6324 | 79973.5569 | 32.84 | 100%
[5 empty] | 32.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4955.8989 | 80010.1478 | 32.85 | 100%
[5 empty] | 32.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4958.1654 | 80046.7388 | 32.86 | 100%
[5 empty] | 32.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4960.4318 | 80083.3297 | 32.87 | 100%
[5 empty] | 32.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4962.6983 | 80119.9207 | 32.88 | 100%
[5 empty] | 32.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4964.9648 | 80156.5116 | 32.89 | 100%
[5 empty] | 32.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4967.2313 | 80193.1025 | 32.9 | 100%
[5 empty] | 32.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4969.4977 | 80229.6935 | 32.91 | 100%
[5 empty] | 32.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4971.7642 | 80266.2844 | 32.92 | 100%
[5 empty] | 32.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4974.0307 | 80302.8754 | 32.93 | 100%
[5 empty] | 32.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4976.2972 | 80339.4663 | 32.94 | 100%
[5 empty] | 32.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4978.5636 | 80376.0573 | 32.95 | 100%
[5 empty] | 32.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4980.8301 | 80412.6482 | 32.96 | 100%
[5 empty] | 32.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4983.0966 | 80449.2391 | 32.97 | 100%
[5 empty] | 32.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4985.3631 | 80485.8301 | 32.98 | 100%
[5 empty] | 32.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4987.6295 | 80522.421 | 32.99 | 100%
[5 empty] | 33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4989.896 | 80559.012 | 33 | 100%
[5 empty] | 33.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4992.1625 | 80595.6029 | 33.01 | 100%
[5 empty] | 33.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4994.429 | 80632.1939 | 33.02 | 100%
[5 empty] | 33.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4996.6954 | 80668.7848 | 33.03 | 100%
[5 empty] | 33.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 4998.9619 | 80705.3757 | 33.04 | 100%
[5 empty] | 33.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5001.2284 | 80741.9667 | 33.05 | 100%
[5 empty] | 33.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5003.4949 | 80778.5576 | 33.06 | 100%
[5 empty] | 33.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5005.7613 | 80815.1486 | 33.07 | 100%
[5 empty] | 33.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5008.0278 | 80851.7395 | 33.08 | 100%
[5 empty] | 33.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5010.2943 | 80888.3305 | 33.09 | 100%
[5 empty] | 33.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5012.5608 | 80924.9214 | 33.1 | 100%
[5 empty] | 33.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5014.8272 | 80961.5124 | 33.11 | 100%
[5 empty] | 33.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5017.0937 | 80998.1033 | 33.12 | 100%
[5 empty] | 33.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5019.3602 | 81034.6942 | 33.13 | 100%
[5 empty] | 33.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5021.6267 | 81071.2852 | 33.14 | 100%
[5 empty] | 33.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5023.8931 | 81107.8761 | 33.15 | 100%
[5 empty] | 33.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5026.1596 | 81144.4671 | 33.16 | 100%
[5 empty] | 33.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5028.4261 | 81181.058 | 33.17 | 100%
[5 empty] | 33.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5030.6926 | 81217.649 | 33.18 | 100%
[5 empty] | 33.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5032.959 | 81254.2399 | 33.19 | 100%
[5 empty] | 33.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5035.2255 | 81290.8308 | 33.2 | 100%
[5 empty] | 33.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5037.492 | 81327.4218 | 33.21 | 100%
[5 empty] | 33.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5039.7585 | 81364.0127 | 33.22 | 100%
[5 empty] | 33.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5042.0249 | 81400.6037 | 33.23 | 100%
[5 empty] | 33.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5044.2914 | 81437.1946 | 33.24 | 100%
[5 empty] | 33.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5046.5579 | 81473.7856 | 33.25 | 100%
[5 empty] | 33.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5048.8244 | 81510.3765 | 33.26 | 100%
[5 empty] | 33.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5051.0908 | 81546.9675 | 33.27 | 100%
[5 empty] | 33.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5053.3573 | 81583.5584 | 33.28 | 100%
[5 empty] | 33.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5055.6238 | 81620.1493 | 33.29 | 100%
[5 empty] | 33.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5057.8903 | 81656.7403 | 33.3 | 100%
[5 empty] | 33.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5060.1567 | 81693.3312 | 33.31 | 100%
[5 empty] | 33.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5062.4232 | 81729.9222 | 33.32 | 100%
[5 empty] | 33.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5064.6897 | 81766.5131 | 33.33 | 100%
[5 empty] | 33.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5066.9562 | 81803.1041 | 33.34 | 100%
[5 empty] | 33.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5069.2226 | 81839.695 | 33.35 | 100%
[5 empty] | 33.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5071.4891 | 81876.2859 | 33.36 | 100%
[5 empty] | 33.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5073.7556 | 81912.8769 | 33.37 | 100%
[5 empty] | 33.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5076.0221 | 81949.4678 | 33.38 | 100%
[5 empty] | 33.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5078.2885 | 81986.0588 | 33.39 | 100%
[5 empty] | 33.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5080.555 | 82022.6497 | 33.4 | 100%
[5 empty] | 33.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5082.8215 | 82059.2407 | 33.41 | 100%
[5 empty] | 33.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5085.088 | 82095.8316 | 33.42 | 100%
[5 empty] | 33.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5087.3544 | 82132.4226 | 33.43 | 100%
[5 empty] | 33.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5089.6209 | 82169.0135 | 33.44 | 100%
[5 empty] | 33.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5091.8874 | 82205.6044 | 33.45 | 100%
[5 empty] | 33.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5094.1539 | 82242.1954 | 33.46 | 100%
[5 empty] | 33.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5096.4203 | 82278.7863 | 33.47 | 100%
[5 empty] | 33.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5098.6868 | 82315.3773 | 33.48 | 100%
[5 empty] | 33.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5100.9533 | 82351.9682 | 33.49 | 100%
[5 empty] | 33.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5103.2198 | 82388.5592 | 33.5 | 100%
[5 empty] | 33.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5105.4862 | 82425.1501 | 33.51 | 100%
[5 empty] | 33.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5107.7527 | 82461.741 | 33.52 | 100%
[5 empty] | 33.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5110.0192 | 82498.332 | 33.53 | 100%
[5 empty] | 33.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5112.2857 | 82534.9229 | 33.54 | 100%
[5 empty] | 33.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5114.5521 | 82571.5139 | 33.55 | 100%
[5 empty] | 33.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5116.8186 | 82608.1048 | 33.56 | 100%
[5 empty] | 33.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5119.0851 | 82644.6958 | 33.57 | 100%
[5 empty] | 33.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5121.3516 | 82681.2867 | 33.58 | 100%
[5 empty] | 33.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5123.618 | 82717.8776 | 33.59 | 100%
[5 empty] | 33.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5125.8845 | 82754.4686 | 33.6 | 100%
[5 empty] | 33.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5128.151 | 82791.0595 | 33.61 | 100%
[5 empty] | 33.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5130.4175 | 82827.6505 | 33.62 | 100%
[5 empty] | 33.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5132.6839 | 82864.2414 | 33.63 | 100%
[5 empty] | 33.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5134.9504 | 82900.8324 | 33.64 | 100%
[5 empty] | 33.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5137.2169 | 82937.4233 | 33.65 | 100%
[5 empty] | 33.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5139.4834 | 82974.0143 | 33.66 | 100%
[5 empty] | 33.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5141.7498 | 83010.6052 | 33.67 | 100%
[5 empty] | 33.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5144.0163 | 83047.1961 | 33.68 | 100%
[5 empty] | 33.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5146.2828 | 83083.7871 | 33.69 | 100%
[5 empty] | 33.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5148.5493 | 83120.378 | 33.7 | 100%
[5 empty] | 33.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5150.8157 | 83156.969 | 33.71 | 100%
[5 empty] | 33.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5153.0822 | 83193.5599 | 33.72 | 100%
[5 empty] | 33.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5155.3487 | 83230.1509 | 33.73 | 100%
[5 empty] | 33.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5157.6152 | 83266.7418 | 33.74 | 100%
[5 empty] | 33.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5159.8816 | 83303.3327 | 33.75 | 100%
[5 empty] | 33.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5162.1481 | 83339.9237 | 33.76 | 100%
[5 empty] | 33.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5164.4146 | 83376.5146 | 33.77 | 100%
[5 empty] | 33.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5166.6811 | 83413.1056 | 33.78 | 100%
[5 empty] | 33.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5168.9476 | 83449.6965 | 33.79 | 100%
[5 empty] | 33.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5171.214 | 83486.2875 | 33.8 | 100%
[5 empty] | 33.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5173.4805 | 83522.8784 | 33.81 | 100%
[5 empty] | 33.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5175.747 | 83559.4694 | 33.82 | 100%
[5 empty] | 33.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5178.0135 | 83596.0603 | 33.83 | 100%
[5 empty] | 33.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5180.2799 | 83632.6512 | 33.84 | 100%
[5 empty] | 33.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5182.5464 | 83669.2422 | 33.85 | 100%
[5 empty] | 33.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5184.8129 | 83705.8331 | 33.86 | 100%
[5 empty] | 33.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5187.0794 | 83742.4241 | 33.87 | 100%
[5 empty] | 33.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5189.3458 | 83779.015 | 33.88 | 100%
[5 empty] | 33.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5191.6123 | 83815.606 | 33.89 | 100%
[5 empty] | 33.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5193.8788 | 83852.1969 | 33.9 | 100%
[5 empty] | 33.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5196.1453 | 83888.7878 | 33.91 | 100%
[5 empty] | 33.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5198.4117 | 83925.3788 | 33.92 | 100%
[5 empty] | 33.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5200.6782 | 83961.9697 | 33.93 | 100%
[5 empty] | 33.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5202.9447 | 83998.5607 | 33.94 | 100%
[5 empty] | 33.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5205.2112 | 84035.1516 | 33.95 | 100%
[5 empty] | 33.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5207.4776 | 84071.7426 | 33.96 | 100%
[5 empty] | 33.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5209.7441 | 84108.3335 | 33.97 | 100%
[5 empty] | 33.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5212.0106 | 84144.9244 | 33.98 | 100%
[5 empty] | 33.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5214.2771 | 84181.5154 | 33.99 | 100%
[5 empty] | 34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5216.5435 | 84218.1063 | 34 | 100%
[5 empty] | 34.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5218.81 | 84254.6973 | 34.01 | 100%
[5 empty] | 34.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5221.0765 | 84291.2882 | 34.02 | 100%
[5 empty] | 34.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5223.343 | 84327.8792 | 34.03 | 100%
[5 empty] | 34.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5225.6094 | 84364.4701 | 34.04 | 100%
[5 empty] | 34.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5227.8759 | 84401.0611 | 34.05 | 100%
[5 empty] | 34.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5230.1424 | 84437.652 | 34.06 | 100%
[5 empty] | 34.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5232.4089 | 84474.2429 | 34.07 | 100%
[5 empty] | 34.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5234.6753 | 84510.8339 | 34.08 | 100%
[5 empty] | 34.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5236.9418 | 84547.4248 | 34.09 | 100%
[5 empty] | 34.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5239.2083 | 84584.0158 | 34.1 | 100%
[5 empty] | 34.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5241.4748 | 84620.6067 | 34.11 | 100%
[5 empty] | 34.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5243.7412 | 84657.1977 | 34.12 | 100%
[5 empty] | 34.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5246.0077 | 84693.7886 | 34.13 | 100%
[5 empty] | 34.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5248.2742 | 84730.3795 | 34.14 | 100%
[5 empty] | 34.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5250.5407 | 84766.9705 | 34.15 | 100%
[5 empty] | 34.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5252.8071 | 84803.5614 | 34.16 | 100%
[5 empty] | 34.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5255.0736 | 84840.1524 | 34.17 | 100%
[5 empty] | 34.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5257.3401 | 84876.7433 | 34.18 | 100%
[5 empty] | 34.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5259.6066 | 84913.3343 | 34.19 | 100%
[5 empty] | 34.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5261.873 | 84949.9252 | 34.2 | 100%
[5 empty] | 34.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5264.1395 | 84986.5162 | 34.21 | 100%
[5 empty] | 34.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5266.406 | 85023.1071 | 34.22 | 100%
[5 empty] | 34.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5268.6725 | 85059.698 | 34.23 | 100%
[5 empty] | 34.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5270.9389 | 85096.289 | 34.24 | 100%
[5 empty] | 34.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5273.2054 | 85132.8799 | 34.25 | 100%
[5 empty] | 34.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5275.4719 | 85169.4709 | 34.26 | 100%
[5 empty] | 34.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5277.7384 | 85206.0618 | 34.27 | 100%
[5 empty] | 34.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5280.0048 | 85242.6528 | 34.28 | 100%
[5 empty] | 34.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5282.2713 | 85279.2437 | 34.29 | 100%
[5 empty] | 34.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5284.5378 | 85315.8346 | 34.3 | 100%
[5 empty] | 34.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5286.8043 | 85352.4256 | 34.31 | 100%
[5 empty] | 34.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5289.0707 | 85389.0165 | 34.32 | 100%
[5 empty] | 34.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5291.3372 | 85425.6075 | 34.33 | 100%
[5 empty] | 34.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5293.6037 | 85462.1984 | 34.34 | 100%
[5 empty] | 34.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5295.8702 | 85498.7894 | 34.35 | 100%
[5 empty] | 34.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5298.1366 | 85535.3803 | 34.36 | 100%
[5 empty] | 34.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5300.4031 | 85571.9713 | 34.37 | 100%
[5 empty] | 34.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5302.6696 | 85608.5622 | 34.38 | 100%
[5 empty] | 34.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5304.9361 | 85645.1531 | 34.39 | 100%
[5 empty] | 34.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5307.2025 | 85681.7441 | 34.4 | 100%
[5 empty] | 34.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5309.469 | 85718.335 | 34.41 | 100%
[5 empty] | 34.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5311.7355 | 85754.926 | 34.42 | 100%
[5 empty] | 34.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5314.002 | 85791.5169 | 34.43 | 100%
[5 empty] | 34.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5316.2684 | 85828.1079 | 34.44 | 100%
[5 empty] | 34.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5318.5349 | 85864.6988 | 34.45 | 100%
[5 empty] | 34.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5320.8014 | 85901.2897 | 34.46 | 100%
[5 empty] | 34.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5323.0679 | 85937.8807 | 34.47 | 100%
[5 empty] | 34.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5325.3343 | 85974.4716 | 34.48 | 100%
[5 empty] | 34.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5327.6008 | 86011.0626 | 34.49 | 100%
[5 empty] | 34.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5329.8673 | 86047.6535 | 34.5 | 100%
[5 empty] | 34.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5332.1338 | 86084.2445 | 34.51 | 100%
[5 empty] | 34.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5334.4002 | 86120.8354 | 34.52 | 100%
[5 empty] | 34.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5336.6667 | 86157.4263 | 34.53 | 100%
[5 empty] | 34.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5338.9332 | 86194.0173 | 34.54 | 100%
[5 empty] | 34.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5341.1997 | 86230.6082 | 34.55 | 100%
[5 empty] | 34.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5343.4661 | 86267.1992 | 34.56 | 100%
[5 empty] | 34.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5345.7326 | 86303.7901 | 34.57 | 100%
[5 empty] | 34.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5347.9991 | 86340.3811 | 34.58 | 100%
[5 empty] | 34.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5350.2656 | 86376.972 | 34.59 | 100%
[5 empty] | 34.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5352.532 | 86413.563 | 34.6 | 100%
[5 empty] | 34.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5354.7985 | 86450.1539 | 34.61 | 100%
[5 empty] | 34.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5357.065 | 86486.7448 | 34.62 | 100%
[5 empty] | 34.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5359.3315 | 86523.3358 | 34.63 | 100%
[5 empty] | 34.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5361.5979 | 86559.9267 | 34.64 | 100%
[5 empty] | 34.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5363.8644 | 86596.5177 | 34.65 | 100%
[5 empty] | 34.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5366.1309 | 86633.1086 | 34.66 | 100%
[5 empty] | 34.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5368.3974 | 86669.6996 | 34.67 | 100%
[5 empty] | 34.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5370.6638 | 86706.2905 | 34.68 | 100%
[5 empty] | 34.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5372.9303 | 86742.8814 | 34.69 | 100%
[5 empty] | 34.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5375.1968 | 86779.4724 | 34.7 | 100%
[5 empty] | 34.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5377.4633 | 86816.0633 | 34.71 | 100%
[5 empty] | 34.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5379.7297 | 86852.6543 | 34.72 | 100%
[5 empty] | 34.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5381.9962 | 86889.2452 | 34.73 | 100%
[5 empty] | 34.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5384.2627 | 86925.8362 | 34.74 | 100%
[5 empty] | 34.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5386.5292 | 86962.4271 | 34.75 | 100%
[5 empty] | 34.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5388.7956 | 86999.0181 | 34.76 | 100%
[5 empty] | 34.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5391.0621 | 87035.609 | 34.77 | 100%
[5 empty] | 34.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5393.3286 | 87072.1999 | 34.78 | 100%
[5 empty] | 34.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5395.5951 | 87108.7909 | 34.79 | 100%
[5 empty] | 34.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5397.8615 | 87145.3818 | 34.8 | 100%
[5 empty] | 34.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5400.128 | 87181.9728 | 34.81 | 100%
[5 empty] | 34.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5402.3945 | 87218.5637 | 34.82 | 100%
[5 empty] | 34.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5404.661 | 87255.1547 | 34.83 | 100%
[5 empty] | 34.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5406.9274 | 87291.7456 | 34.84 | 100%
[5 empty] | 34.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5409.1939 | 87328.3365 | 34.85 | 100%
[5 empty] | 34.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5411.4604 | 87364.9275 | 34.86 | 100%
[5 empty] | 34.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5413.7269 | 87401.5184 | 34.87 | 100%
[5 empty] | 34.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5415.9933 | 87438.1094 | 34.88 | 100%
[5 empty] | 34.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5418.2598 | 87474.7003 | 34.89 | 100%
[5 empty] | 34.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5420.5263 | 87511.2913 | 34.9 | 100%
[5 empty] | 34.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5422.7928 | 87547.8822 | 34.91 | 100%
[5 empty] | 34.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5425.0592 | 87584.4732 | 34.92 | 100%
[5 empty] | 34.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5427.3257 | 87621.0641 | 34.93 | 100%
[5 empty] | 34.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5429.5922 | 87657.655 | 34.94 | 100%
[5 empty] | 34.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5431.8587 | 87694.246 | 34.95 | 100%
[5 empty] | 34.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5434.1251 | 87730.8369 | 34.96 | 100%
[5 empty] | 34.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5436.3916 | 87767.4279 | 34.97 | 100%
[5 empty] | 34.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5438.6581 | 87804.0188 | 34.98 | 100%
[5 empty] | 34.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5440.9246 | 87840.6098 | 34.99 | 100%
[5 empty] | 35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5443.1911 | 87877.2007 | 35 | 100%
[5 empty] | 35.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5445.4575 | 87913.7916 | 35.01 | 100%
[5 empty] | 35.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5447.724 | 87950.3826 | 35.02 | 100%
[5 empty] | 35.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5449.9905 | 87986.9735 | 35.03 | 100%
[5 empty] | 35.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5452.257 | 88023.5645 | 35.04 | 100%
[5 empty] | 35.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5454.5234 | 88060.1554 | 35.05 | 100%
[5 empty] | 35.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5456.7899 | 88096.7464 | 35.06 | 100%
[5 empty] | 35.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5459.0564 | 88133.3373 | 35.07 | 100%
[5 empty] | 35.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5461.3229 | 88169.9282 | 35.08 | 100%
[5 empty] | 35.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5463.5893 | 88206.5192 | 35.09 | 100%
[5 empty] | 35.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5465.8558 | 88243.1101 | 35.1 | 100%
[5 empty] | 35.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5468.1223 | 88279.7011 | 35.11 | 100%
[5 empty] | 35.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5470.3888 | 88316.292 | 35.12 | 100%
[5 empty] | 35.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5472.6552 | 88352.883 | 35.13 | 100%
[5 empty] | 35.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5474.9217 | 88389.4739 | 35.14 | 100%
[5 empty] | 35.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5477.1882 | 88426.0649 | 35.15 | 100%
[5 empty] | 35.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5479.4547 | 88462.6558 | 35.16 | 100%
[5 empty] | 35.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5481.7211 | 88499.2467 | 35.17 | 100%
[5 empty] | 35.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5483.9876 | 88535.8377 | 35.18 | 100%
[5 empty] | 35.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5486.2541 | 88572.4286 | 35.19 | 100%
[5 empty] | 35.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5488.5206 | 88609.0196 | 35.2 | 100%
[5 empty] | 35.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5490.787 | 88645.6105 | 35.21 | 100%
[5 empty] | 35.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5493.0535 | 88682.2015 | 35.22 | 100%
[5 empty] | 35.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5495.32 | 88718.7924 | 35.23 | 100%
[5 empty] | 35.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5497.5865 | 88755.3833 | 35.24 | 100%
[5 empty] | 35.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5499.8529 | 88791.9743 | 35.25 | 100%
[5 empty] | 35.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5502.1194 | 88828.5652 | 35.26 | 100%
[5 empty] | 35.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5504.3859 | 88865.1562 | 35.27 | 100%
[5 empty] | 35.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5506.6524 | 88901.7471 | 35.28 | 100%
[5 empty] | 35.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5508.9188 | 88938.3381 | 35.29 | 100%
[5 empty] | 35.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5511.1853 | 88974.929 | 35.3 | 100%
[5 empty] | 35.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5513.4518 | 89011.52 | 35.31 | 100%
[5 empty] | 35.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5515.7183 | 89048.1109 | 35.32 | 100%
[5 empty] | 35.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5517.9847 | 89084.7018 | 35.33 | 100%
[5 empty] | 35.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5520.2512 | 89121.2928 | 35.34 | 100%
[5 empty] | 35.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5522.5177 | 89157.8837 | 35.35 | 100%
[5 empty] | 35.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5524.7842 | 89194.4747 | 35.36 | 100%
[5 empty] | 35.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5527.0506 | 89231.0656 | 35.37 | 100%
[5 empty] | 35.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5529.3171 | 89267.6566 | 35.38 | 100%
[5 empty] | 35.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5531.5836 | 89304.2475 | 35.39 | 100%
[5 empty] | 35.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5533.8501 | 89340.8384 | 35.4 | 100%
[5 empty] | 35.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5536.1165 | 89377.4294 | 35.41 | 100%
[5 empty] | 35.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5538.383 | 89414.0203 | 35.42 | 100%
[5 empty] | 35.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5540.6495 | 89450.6113 | 35.43 | 100%
[5 empty] | 35.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5542.916 | 89487.2022 | 35.44 | 100%
[5 empty] | 35.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5545.1824 | 89523.7932 | 35.45 | 100%
[5 empty] | 35.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5547.4489 | 89560.3841 | 35.46 | 100%
[5 empty] | 35.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5549.7154 | 89596.975 | 35.47 | 100%
[5 empty] | 35.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5551.9819 | 89633.566 | 35.48 | 100%
[5 empty] | 35.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5554.2483 | 89670.1569 | 35.49 | 100%
[5 empty] | 35.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5556.5148 | 89706.7479 | 35.5 | 100%
[5 empty] | 35.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5558.7813 | 89743.3388 | 35.51 | 100%
[5 empty] | 35.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5561.0478 | 89779.9298 | 35.52 | 100%
[5 empty] | 35.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5563.3142 | 89816.5207 | 35.53 | 100%
[5 empty] | 35.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5565.5807 | 89853.1117 | 35.54 | 100%
[5 empty] | 35.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5567.8472 | 89889.7026 | 35.55 | 100%
[5 empty] | 35.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5570.1137 | 89926.2935 | 35.56 | 100%
[5 empty] | 35.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5572.3801 | 89962.8845 | 35.57 | 100%
[5 empty] | 35.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5574.6466 | 89999.4754 | 35.58 | 100%
[5 empty] | 35.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5576.9131 | 90036.0664 | 35.59 | 100%
[5 empty] | 35.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5579.1796 | 90072.6573 | 35.6 | 100%
[5 empty] | 35.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5581.446 | 90109.2483 | 35.61 | 100%
[5 empty] | 35.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5583.7125 | 90145.8392 | 35.62 | 100%
[5 empty] | 35.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5585.979 | 90182.4301 | 35.63 | 100%
[5 empty] | 35.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5588.2455 | 90219.0211 | 35.64 | 100%
[5 empty] | 35.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5590.5119 | 90255.612 | 35.65 | 100%
[5 empty] | 35.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5592.7784 | 90292.203 | 35.66 | 100%
[5 empty] | 35.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5595.0449 | 90328.7939 | 35.67 | 100%
[5 empty] | 35.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5597.3114 | 90365.3849 | 35.68 | 100%
[5 empty] | 35.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5599.5778 | 90401.9758 | 35.69 | 100%
[5 empty] | 35.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5601.8443 | 90438.5668 | 35.7 | 100%
[5 empty] | 35.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5604.1108 | 90475.1577 | 35.71 | 100%
[5 empty] | 35.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5606.3773 | 90511.7486 | 35.72 | 100%
[5 empty] | 35.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5608.6437 | 90548.3396 | 35.73 | 100%
[5 empty] | 35.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5610.9102 | 90584.9305 | 35.74 | 100%
[5 empty] | 35.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5613.1767 | 90621.5215 | 35.75 | 100%
[5 empty] | 35.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5615.4432 | 90658.1124 | 35.76 | 100%
[5 empty] | 35.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5617.7096 | 90694.7034 | 35.77 | 100%
[5 empty] | 35.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5619.9761 | 90731.2943 | 35.78 | 100%
[5 empty] | 35.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5622.2426 | 90767.8852 | 35.79 | 100%
[5 empty] | 35.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5624.5091 | 90804.4762 | 35.8 | 100%
[5 empty] | 35.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5626.7755 | 90841.0671 | 35.81 | 100%
[5 empty] | 35.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5629.042 | 90877.6581 | 35.82 | 100%
[5 empty] | 35.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5631.3085 | 90914.249 | 35.83 | 100%
[5 empty] | 35.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5633.575 | 90950.84 | 35.84 | 100%
[5 empty] | 35.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5635.8414 | 90987.4309 | 35.85 | 100%
[5 empty] | 35.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5638.1079 | 91024.0219 | 35.86 | 100%
[5 empty] | 35.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5640.3744 | 91060.6128 | 35.87 | 100%
[5 empty] | 35.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5642.6409 | 91097.2037 | 35.88 | 100%
[5 empty] | 35.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5644.9073 | 91133.7947 | 35.89 | 100%
[5 empty] | 35.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5647.1738 | 91170.3856 | 35.9 | 100%
[5 empty] | 35.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5649.4403 | 91206.9766 | 35.91 | 100%
[5 empty] | 35.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5651.7068 | 91243.5675 | 35.92 | 100%
[5 empty] | 35.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5653.9732 | 91280.1585 | 35.93 | 100%
[5 empty] | 35.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5656.2397 | 91316.7494 | 35.94 | 100%
[5 empty] | 35.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5658.5062 | 91353.3403 | 35.95 | 100%
[5 empty] | 35.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5660.7727 | 91389.9313 | 35.96 | 100%
[5 empty] | 35.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5663.0391 | 91426.5222 | 35.97 | 100%
[5 empty] | 35.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5665.3056 | 91463.1132 | 35.98 | 100%
[5 empty] | 35.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5667.5721 | 91499.7041 | 35.99 | 100%
[5 empty] | 36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5669.8386 | 91536.2951 | 36 | 100%
[5 empty] | 36.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5672.105 | 91572.886 | 36.01 | 100%
[5 empty] | 36.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5674.3715 | 91609.4769 | 36.02 | 100%
[5 empty] | 36.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5676.638 | 91646.0679 | 36.03 | 100%
[5 empty] | 36.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5678.9045 | 91682.6588 | 36.04 | 100%
[5 empty] | 36.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5681.1709 | 91719.2498 | 36.05 | 100%
[5 empty] | 36.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5683.4374 | 91755.8407 | 36.06 | 100%
[5 empty] | 36.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5685.7039 | 91792.4317 | 36.07 | 100%
[5 empty] | 36.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5687.9704 | 91829.0226 | 36.08 | 100%
[5 empty] | 36.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5690.2368 | 91865.6136 | 36.09 | 100%
[5 empty] | 36.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5692.5033 | 91902.2045 | 36.1 | 100%
[5 empty] | 36.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5694.7698 | 91938.7954 | 36.11 | 100%
[5 empty] | 36.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5697.0363 | 91975.3864 | 36.12 | 100%
[5 empty] | 36.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5699.3027 | 92011.9773 | 36.13 | 100%
[5 empty] | 36.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5701.5692 | 92048.5683 | 36.14 | 100%
[5 empty] | 36.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5703.8357 | 92085.1592 | 36.15 | 100%
[5 empty] | 36.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5706.1022 | 92121.7502 | 36.16 | 100%
[5 empty] | 36.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5708.3687 | 92158.3411 | 36.17 | 100%
[5 empty] | 36.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5710.6351 | 92194.932 | 36.18 | 100%
[5 empty] | 36.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5712.9016 | 92231.523 | 36.19 | 100%
[5 empty] | 36.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5715.1681 | 92268.1139 | 36.2 | 100%
[5 empty] | 36.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5717.4346 | 92304.7049 | 36.21 | 100%
[5 empty] | 36.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5719.701 | 92341.2958 | 36.22 | 100%
[5 empty] | 36.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5721.9675 | 92377.8868 | 36.23 | 100%
[5 empty] | 36.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5724.234 | 92414.4777 | 36.24 | 100%
[5 empty] | 36.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5726.5005 | 92451.0687 | 36.25 | 100%
[5 empty] | 36.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5728.7669 | 92487.6596 | 36.26 | 100%
[5 empty] | 36.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5731.0334 | 92524.2505 | 36.27 | 100%
[5 empty] | 36.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5733.2999 | 92560.8415 | 36.28 | 100%
[5 empty] | 36.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5735.5664 | 92597.4324 | 36.29 | 100%
[5 empty] | 36.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5737.8328 | 92634.0234 | 36.3 | 100%
[5 empty] | 36.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5740.0993 | 92670.6143 | 36.31 | 100%
[5 empty] | 36.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5742.3658 | 92707.2053 | 36.32 | 100%
[5 empty] | 36.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5744.6323 | 92743.7962 | 36.33 | 100%
[5 empty] | 36.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5746.8987 | 92780.3871 | 36.34 | 100%
[5 empty] | 36.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5749.1652 | 92816.9781 | 36.35 | 100%
[5 empty] | 36.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5751.4317 | 92853.569 | 36.36 | 100%
[5 empty] | 36.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5753.6982 | 92890.16 | 36.37 | 100%
[5 empty] | 36.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5755.9646 | 92926.7509 | 36.38 | 100%
[5 empty] | 36.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5758.2311 | 92963.3419 | 36.39 | 100%
[5 empty] | 36.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5760.4976 | 92999.9328 | 36.4 | 100%
[5 empty] | 36.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5762.7641 | 93036.5238 | 36.41 | 100%
[5 empty] | 36.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5765.0305 | 93073.1147 | 36.42 | 100%
[5 empty] | 36.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5767.297 | 93109.7056 | 36.43 | 100%
[5 empty] | 36.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5769.5635 | 93146.2966 | 36.44 | 100%
[5 empty] | 36.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5771.83 | 93182.8875 | 36.45 | 100%
[5 empty] | 36.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5774.0964 | 93219.4785 | 36.46 | 100%
[5 empty] | 36.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5776.3629 | 93256.0694 | 36.47 | 100%
[5 empty] | 36.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5778.6294 | 93292.6604 | 36.48 | 100%
[5 empty] | 36.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5780.8959 | 93329.2513 | 36.49 | 100%
[5 empty] | 36.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5783.1623 | 93365.8422 | 36.5 | 100%
[5 empty] | 36.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5785.4288 | 93402.4332 | 36.51 | 100%
[5 empty] | 36.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5787.6953 | 93439.0241 | 36.52 | 100%
[5 empty] | 36.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5789.9618 | 93475.6151 | 36.53 | 100%
[5 empty] | 36.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5792.2282 | 93512.206 | 36.54 | 100%
[5 empty] | 36.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5794.4947 | 93548.797 | 36.55 | 100%
[5 empty] | 36.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5796.7612 | 93585.3879 | 36.56 | 100%
[5 empty] | 36.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5799.0277 | 93621.9788 | 36.57 | 100%
[5 empty] | 36.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5801.2941 | 93658.5698 | 36.58 | 100%
[5 empty] | 36.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5803.5606 | 93695.1607 | 36.59 | 100%
[5 empty] | 36.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5805.8271 | 93731.7517 | 36.6 | 100%
[5 empty] | 36.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5808.0936 | 93768.3426 | 36.61 | 100%
[5 empty] | 36.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5810.36 | 93804.9336 | 36.62 | 100%
[5 empty] | 36.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5812.6265 | 93841.5245 | 36.63 | 100%
[5 empty] | 36.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5814.893 | 93878.1155 | 36.64 | 100%
[5 empty] | 36.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5817.1595 | 93914.7064 | 36.65 | 100%
[5 empty] | 36.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5819.4259 | 93951.2973 | 36.66 | 100%
[5 empty] | 36.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5821.6924 | 93987.8883 | 36.67 | 100%
[5 empty] | 36.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5823.9589 | 94024.4792 | 36.68 | 100%
[5 empty] | 36.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5826.2254 | 94061.0702 | 36.69 | 100%
[5 empty] | 36.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5828.4918 | 94097.6611 | 36.7 | 100%
[5 empty] | 36.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5830.7583 | 94134.2521 | 36.71 | 100%
[5 empty] | 36.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5833.0248 | 94170.843 | 36.72 | 100%
[5 empty] | 36.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5835.2913 | 94207.4339 | 36.73 | 100%
[5 empty] | 36.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5837.5577 | 94244.0249 | 36.74 | 100%
[5 empty] | 36.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5839.8242 | 94280.6158 | 36.75 | 100%
[5 empty] | 36.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5842.0907 | 94317.2068 | 36.76 | 100%
[5 empty] | 36.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5844.3572 | 94353.7977 | 36.77 | 100%
[5 empty] | 36.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5846.6236 | 94390.3887 | 36.78 | 100%
[5 empty] | 36.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5848.8901 | 94426.9796 | 36.79 | 100%
[5 empty] | 36.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5851.1566 | 94463.5706 | 36.8 | 100%
[5 empty] | 36.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5853.4231 | 94500.1615 | 36.81 | 100%
[5 empty] | 36.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5855.6895 | 94536.7524 | 36.82 | 100%
[5 empty] | 36.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5857.956 | 94573.3434 | 36.83 | 100%
[5 empty] | 36.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5860.2225 | 94609.9343 | 36.84 | 100%
[5 empty] | 36.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5862.489 | 94646.5253 | 36.85 | 100%
[5 empty] | 36.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5864.7554 | 94683.1162 | 36.86 | 100%
[5 empty] | 36.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5867.0219 | 94719.7072 | 36.87 | 100%
[5 empty] | 36.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5869.2884 | 94756.2981 | 36.88 | 100%
[5 empty] | 36.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5871.5549 | 94792.889 | 36.89 | 100%
[5 empty] | 36.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5873.8213 | 94829.48 | 36.9 | 100%
[5 empty] | 36.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5876.0878 | 94866.0709 | 36.91 | 100%
[5 empty] | 36.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5878.3543 | 94902.6619 | 36.92 | 100%
[5 empty] | 36.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5880.6208 | 94939.2528 | 36.93 | 100%
[5 empty] | 36.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5882.8872 | 94975.8438 | 36.94 | 100%
[5 empty] | 36.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5885.1537 | 95012.4347 | 36.95 | 100%
[5 empty] | 36.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5887.4202 | 95049.0257 | 36.96 | 100%
[5 empty] | 36.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5889.6867 | 95085.6166 | 36.97 | 100%
[5 empty] | 36.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5891.9531 | 95122.2075 | 36.98 | 100%
[5 empty] | 36.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5894.2196 | 95158.7985 | 36.99 | 100%
[5 empty] | 37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5896.4861 | 95195.3894 | 37 | 100%
[5 empty] | 37.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5898.7526 | 95231.9804 | 37.01 | 100%
[5 empty] | 37.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5901.019 | 95268.5713 | 37.02 | 100%
[5 empty] | 37.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5903.2855 | 95305.1623 | 37.03 | 100%
[5 empty] | 37.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5905.552 | 95341.7532 | 37.04 | 100%
[5 empty] | 37.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5907.8185 | 95378.3441 | 37.05 | 100%
[5 empty] | 37.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5910.0849 | 95414.9351 | 37.06 | 100%
[5 empty] | 37.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5912.3514 | 95451.526 | 37.07 | 100%
[5 empty] | 37.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5914.6179 | 95488.117 | 37.08 | 100%
[5 empty] | 37.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5916.8844 | 95524.7079 | 37.09 | 100%
[5 empty] | 37.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5919.1508 | 95561.2989 | 37.1 | 100%
[5 empty] | 37.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5921.4173 | 95597.8898 | 37.11 | 100%
[5 empty] | 37.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5923.6838 | 95634.4807 | 37.12 | 100%
[5 empty] | 37.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5925.9503 | 95671.0717 | 37.13 | 100%
[5 empty] | 37.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5928.2167 | 95707.6626 | 37.14 | 100%
[5 empty] | 37.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5930.4832 | 95744.2536 | 37.15 | 100%
[5 empty] | 37.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5932.7497 | 95780.8445 | 37.16 | 100%
[5 empty] | 37.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5935.0162 | 95817.4355 | 37.17 | 100%
[5 empty] | 37.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5937.2826 | 95854.0264 | 37.18 | 100%
[5 empty] | 37.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5939.5491 | 95890.6174 | 37.19 | 100%
[5 empty] | 37.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5941.8156 | 95927.2083 | 37.2 | 100%
[5 empty] | 37.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5944.0821 | 95963.7992 | 37.21 | 100%
[5 empty] | 37.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5946.3485 | 96000.3902 | 37.22 | 100%
[5 empty] | 37.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5948.615 | 96036.9811 | 37.23 | 100%
[5 empty] | 37.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5950.8815 | 96073.5721 | 37.24 | 100%
[5 empty] | 37.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5953.148 | 96110.163 | 37.25 | 100%
[5 empty] | 37.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5955.4144 | 96146.754 | 37.26 | 100%
[5 empty] | 37.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5957.6809 | 96183.3449 | 37.27 | 100%
[5 empty] | 37.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5959.9474 | 96219.9358 | 37.28 | 100%
[5 empty] | 37.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5962.2139 | 96256.5268 | 37.29 | 100%
[5 empty] | 37.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5964.4803 | 96293.1177 | 37.3 | 100%
[5 empty] | 37.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5966.7468 | 96329.7087 | 37.31 | 100%
[5 empty] | 37.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5969.0133 | 96366.2996 | 37.32 | 100%
[5 empty] | 37.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5971.2798 | 96402.8906 | 37.33 | 100%
[5 empty] | 37.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5973.5462 | 96439.4815 | 37.34 | 100%
[5 empty] | 37.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5975.8127 | 96476.0725 | 37.35 | 100%
[5 empty] | 37.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5978.0792 | 96512.6634 | 37.36 | 100%
[5 empty] | 37.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5980.3457 | 96549.2543 | 37.37 | 100%
[5 empty] | 37.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5982.6122 | 96585.8453 | 37.38 | 100%
[5 empty] | 37.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5984.8786 | 96622.4362 | 37.39 | 100%
[5 empty] | 37.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5987.1451 | 96659.0272 | 37.4 | 100%
[5 empty] | 37.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5989.4116 | 96695.6181 | 37.41 | 100%
[5 empty] | 37.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5991.6781 | 96732.2091 | 37.42 | 100%
[5 empty] | 37.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5993.9445 | 96768.8 | 37.43 | 100%
[5 empty] | 37.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5996.211 | 96805.3909 | 37.44 | 100%
[5 empty] | 37.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 5998.4775 | 96841.9819 | 37.45 | 100%
[5 empty] | 37.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6000.744 | 96878.5728 | 37.46 | 100%
[5 empty] | 37.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6003.0104 | 96915.1638 | 37.47 | 100%
[5 empty] | 37.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6005.2769 | 96951.7547 | 37.48 | 100%
[5 empty] | 37.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6007.5434 | 96988.3457 | 37.49 | 100%
[5 empty] | 37.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6009.8099 | 97024.9366 | 37.5 | 100%
[5 empty] | 37.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6012.0763 | 97061.5275 | 37.51 | 100%
[5 empty] | 37.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6014.3428 | 97098.1185 | 37.52 | 100%
[5 empty] | 37.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6016.6093 | 97134.7094 | 37.53 | 100%
[5 empty] | 37.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6018.8758 | 97171.3004 | 37.54 | 100%
[5 empty] | 37.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6021.1422 | 97207.8913 | 37.55 | 100%
[5 empty] | 37.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6023.4087 | 97244.4823 | 37.56 | 100%
[5 empty] | 37.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6025.6752 | 97281.0732 | 37.57 | 100%
[5 empty] | 37.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6027.9417 | 97317.6642 | 37.58 | 100%
[5 empty] | 37.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6030.2081 | 97354.2551 | 37.59 | 100%
[5 empty] | 37.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6032.4746 | 97390.846 | 37.6 | 100%
[5 empty] | 37.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6034.7411 | 97427.437 | 37.61 | 100%
[5 empty] | 37.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6037.0076 | 97464.0279 | 37.62 | 100%
[5 empty] | 37.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6039.274 | 97500.6189 | 37.63 | 100%
[5 empty] | 37.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6041.5405 | 97537.2098 | 37.64 | 100%
[5 empty] | 37.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6043.807 | 97573.8008 | 37.65 | 100%
[5 empty] | 37.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6046.0735 | 97610.3917 | 37.66 | 100%
[5 empty] | 37.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6048.3399 | 97646.9826 | 37.67 | 100%
[5 empty] | 37.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6050.6064 | 97683.5736 | 37.68 | 100%
[5 empty] | 37.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6052.8729 | 97720.1645 | 37.69 | 100%
[5 empty] | 37.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6055.1394 | 97756.7555 | 37.7 | 100%
[5 empty] | 37.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6057.4058 | 97793.3464 | 37.71 | 100%
[5 empty] | 37.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6059.6723 | 97829.9374 | 37.72 | 100%
[5 empty] | 37.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6061.9388 | 97866.5283 | 37.73 | 100%
[5 empty] | 37.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6064.2053 | 97903.1193 | 37.74 | 100%
[5 empty] | 37.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6066.4717 | 97939.7102 | 37.75 | 100%
[5 empty] | 37.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6068.7382 | 97976.3011 | 37.76 | 100%
[5 empty] | 37.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6071.0047 | 98012.8921 | 37.77 | 100%
[5 empty] | 37.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6073.2712 | 98049.483 | 37.78 | 100%
[5 empty] | 37.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6075.5376 | 98086.074 | 37.79 | 100%
[5 empty] | 37.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6077.8041 | 98122.6649 | 37.8 | 100%
[5 empty] | 37.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6080.0706 | 98159.2559 | 37.81 | 100%
[5 empty] | 37.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6082.3371 | 98195.8468 | 37.82 | 100%
[5 empty] | 37.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6084.6035 | 98232.4377 | 37.83 | 100%
[5 empty] | 37.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6086.87 | 98269.0287 | 37.84 | 100%
[5 empty] | 37.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6089.1365 | 98305.6196 | 37.85 | 100%
[5 empty] | 37.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6091.403 | 98342.2106 | 37.86 | 100%
[5 empty] | 37.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6093.6694 | 98378.8015 | 37.87 | 100%
[5 empty] | 37.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6095.9359 | 98415.3925 | 37.88 | 100%
[5 empty] | 37.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6098.2024 | 98451.9834 | 37.89 | 100%
[5 empty] | 37.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6100.4689 | 98488.5744 | 37.9 | 100%
[5 empty] | 37.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6102.7353 | 98525.1653 | 37.91 | 100%
[5 empty] | 37.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6105.0018 | 98561.7562 | 37.92 | 100%
[5 empty] | 37.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6107.2683 | 98598.3472 | 37.93 | 100%
[5 empty] | 37.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6109.5348 | 98634.9381 | 37.94 | 100%
[5 empty] | 37.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6111.8012 | 98671.5291 | 37.95 | 100%
[5 empty] | 37.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6114.0677 | 98708.12 | 37.96 | 100%
[5 empty] | 37.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6116.3342 | 98744.711 | 37.97 | 100%
[5 empty] | 37.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6118.6007 | 98781.3019 | 37.98 | 100%
[5 empty] | 37.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6120.8671 | 98817.8928 | 37.99 | 100%
[5 empty] | 38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6123.1336 | 98854.4838 | 38 | 100%
[5 empty] | 38.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6125.4001 | 98891.0747 | 38.01 | 100%
[5 empty] | 38.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6127.6666 | 98927.6657 | 38.02 | 100%
[5 empty] | 38.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6129.933 | 98964.2566 | 38.03 | 100%
[5 empty] | 38.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6132.1995 | 99000.8476 | 38.04 | 100%
[5 empty] | 38.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6134.466 | 99037.4385 | 38.05 | 100%
[5 empty] | 38.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6136.7325 | 99074.0294 | 38.06 | 100%
[5 empty] | 38.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6138.9989 | 99110.6204 | 38.07 | 100%
[5 empty] | 38.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6141.2654 | 99147.2113 | 38.08 | 100%
[5 empty] | 38.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6143.5319 | 99183.8023 | 38.09 | 100%
[5 empty] | 38.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6145.7984 | 99220.3932 | 38.1 | 100%
[5 empty] | 38.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6148.0648 | 99256.9842 | 38.11 | 100%
[5 empty] | 38.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6150.3313 | 99293.5751 | 38.12 | 100%
[5 empty] | 38.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6152.5978 | 99330.1661 | 38.13 | 100%
[5 empty] | 38.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6154.8643 | 99366.757 | 38.14 | 100%
[5 empty] | 38.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6157.1307 | 99403.3479 | 38.15 | 100%
[5 empty] | 38.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6159.3972 | 99439.9389 | 38.16 | 100%
[5 empty] | 38.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6161.6637 | 99476.5298 | 38.17 | 100%
[5 empty] | 38.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6163.9302 | 99513.1208 | 38.18 | 100%
[5 empty] | 38.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6166.1966 | 99549.7117 | 38.19 | 100%
[5 empty] | 38.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6168.4631 | 99586.3027 | 38.2 | 100%
[5 empty] | 38.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6170.7296 | 99622.8936 | 38.21 | 100%
[5 empty] | 38.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6172.9961 | 99659.4845 | 38.22 | 100%
[5 empty] | 38.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6175.2625 | 99696.0755 | 38.23 | 100%
[5 empty] | 38.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6177.529 | 99732.6664 | 38.24 | 100%
[5 empty] | 38.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6179.7955 | 99769.2574 | 38.25 | 100%
[5 empty] | 38.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6182.062 | 99805.8483 | 38.26 | 100%
[5 empty] | 38.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6184.3284 | 99842.4393 | 38.27 | 100%
[5 empty] | 38.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6186.5949 | 99879.0302 | 38.28 | 100%
[5 empty] | 38.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6188.8614 | 99915.6212 | 38.29 | 100%
[5 empty] | 38.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6191.1279 | 99952.2121 | 38.3 | 100%
[5 empty] | 38.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6193.3943 | 99988.803 | 38.31 | 100%
[5 empty] | 38.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6195.6608 | 100025.394 | 38.32 | 100%
[5 empty] | 38.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6197.9273 | 100061.9849 | 38.33 | 100%
[5 empty] | 38.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6200.1938 | 100098.5759 | 38.34 | 100%
[5 empty] | 38.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6202.4602 | 100135.1668 | 38.35 | 100%
[5 empty] | 38.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6204.7267 | 100171.7578 | 38.36 | 100%
[5 empty] | 38.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6206.9932 | 100208.3487 | 38.37 | 100%
[5 empty] | 38.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6209.2597 | 100244.9396 | 38.38 | 100%
[5 empty] | 38.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6211.5261 | 100281.5306 | 38.39 | 100%
[5 empty] | 38.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6213.7926 | 100318.1215 | 38.4 | 100%
[5 empty] | 38.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6216.0591 | 100354.7125 | 38.41 | 100%
[5 empty] | 38.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6218.3256 | 100391.3034 | 38.42 | 100%
[5 empty] | 38.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6220.592 | 100427.8944 | 38.43 | 100%
[5 empty] | 38.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6222.8585 | 100464.4853 | 38.44 | 100%
[5 empty] | 38.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6225.125 | 100501.0763 | 38.45 | 100%
[5 empty] | 38.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6227.3915 | 100537.6672 | 38.46 | 100%
[5 empty] | 38.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6229.6579 | 100574.2581 | 38.47 | 100%
[5 empty] | 38.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6231.9244 | 100610.8491 | 38.48 | 100%
[5 empty] | 38.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6234.1909 | 100647.44 | 38.49 | 100%
[5 empty] | 38.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6236.4574 | 100684.031 | 38.5 | 100%
[5 empty] | 38.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6238.7238 | 100720.6219 | 38.51 | 100%
[5 empty] | 38.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6240.9903 | 100757.2129 | 38.52 | 100%
[5 empty] | 38.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6243.2568 | 100793.8038 | 38.53 | 100%
[5 empty] | 38.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6245.5233 | 100830.3947 | 38.54 | 100%
[5 empty] | 38.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6247.7897 | 100866.9857 | 38.55 | 100%
[5 empty] | 38.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6250.0562 | 100903.5766 | 38.56 | 100%
[5 empty] | 38.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6252.3227 | 100940.1676 | 38.57 | 100%
[5 empty] | 38.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6254.5892 | 100976.7585 | 38.58 | 100%
[5 empty] | 38.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6256.8557 | 101013.3495 | 38.59 | 100%
[5 empty] | 38.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6259.1221 | 101049.9404 | 38.6 | 100%
[5 empty] | 38.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6261.3886 | 101086.5313 | 38.61 | 100%
[5 empty] | 38.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6263.6551 | 101123.1223 | 38.62 | 100%
[5 empty] | 38.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6265.9216 | 101159.7132 | 38.63 | 100%
[5 empty] | 38.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6268.188 | 101196.3042 | 38.64 | 100%
[5 empty] | 38.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6270.4545 | 101232.8951 | 38.65 | 100%
[5 empty] | 38.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6272.721 | 101269.4861 | 38.66 | 100%
[5 empty] | 38.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6274.9875 | 101306.077 | 38.67 | 100%
[5 empty] | 38.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6277.2539 | 101342.668 | 38.68 | 100%
[5 empty] | 38.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6279.5204 | 101379.2589 | 38.69 | 100%
[5 empty] | 38.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6281.7869 | 101415.8498 | 38.7 | 100%
[5 empty] | 38.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6284.0534 | 101452.4408 | 38.71 | 100%
[5 empty] | 38.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6286.3198 | 101489.0317 | 38.72 | 100%
[5 empty] | 38.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6288.5863 | 101525.6227 | 38.73 | 100%
[5 empty] | 38.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6290.8528 | 101562.2136 | 38.74 | 100%
[5 empty] | 38.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6293.1193 | 101598.8046 | 38.75 | 100%
[5 empty] | 38.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6295.3857 | 101635.3955 | 38.76 | 100%
[5 empty] | 38.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6297.6522 | 101671.9864 | 38.77 | 100%
[5 empty] | 38.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6299.9187 | 101708.5774 | 38.78 | 100%
[5 empty] | 38.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6302.1852 | 101745.1683 | 38.79 | 100%
[5 empty] | 38.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6304.4516 | 101781.7593 | 38.8 | 100%
[5 empty] | 38.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6306.7181 | 101818.3502 | 38.81 | 100%
[5 empty] | 38.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6308.9846 | 101854.9412 | 38.82 | 100%
[5 empty] | 38.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6311.2511 | 101891.5321 | 38.83 | 100%
[5 empty] | 38.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6313.5175 | 101928.1231 | 38.84 | 100%
[5 empty] | 38.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6315.784 | 101964.714 | 38.85 | 100%
[5 empty] | 38.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6318.0505 | 102001.3049 | 38.86 | 100%
[5 empty] | 38.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6320.317 | 102037.8959 | 38.87 | 100%
[5 empty] | 38.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6322.5834 | 102074.4868 | 38.88 | 100%
[5 empty] | 38.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6324.8499 | 102111.0778 | 38.89 | 100%
[5 empty] | 38.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6327.1164 | 102147.6687 | 38.9 | 100%
[5 empty] | 38.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6329.3829 | 102184.2597 | 38.91 | 100%
[5 empty] | 38.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6331.6493 | 102220.8506 | 38.92 | 100%
[5 empty] | 38.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6333.9158 | 102257.4415 | 38.93 | 100%
[5 empty] | 38.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6336.1823 | 102294.0325 | 38.94 | 100%
[5 empty] | 38.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6338.4488 | 102330.6234 | 38.95 | 100%
[5 empty] | 38.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6340.7152 | 102367.2144 | 38.96 | 100%
[5 empty] | 38.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6342.9817 | 102403.8053 | 38.97 | 100%
[5 empty] | 38.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6345.2482 | 102440.3963 | 38.98 | 100%
[5 empty] | 38.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6347.5147 | 102476.9872 | 38.99 | 100%
[5 empty] | 39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6349.7811 | 102513.5782 | 39 | 100%
[5 empty] | 39.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6352.0476 | 102550.1691 | 39.01 | 100%
[5 empty] | 39.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6354.3141 | 102586.76 | 39.02 | 100%
[5 empty] | 39.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6356.5806 | 102623.351 | 39.03 | 100%
[5 empty] | 39.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6358.847 | 102659.9419 | 39.04 | 100%
[5 empty] | 39.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6361.1135 | 102696.5329 | 39.05 | 100%
[5 empty] | 39.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6363.38 | 102733.1238 | 39.06 | 100%
[5 empty] | 39.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6365.6465 | 102769.7148 | 39.07 | 100%
[5 empty] | 39.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6367.9129 | 102806.3057 | 39.08 | 100%
[5 empty] | 39.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6370.1794 | 102842.8966 | 39.09 | 100%
[5 empty] | 39.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6372.4459 | 102879.4876 | 39.1 | 100%
[5 empty] | 39.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6374.7124 | 102916.0785 | 39.11 | 100%
[5 empty] | 39.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6376.9788 | 102952.6695 | 39.12 | 100%
[5 empty] | 39.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6379.2453 | 102989.2604 | 39.13 | 100%
[5 empty] | 39.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6381.5118 | 103025.8514 | 39.14 | 100%
[5 empty] | 39.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6383.7783 | 103062.4423 | 39.15 | 100%
[5 empty] | 39.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6386.0447 | 103099.0332 | 39.16 | 100%
[5 empty] | 39.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6388.3112 | 103135.6242 | 39.17 | 100%
[5 empty] | 39.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6390.5777 | 103172.2151 | 39.18 | 100%
[5 empty] | 39.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6392.8442 | 103208.8061 | 39.19 | 100%
[5 empty] | 39.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6395.1106 | 103245.397 | 39.2 | 100%
[5 empty] | 39.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6397.3771 | 103281.988 | 39.21 | 100%
[5 empty] | 39.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6399.6436 | 103318.5789 | 39.22 | 100%
[5 empty] | 39.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6401.9101 | 103355.1699 | 39.23 | 100%
[5 empty] | 39.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6404.1765 | 103391.7608 | 39.24 | 100%
[5 empty] | 39.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6406.443 | 103428.3517 | 39.25 | 100%
[5 empty] | 39.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6408.7095 | 103464.9427 | 39.26 | 100%
[5 empty] | 39.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6410.976 | 103501.5336 | 39.27 | 100%
[5 empty] | 39.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6413.2424 | 103538.1246 | 39.28 | 100%
[5 empty] | 39.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6415.5089 | 103574.7155 | 39.29 | 100%
[5 empty] | 39.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6417.7754 | 103611.3065 | 39.3 | 100%
[5 empty] | 39.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6420.0419 | 103647.8974 | 39.31 | 100%
[5 empty] | 39.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6422.3083 | 103684.4883 | 39.32 | 100%
[5 empty] | 39.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6424.5748 | 103721.0793 | 39.33 | 100%
[5 empty] | 39.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6426.8413 | 103757.6702 | 39.34 | 100%
[5 empty] | 39.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6429.1078 | 103794.2612 | 39.35 | 100%
[5 empty] | 39.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6431.3742 | 103830.8521 | 39.36 | 100%
[5 empty] | 39.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6433.6407 | 103867.4431 | 39.37 | 100%
[5 empty] | 39.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6435.9072 | 103904.034 | 39.38 | 100%
[5 empty] | 39.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6438.1737 | 103940.625 | 39.39 | 100%
[5 empty] | 39.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6440.4401 | 103977.2159 | 39.4 | 100%
[5 empty] | 39.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6442.7066 | 104013.8068 | 39.41 | 100%
[5 empty] | 39.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6444.9731 | 104050.3978 | 39.42 | 100%
[5 empty] | 39.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6447.2396 | 104086.9887 | 39.43 | 100%
[5 empty] | 39.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6449.506 | 104123.5797 | 39.44 | 100%
[5 empty] | 39.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6451.7725 | 104160.1706 | 39.45 | 100%
[5 empty] | 39.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6454.039 | 104196.7616 | 39.46 | 100%
[5 empty] | 39.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6456.3055 | 104233.3525 | 39.47 | 100%
[5 empty] | 39.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6458.5719 | 104269.9434 | 39.48 | 100%
[5 empty] | 39.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6460.8384 | 104306.5344 | 39.49 | 100%
[5 empty] | 39.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6463.1049 | 104343.1253 | 39.5 | 100%
[5 empty] | 39.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6465.3714 | 104379.7163 | 39.51 | 100%
[5 empty] | 39.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6467.6378 | 104416.3072 | 39.52 | 100%
[5 empty] | 39.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6469.9043 | 104452.8982 | 39.53 | 100%
[5 empty] | 39.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6472.1708 | 104489.4891 | 39.54 | 100%
[5 empty] | 39.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6474.4373 | 104526.08 | 39.55 | 100%
[5 empty] | 39.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6476.7037 | 104562.671 | 39.56 | 100%
[5 empty] | 39.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6478.9702 | 104599.2619 | 39.57 | 100%
[5 empty] | 39.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6481.2367 | 104635.8529 | 39.58 | 100%
[5 empty] | 39.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6483.5032 | 104672.4438 | 39.59 | 100%
[5 empty] | 39.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6485.7696 | 104709.0348 | 39.6 | 100%
[5 empty] | 39.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6488.0361 | 104745.6257 | 39.61 | 100%
[5 empty] | 39.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6490.3026 | 104782.2167 | 39.62 | 100%
[5 empty] | 39.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6492.5691 | 104818.8076 | 39.63 | 100%
[5 empty] | 39.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6494.8355 | 104855.3985 | 39.64 | 100%
[5 empty] | 39.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6497.102 | 104891.9895 | 39.65 | 100%
[5 empty] | 39.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6499.3685 | 104928.5804 | 39.66 | 100%
[5 empty] | 39.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6501.635 | 104965.1714 | 39.67 | 100%
[5 empty] | 39.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6503.9014 | 105001.7623 | 39.68 | 100%
[5 empty] | 39.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6506.1679 | 105038.3533 | 39.69 | 100%
[5 empty] | 39.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6508.4344 | 105074.9442 | 39.7 | 100%
[5 empty] | 39.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6510.7009 | 105111.5351 | 39.71 | 100%
[5 empty] | 39.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6512.9673 | 105148.1261 | 39.72 | 100%
[5 empty] | 39.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6515.2338 | 105184.717 | 39.73 | 100%
[5 empty] | 39.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6517.5003 | 105221.308 | 39.74 | 100%
[5 empty] | 39.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6519.7668 | 105257.8989 | 39.75 | 100%
[5 empty] | 39.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6522.0333 | 105294.4899 | 39.76 | 100%
[5 empty] | 39.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6524.2997 | 105331.0808 | 39.77 | 100%
[5 empty] | 39.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6526.5662 | 105367.6718 | 39.78 | 100%
[5 empty] | 39.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6528.8327 | 105404.2627 | 39.79 | 100%
[5 empty] | 39.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6531.0992 | 105440.8536 | 39.8 | 100%
[5 empty] | 39.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6533.3656 | 105477.4446 | 39.81 | 100%
[5 empty] | 39.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6535.6321 | 105514.0355 | 39.82 | 100%
[5 empty] | 39.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6537.8986 | 105550.6265 | 39.83 | 100%
[5 empty] | 39.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6540.1651 | 105587.2174 | 39.84 | 100%
[5 empty] | 39.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6542.4315 | 105623.8084 | 39.85 | 100%
[5 empty] | 39.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6544.698 | 105660.3993 | 39.86 | 100%
[5 empty] | 39.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6546.9645 | 105696.9902 | 39.87 | 100%
[5 empty] | 39.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6549.231 | 105733.5812 | 39.88 | 100%
[5 empty] | 39.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6551.4974 | 105770.1721 | 39.89 | 100%
[5 empty] | 39.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6553.7639 | 105806.7631 | 39.9 | 100%
[5 empty] | 39.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6556.0304 | 105843.354 | 39.91 | 100%
[5 empty] | 39.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6558.2969 | 105879.945 | 39.92 | 100%
[5 empty] | 39.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6560.5633 | 105916.5359 | 39.93 | 100%
[5 empty] | 39.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6562.8298 | 105953.1269 | 39.94 | 100%
[5 empty] | 39.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6565.0963 | 105989.7178 | 39.95 | 100%
[5 empty] | 39.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6567.3628 | 106026.3087 | 39.96 | 100%
[5 empty] | 39.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6569.6292 | 106062.8997 | 39.97 | 100%
[5 empty] | 39.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6571.8957 | 106099.4906 | 39.98 | 100%
[5 empty] | 39.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6574.1622 | 106136.0816 | 39.99 | 100%
[5 empty] | 40 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6576.4287 | 106172.6725 | 40 | 100%
[5 empty] | 40.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6578.6951 | 106209.2635 | 40.01 | 100%
[5 empty] | 40.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6580.9616 | 106245.8544 | 40.02 | 100%
[5 empty] | 40.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6583.2281 | 106282.4453 | 40.03 | 100%
[5 empty] | 40.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6585.4946 | 106319.0363 | 40.04 | 100%
[5 empty] | 40.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6587.761 | 106355.6272 | 40.05 | 100%
[5 empty] | 40.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6590.0275 | 106392.2182 | 40.06 | 100%
[5 empty] | 40.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6592.294 | 106428.8091 | 40.07 | 100%
[5 empty] | 40.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6594.5605 | 106465.4001 | 40.08 | 100%
[5 empty] | 40.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6596.8269 | 106501.991 | 40.09 | 100%
[5 empty] | 40.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6599.0934 | 106538.5819 | 40.1 | 100%
[5 empty] | 40.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6601.3599 | 106575.1729 | 40.11 | 100%
[5 empty] | 40.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6603.6264 | 106611.7638 | 40.12 | 100%
[5 empty] | 40.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6605.8928 | 106648.3548 | 40.13 | 100%
[5 empty] | 40.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6608.1593 | 106684.9457 | 40.14 | 100%
[5 empty] | 40.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6610.4258 | 106721.5367 | 40.15 | 100%
[5 empty] | 40.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6612.6923 | 106758.1276 | 40.16 | 100%
[5 empty] | 40.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6614.9587 | 106794.7186 | 40.17 | 100%
[5 empty] | 40.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6617.2252 | 106831.3095 | 40.18 | 100%
[5 empty] | 40.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6619.4917 | 106867.9004 | 40.19 | 100%
[5 empty] | 40.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6621.7582 | 106904.4914 | 40.2 | 100%
[5 empty] | 40.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6624.0246 | 106941.0823 | 40.21 | 100%
[5 empty] | 40.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6626.2911 | 106977.6733 | 40.22 | 100%
[5 empty] | 40.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6628.5576 | 107014.2642 | 40.23 | 100%
[5 empty] | 40.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6630.8241 | 107050.8552 | 40.24 | 100%
[5 empty] | 40.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6633.0905 | 107087.4461 | 40.25 | 100%
[5 empty] | 40.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6635.357 | 107124.037 | 40.26 | 100%
[5 empty] | 40.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6637.6235 | 107160.628 | 40.27 | 100%
[5 empty] | 40.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6639.89 | 107197.2189 | 40.28 | 100%
[5 empty] | 40.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6642.1564 | 107233.8099 | 40.29 | 100%
[5 empty] | 40.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6644.4229 | 107270.4008 | 40.3 | 100%
[5 empty] | 40.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6646.6894 | 107306.9918 | 40.31 | 100%
[5 empty] | 40.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6648.9559 | 107343.5827 | 40.32 | 100%
[5 empty] | 40.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6651.2223 | 107380.1737 | 40.33 | 100%
[5 empty] | 40.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6653.4888 | 107416.7646 | 40.34 | 100%
[5 empty] | 40.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6655.7553 | 107453.3555 | 40.35 | 100%
[5 empty] | 40.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6658.0218 | 107489.9465 | 40.36 | 100%
[5 empty] | 40.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6660.2882 | 107526.5374 | 40.37 | 100%
[5 empty] | 40.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6662.5547 | 107563.1284 | 40.38 | 100%
[5 empty] | 40.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6664.8212 | 107599.7193 | 40.39 | 100%
[5 empty] | 40.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6667.0877 | 107636.3103 | 40.4 | 100%
[5 empty] | 40.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6669.3541 | 107672.9012 | 40.41 | 100%
[5 empty] | 40.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6671.6206 | 107709.4921 | 40.42 | 100%
[5 empty] | 40.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6673.8871 | 107746.0831 | 40.43 | 100%
[5 empty] | 40.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6676.1536 | 107782.674 | 40.44 | 100%
[5 empty] | 40.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6678.42 | 107819.265 | 40.45 | 100%
[5 empty] | 40.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6680.6865 | 107855.8559 | 40.46 | 100%
[5 empty] | 40.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6682.953 | 107892.4469 | 40.47 | 100%
[5 empty] | 40.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6685.2195 | 107929.0378 | 40.48 | 100%
[5 empty] | 40.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6687.4859 | 107965.6288 | 40.49 | 100%
[5 empty] | 40.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6689.7524 | 108002.2197 | 40.5 | 100%
[5 empty] | 40.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6692.0189 | 108038.8106 | 40.51 | 100%
[5 empty] | 40.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6694.2854 | 108075.4016 | 40.52 | 100%
[5 empty] | 40.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6696.5518 | 108111.9925 | 40.53 | 100%
[5 empty] | 40.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6698.8183 | 108148.5835 | 40.54 | 100%
[5 empty] | 40.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6701.0848 | 108185.1744 | 40.55 | 100%
[5 empty] | 40.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6703.3513 | 108221.7654 | 40.56 | 100%
[5 empty] | 40.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6705.6177 | 108258.3563 | 40.57 | 100%
[5 empty] | 40.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6707.8842 | 108294.9472 | 40.58 | 100%
[5 empty] | 40.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6710.1507 | 108331.5382 | 40.59 | 100%
[5 empty] | 40.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6712.4172 | 108368.1291 | 40.6 | 100%
[5 empty] | 40.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6714.6836 | 108404.7201 | 40.61 | 100%
[5 empty] | 40.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6716.9501 | 108441.311 | 40.62 | 100%
[5 empty] | 40.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6719.2166 | 108477.902 | 40.63 | 100%
[5 empty] | 40.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6721.4831 | 108514.4929 | 40.64 | 100%
[5 empty] | 40.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6723.7495 | 108551.0838 | 40.65 | 100%
[5 empty] | 40.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6726.016 | 108587.6748 | 40.66 | 100%
[5 empty] | 40.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6728.2825 | 108624.2657 | 40.67 | 100%
[5 empty] | 40.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6730.549 | 108660.8567 | 40.68 | 100%
[5 empty] | 40.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6732.8154 | 108697.4476 | 40.69 | 100%
[5 empty] | 40.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6735.0819 | 108734.0386 | 40.7 | 100%
[5 empty] | 40.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6737.3484 | 108770.6295 | 40.71 | 100%
[5 empty] | 40.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6739.6149 | 108807.2205 | 40.72 | 100%
[5 empty] | 40.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6741.8813 | 108843.8114 | 40.73 | 100%
[5 empty] | 40.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6744.1478 | 108880.4023 | 40.74 | 100%
[5 empty] | 40.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6746.4143 | 108916.9933 | 40.75 | 100%
[5 empty] | 40.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6748.6808 | 108953.5842 | 40.76 | 100%
[5 empty] | 40.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6750.9472 | 108990.1752 | 40.77 | 100%
[5 empty] | 40.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6753.2137 | 109026.7661 | 40.78 | 100%
[5 empty] | 40.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6755.4802 | 109063.3571 | 40.79 | 100%
[5 empty] | 40.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6757.7467 | 109099.948 | 40.8 | 100%
[5 empty] | 40.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6760.0131 | 109136.5389 | 40.81 | 100%
[5 empty] | 40.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6762.2796 | 109173.1299 | 40.82 | 100%
[5 empty] | 40.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6764.5461 | 109209.7208 | 40.83 | 100%
[5 empty] | 40.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6766.8126 | 109246.3118 | 40.84 | 100%
[5 empty] | 40.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6769.079 | 109282.9027 | 40.85 | 100%
[5 empty] | 40.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6771.3455 | 109319.4937 | 40.86 | 100%
[5 empty] | 40.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6773.612 | 109356.0846 | 40.87 | 100%
[5 empty] | 40.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6775.8785 | 109392.6756 | 40.88 | 100%
[5 empty] | 40.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6778.1449 | 109429.2665 | 40.89 | 100%
[5 empty] | 40.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6780.4114 | 109465.8574 | 40.9 | 100%
[5 empty] | 40.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6782.6779 | 109502.4484 | 40.91 | 100%
[5 empty] | 40.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6784.9444 | 109539.0393 | 40.92 | 100%
[5 empty] | 40.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6787.2108 | 109575.6303 | 40.93 | 100%
[5 empty] | 40.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6789.4773 | 109612.2212 | 40.94 | 100%
[5 empty] | 40.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6791.7438 | 109648.8122 | 40.95 | 100%
[5 empty] | 40.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6794.0103 | 109685.4031 | 40.96 | 100%
[5 empty] | 40.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6796.2768 | 109721.994 | 40.97 | 100%
[5 empty] | 40.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6798.5432 | 109758.585 | 40.98 | 100%
[5 empty] | 40.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6800.8097 | 109795.1759 | 40.99 | 100%
[5 empty] | 41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6803.0762 | 109831.7669 | 41 | 100%
[5 empty] | 41.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6805.3427 | 109868.3578 | 41.01 | 100%
[5 empty] | 41.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6807.6091 | 109904.9488 | 41.02 | 100%
[5 empty] | 41.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6809.8756 | 109941.5397 | 41.03 | 100%
[5 empty] | 41.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6812.1421 | 109978.1306 | 41.04 | 100%
[5 empty] | 41.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6814.4086 | 110014.7216 | 41.05 | 100%
[5 empty] | 41.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6816.675 | 110051.3125 | 41.06 | 100%
[5 empty] | 41.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6818.9415 | 110087.9035 | 41.07 | 100%
[5 empty] | 41.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6821.208 | 110124.4944 | 41.08 | 100%
[5 empty] | 41.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6823.4745 | 110161.0854 | 41.09 | 100%
[5 empty] | 41.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6825.7409 | 110197.6763 | 41.1 | 100%
[5 empty] | 41.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6828.0074 | 110234.2673 | 41.11 | 100%
[5 empty] | 41.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6830.2739 | 110270.8582 | 41.12 | 100%
[5 empty] | 41.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6832.5404 | 110307.4491 | 41.13 | 100%
[5 empty] | 41.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6834.8068 | 110344.0401 | 41.14 | 100%
[5 empty] | 41.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6837.0733 | 110380.631 | 41.15 | 100%
[5 empty] | 41.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6839.3398 | 110417.222 | 41.16 | 100%
[5 empty] | 41.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6841.6063 | 110453.8129 | 41.17 | 100%
[5 empty] | 41.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6843.8727 | 110490.4039 | 41.18 | 100%
[5 empty] | 41.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6846.1392 | 110526.9948 | 41.19 | 100%
[5 empty] | 41.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6848.4057 | 110563.5857 | 41.2 | 100%
[5 empty] | 41.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6850.6722 | 110600.1767 | 41.21 | 100%
[5 empty] | 41.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6852.9386 | 110636.7676 | 41.22 | 100%
[5 empty] | 41.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6855.2051 | 110673.3586 | 41.23 | 100%
[5 empty] | 41.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6857.4716 | 110709.9495 | 41.24 | 100%
[5 empty] | 41.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6859.7381 | 110746.5405 | 41.25 | 100%
[5 empty] | 41.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6862.0045 | 110783.1314 | 41.26 | 100%
[5 empty] | 41.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6864.271 | 110819.7224 | 41.27 | 100%
[5 empty] | 41.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6866.5375 | 110856.3133 | 41.28 | 100%
[5 empty] | 41.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6868.804 | 110892.9042 | 41.29 | 100%
[5 empty] | 41.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6871.0704 | 110929.4952 | 41.3 | 100%
[5 empty] | 41.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6873.3369 | 110966.0861 | 41.31 | 100%
[5 empty] | 41.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6875.6034 | 111002.6771 | 41.32 | 100%
[5 empty] | 41.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6877.8699 | 111039.268 | 41.33 | 100%
[5 empty] | 41.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6880.1363 | 111075.859 | 41.34 | 100%
[5 empty] | 41.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6882.4028 | 111112.4499 | 41.35 | 100%
[5 empty] | 41.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6884.6693 | 111149.0408 | 41.36 | 100%
[5 empty] | 41.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6886.9358 | 111185.6318 | 41.37 | 100%
[5 empty] | 41.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6889.2022 | 111222.2227 | 41.38 | 100%
[5 empty] | 41.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6891.4687 | 111258.8137 | 41.39 | 100%
[5 empty] | 41.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6893.7352 | 111295.4046 | 41.4 | 100%
[5 empty] | 41.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6896.0017 | 111331.9956 | 41.41 | 100%
[5 empty] | 41.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6898.2681 | 111368.5865 | 41.42 | 100%
[5 empty] | 41.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6900.5346 | 111405.1775 | 41.43 | 100%
[5 empty] | 41.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6902.8011 | 111441.7684 | 41.44 | 100%
[5 empty] | 41.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6905.0676 | 111478.3593 | 41.45 | 100%
[5 empty] | 41.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6907.334 | 111514.9503 | 41.46 | 100%
[5 empty] | 41.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6909.6005 | 111551.5412 | 41.47 | 100%
[5 empty] | 41.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6911.867 | 111588.1322 | 41.48 | 100%
[5 empty] | 41.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6914.1335 | 111624.7231 | 41.49 | 100%
[5 empty] | 41.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6916.3999 | 111661.3141 | 41.5 | 100%
[5 empty] | 41.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6918.6664 | 111697.905 | 41.51 | 100%
[5 empty] | 41.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6920.9329 | 111734.4959 | 41.52 | 100%
[5 empty] | 41.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6923.1994 | 111771.0869 | 41.53 | 100%
[5 empty] | 41.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6925.4658 | 111807.6778 | 41.54 | 100%
[5 empty] | 41.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6927.7323 | 111844.2688 | 41.55 | 100%
[5 empty] | 41.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6929.9988 | 111880.8597 | 41.56 | 100%
[5 empty] | 41.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6932.2653 | 111917.4507 | 41.57 | 100%
[5 empty] | 41.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6934.5317 | 111954.0416 | 41.58 | 100%
[5 empty] | 41.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6936.7982 | 111990.6325 | 41.59 | 100%
[5 empty] | 41.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6939.0647 | 112027.2235 | 41.6 | 100%
[5 empty] | 41.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6941.3312 | 112063.8144 | 41.61 | 100%
[5 empty] | 41.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6943.5976 | 112100.4054 | 41.62 | 100%
[5 empty] | 41.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6945.8641 | 112136.9963 | 41.63 | 100%
[5 empty] | 41.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6948.1306 | 112173.5873 | 41.64 | 100%
[5 empty] | 41.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6950.3971 | 112210.1782 | 41.65 | 100%
[5 empty] | 41.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6952.6635 | 112246.7692 | 41.66 | 100%
[5 empty] | 41.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6954.93 | 112283.3601 | 41.67 | 100%
[5 empty] | 41.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6957.1965 | 112319.951 | 41.68 | 100%
[5 empty] | 41.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6959.463 | 112356.542 | 41.69 | 100%
[5 empty] | 41.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6961.7294 | 112393.1329 | 41.7 | 100%
[5 empty] | 41.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6963.9959 | 112429.7239 | 41.71 | 100%
[5 empty] | 41.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6966.2624 | 112466.3148 | 41.72 | 100%
[5 empty] | 41.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6968.5289 | 112502.9058 | 41.73 | 100%
[5 empty] | 41.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6970.7953 | 112539.4967 | 41.74 | 100%
[5 empty] | 41.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6973.0618 | 112576.0876 | 41.75 | 100%
[5 empty] | 41.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6975.3283 | 112612.6786 | 41.76 | 100%
[5 empty] | 41.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6977.5948 | 112649.2695 | 41.77 | 100%
[5 empty] | 41.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6979.8612 | 112685.8605 | 41.78 | 100%
[5 empty] | 41.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6982.1277 | 112722.4514 | 41.79 | 100%
[5 empty] | 41.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6984.3942 | 112759.0424 | 41.8 | 100%
[5 empty] | 41.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6986.6607 | 112795.6333 | 41.81 | 100%
[5 empty] | 41.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6988.9271 | 112832.2243 | 41.82 | 100%
[5 empty] | 41.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6991.1936 | 112868.8152 | 41.83 | 100%
[5 empty] | 41.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6993.4601 | 112905.4061 | 41.84 | 100%
[5 empty] | 41.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6995.7266 | 112941.9971 | 41.85 | 100%
[5 empty] | 41.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 6997.993 | 112978.588 | 41.86 | 100%
[5 empty] | 41.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7000.2595 | 113015.179 | 41.87 | 100%
[5 empty] | 41.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7002.526 | 113051.7699 | 41.88 | 100%
[5 empty] | 41.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7004.7925 | 113088.3609 | 41.89 | 100%
[5 empty] | 41.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7007.0589 | 113124.9518 | 41.9 | 100%
[5 empty] | 41.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7009.3254 | 113161.5427 | 41.91 | 100%
[5 empty] | 41.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7011.5919 | 113198.1337 | 41.92 | 100%
[5 empty] | 41.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7013.8584 | 113234.7246 | 41.93 | 100%
[5 empty] | 41.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7016.1248 | 113271.3156 | 41.94 | 100%
[5 empty] | 41.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7018.3913 | 113307.9065 | 41.95 | 100%
[5 empty] | 41.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7020.6578 | 113344.4975 | 41.96 | 100%
[5 empty] | 41.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7022.9243 | 113381.0884 | 41.97 | 100%
[5 empty] | 41.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7025.1907 | 113417.6794 | 41.98 | 100%
[5 empty] | 41.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7027.4572 | 113454.2703 | 41.99 | 100%
[5 empty] | 42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7029.7237 | 113490.8612 | 42 | 100%
[5 empty] | 42.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7031.9902 | 113527.4522 | 42.01 | 100%
[5 empty] | 42.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7034.2566 | 113564.0431 | 42.02 | 100%
[5 empty] | 42.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7036.5231 | 113600.6341 | 42.03 | 100%
[5 empty] | 42.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7038.7896 | 113637.225 | 42.04 | 100%
[5 empty] | 42.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7041.0561 | 113673.816 | 42.05 | 100%
[5 empty] | 42.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7043.3225 | 113710.4069 | 42.06 | 100%
[5 empty] | 42.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7045.589 | 113746.9978 | 42.07 | 100%
[5 empty] | 42.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7047.8555 | 113783.5888 | 42.08 | 100%
[5 empty] | 42.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7050.122 | 113820.1797 | 42.09 | 100%
[5 empty] | 42.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7052.3884 | 113856.7707 | 42.1 | 100%
[5 empty] | 42.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7054.6549 | 113893.3616 | 42.11 | 100%
[5 empty] | 42.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7056.9214 | 113929.9526 | 42.12 | 100%
[5 empty] | 42.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7059.1879 | 113966.5435 | 42.13 | 100%
[5 empty] | 42.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7061.4544 | 114003.1344 | 42.14 | 100%
[5 empty] | 42.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7063.7208 | 114039.7254 | 42.15 | 100%
[5 empty] | 42.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7065.9873 | 114076.3163 | 42.16 | 100%
[5 empty] | 42.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7068.2538 | 114112.9073 | 42.17 | 100%
[5 empty] | 42.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7070.5203 | 114149.4982 | 42.18 | 100%
[5 empty] | 42.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7072.7867 | 114186.0892 | 42.19 | 100%
[5 empty] | 42.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7075.0532 | 114222.6801 | 42.2 | 100%
[5 empty] | 42.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7077.3197 | 114259.2711 | 42.21 | 100%
[5 empty] | 42.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7079.5862 | 114295.862 | 42.22 | 100%
[5 empty] | 42.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7081.8526 | 114332.4529 | 42.23 | 100%
[5 empty] | 42.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7084.1191 | 114369.0439 | 42.24 | 100%
[5 empty] | 42.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7086.3856 | 114405.6348 | 42.25 | 100%
[5 empty] | 42.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7088.6521 | 114442.2258 | 42.26 | 100%
[5 empty] | 42.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7090.9185 | 114478.8167 | 42.27 | 100%
[5 empty] | 42.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7093.185 | 114515.4077 | 42.28 | 100%
[5 empty] | 42.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7095.4515 | 114551.9986 | 42.29 | 100%
[5 empty] | 42.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7097.718 | 114588.5895 | 42.3 | 100%
[5 empty] | 42.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7099.9844 | 114625.1805 | 42.31 | 100%
[5 empty] | 42.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7102.2509 | 114661.7714 | 42.32 | 100%
[5 empty] | 42.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7104.5174 | 114698.3624 | 42.33 | 100%
[5 empty] | 42.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7106.7839 | 114734.9533 | 42.34 | 100%
[5 empty] | 42.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7109.0503 | 114771.5443 | 42.35 | 100%
[5 empty] | 42.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7111.3168 | 114808.1352 | 42.36 | 100%
[5 empty] | 42.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7113.5833 | 114844.7262 | 42.37 | 100%
[5 empty] | 42.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7115.8498 | 114881.3171 | 42.38 | 100%
[5 empty] | 42.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7118.1162 | 114917.908 | 42.39 | 100%
[5 empty] | 42.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7120.3827 | 114954.499 | 42.4 | 100%
[5 empty] | 42.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7122.6492 | 114991.0899 | 42.41 | 100%
[5 empty] | 42.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7124.9157 | 115027.6809 | 42.42 | 100%
[5 empty] | 42.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7127.1821 | 115064.2718 | 42.43 | 100%
[5 empty] | 42.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7129.4486 | 115100.8628 | 42.44 | 100%
[5 empty] | 42.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7131.7151 | 115137.4537 | 42.45 | 100%
[5 empty] | 42.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7133.9816 | 115174.0446 | 42.46 | 100%
[5 empty] | 42.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7136.248 | 115210.6356 | 42.47 | 100%
[5 empty] | 42.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7138.5145 | 115247.2265 | 42.48 | 100%
[5 empty] | 42.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7140.781 | 115283.8175 | 42.49 | 100%
[5 empty] | 42.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7143.0475 | 115320.4084 | 42.5 | 100%
[5 empty] | 42.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7145.3139 | 115356.9994 | 42.51 | 100%
[5 empty] | 42.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7147.5804 | 115393.5903 | 42.52 | 100%
[5 empty] | 42.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7149.8469 | 115430.1813 | 42.53 | 100%
[5 empty] | 42.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7152.1134 | 115466.7722 | 42.54 | 100%
[5 empty] | 42.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7154.3798 | 115503.3631 | 42.55 | 100%
[5 empty] | 42.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7156.6463 | 115539.9541 | 42.56 | 100%
[5 empty] | 42.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7158.9128 | 115576.545 | 42.57 | 100%
[5 empty] | 42.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7161.1793 | 115613.136 | 42.58 | 100%
[5 empty] | 42.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7163.4457 | 115649.7269 | 42.59 | 100%
[5 empty] | 42.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7165.7122 | 115686.3179 | 42.6 | 100%
[5 empty] | 42.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7167.9787 | 115722.9088 | 42.61 | 100%
[5 empty] | 42.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7170.2452 | 115759.4997 | 42.62 | 100%
[5 empty] | 42.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7172.5116 | 115796.0907 | 42.63 | 100%
[5 empty] | 42.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7174.7781 | 115832.6816 | 42.64 | 100%
[5 empty] | 42.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7177.0446 | 115869.2726 | 42.65 | 100%
[5 empty] | 42.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7179.3111 | 115905.8635 | 42.66 | 100%
[5 empty] | 42.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7181.5775 | 115942.4545 | 42.67 | 100%
[5 empty] | 42.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7183.844 | 115979.0454 | 42.68 | 100%
[5 empty] | 42.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7186.1105 | 116015.6363 | 42.69 | 100%
[5 empty] | 42.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7188.377 | 116052.2273 | 42.7 | 100%
[5 empty] | 42.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7190.6434 | 116088.8182 | 42.71 | 100%
[5 empty] | 42.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7192.9099 | 116125.4092 | 42.72 | 100%
[5 empty] | 42.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7195.1764 | 116162.0001 | 42.73 | 100%
[5 empty] | 42.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7197.4429 | 116198.5911 | 42.74 | 100%
[5 empty] | 42.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7199.7093 | 116235.182 | 42.75 | 100%
[5 empty] | 42.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7201.9758 | 116271.773 | 42.76 | 100%
[5 empty] | 42.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7204.2423 | 116308.3639 | 42.77 | 100%
[5 empty] | 42.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7206.5088 | 116344.9548 | 42.78 | 100%
[5 empty] | 42.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7208.7752 | 116381.5458 | 42.79 | 100%
[5 empty] | 42.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7211.0417 | 116418.1367 | 42.8 | 100%
[5 empty] | 42.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7213.3082 | 116454.7277 | 42.81 | 100%
[5 empty] | 42.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7215.5747 | 116491.3186 | 42.82 | 100%
[5 empty] | 42.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7217.8411 | 116527.9096 | 42.83 | 100%
[5 empty] | 42.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7220.1076 | 116564.5005 | 42.84 | 100%
[5 empty] | 42.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7222.3741 | 116601.0914 | 42.85 | 100%
[5 empty] | 42.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7224.6406 | 116637.6824 | 42.86 | 100%
[5 empty] | 42.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7226.907 | 116674.2733 | 42.87 | 100%
[5 empty] | 42.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7229.1735 | 116710.8643 | 42.88 | 100%
[5 empty] | 42.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7231.44 | 116747.4552 | 42.89 | 100%
[5 empty] | 42.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7233.7065 | 116784.0462 | 42.9 | 100%
[5 empty] | 42.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7235.9729 | 116820.6371 | 42.91 | 100%
[5 empty] | 42.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7238.2394 | 116857.2281 | 42.92 | 100%
[5 empty] | 42.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7240.5059 | 116893.819 | 42.93 | 100%
[5 empty] | 42.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7242.7724 | 116930.4099 | 42.94 | 100%
[5 empty] | 42.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7245.0388 | 116967.0009 | 42.95 | 100%
[5 empty] | 42.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7247.3053 | 117003.5918 | 42.96 | 100%
[5 empty] | 42.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7249.5718 | 117040.1828 | 42.97 | 100%
[5 empty] | 42.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7251.8383 | 117076.7737 | 42.98 | 100%
[5 empty] | 42.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7254.1047 | 117113.3647 | 42.99 | 100%
[5 empty] | 43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7256.3712 | 117149.9556 | 43 | 100%
[5 empty] | 43.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7258.6377 | 117186.5465 | 43.01 | 100%
[5 empty] | 43.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7260.9042 | 117223.1375 | 43.02 | 100%
[5 empty] | 43.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7263.1706 | 117259.7284 | 43.03 | 100%
[5 empty] | 43.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7265.4371 | 117296.3194 | 43.04 | 100%
[5 empty] | 43.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7267.7036 | 117332.9103 | 43.05 | 100%
[5 empty] | 43.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7269.9701 | 117369.5013 | 43.06 | 100%
[5 empty] | 43.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7272.2365 | 117406.0922 | 43.07 | 100%
[5 empty] | 43.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7274.503 | 117442.6831 | 43.08 | 100%
[5 empty] | 43.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7276.7695 | 117479.2741 | 43.09 | 100%
[5 empty] | 43.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7279.036 | 117515.865 | 43.1 | 100%
[5 empty] | 43.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7281.3024 | 117552.456 | 43.11 | 100%
[5 empty] | 43.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7283.5689 | 117589.0469 | 43.12 | 100%
[5 empty] | 43.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7285.8354 | 117625.6379 | 43.13 | 100%
[5 empty] | 43.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7288.1019 | 117662.2288 | 43.14 | 100%
[5 empty] | 43.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7290.3683 | 117698.8198 | 43.15 | 100%
[5 empty] | 43.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7292.6348 | 117735.4107 | 43.16 | 100%
[5 empty] | 43.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7294.9013 | 117772.0016 | 43.17 | 100%
[5 empty] | 43.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7297.1678 | 117808.5926 | 43.18 | 100%
[5 empty] | 43.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7299.4342 | 117845.1835 | 43.19 | 100%
[5 empty] | 43.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7301.7007 | 117881.7745 | 43.2 | 100%
[5 empty] | 43.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7303.9672 | 117918.3654 | 43.21 | 100%
[5 empty] | 43.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7306.2337 | 117954.9564 | 43.22 | 100%
[5 empty] | 43.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7308.5001 | 117991.5473 | 43.23 | 100%
[5 empty] | 43.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7310.7666 | 118028.1382 | 43.24 | 100%
[5 empty] | 43.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7313.0331 | 118064.7292 | 43.25 | 100%
[5 empty] | 43.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7315.2996 | 118101.3201 | 43.26 | 100%
[5 empty] | 43.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7317.566 | 118137.9111 | 43.27 | 100%
[5 empty] | 43.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7319.8325 | 118174.502 | 43.28 | 100%
[5 empty] | 43.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7322.099 | 118211.093 | 43.29 | 100%
[5 empty] | 43.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7324.3655 | 118247.6839 | 43.3 | 100%
[5 empty] | 43.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7326.6319 | 118284.2749 | 43.31 | 100%
[5 empty] | 43.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7328.8984 | 118320.8658 | 43.32 | 100%
[5 empty] | 43.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7331.1649 | 118357.4567 | 43.33 | 100%
[5 empty] | 43.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7333.4314 | 118394.0477 | 43.34 | 100%
[5 empty] | 43.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7335.6979 | 118430.6386 | 43.35 | 100%
[5 empty] | 43.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7337.9643 | 118467.2296 | 43.36 | 100%
[5 empty] | 43.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7340.2308 | 118503.8205 | 43.37 | 100%
[5 empty] | 43.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7342.4973 | 118540.4115 | 43.38 | 100%
[5 empty] | 43.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7344.7638 | 118577.0024 | 43.39 | 100%
[5 empty] | 43.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7347.0302 | 118613.5933 | 43.4 | 100%
[5 empty] | 43.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7349.2967 | 118650.1843 | 43.41 | 100%
[5 empty] | 43.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7351.5632 | 118686.7752 | 43.42 | 100%
[5 empty] | 43.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7353.8297 | 118723.3662 | 43.43 | 100%
[5 empty] | 43.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7356.0961 | 118759.9571 | 43.44 | 100%
[5 empty] | 43.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7358.3626 | 118796.5481 | 43.45 | 100%
[5 empty] | 43.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7360.6291 | 118833.139 | 43.46 | 100%
[5 empty] | 43.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7362.8956 | 118869.73 | 43.47 | 100%
[5 empty] | 43.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7365.162 | 118906.3209 | 43.48 | 100%
[5 empty] | 43.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7367.4285 | 118942.9118 | 43.49 | 100%
[5 empty] | 43.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7369.695 | 118979.5028 | 43.5 | 100%
[5 empty] | 43.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7371.9615 | 119016.0937 | 43.51 | 100%
[5 empty] | 43.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7374.2279 | 119052.6847 | 43.52 | 100%
[5 empty] | 43.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7376.4944 | 119089.2756 | 43.53 | 100%
[5 empty] | 43.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7378.7609 | 119125.8666 | 43.54 | 100%
[5 empty] | 43.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7381.0274 | 119162.4575 | 43.55 | 100%
[5 empty] | 43.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7383.2938 | 119199.0484 | 43.56 | 100%
[5 empty] | 43.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7385.5603 | 119235.6394 | 43.57 | 100%
[5 empty] | 43.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7387.8268 | 119272.2303 | 43.58 | 100%
[5 empty] | 43.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7390.0933 | 119308.8213 | 43.59 | 100%
[5 empty] | 43.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7392.3597 | 119345.4122 | 43.6 | 100%
[5 empty] | 43.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7394.6262 | 119382.0032 | 43.61 | 100%
[5 empty] | 43.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7396.8927 | 119418.5941 | 43.62 | 100%
[5 empty] | 43.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7399.1592 | 119455.185 | 43.63 | 100%
[5 empty] | 43.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7401.4256 | 119491.776 | 43.64 | 100%
[5 empty] | 43.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7403.6921 | 119528.3669 | 43.65 | 100%
[5 empty] | 43.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7405.9586 | 119564.9579 | 43.66 | 100%
[5 empty] | 43.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7408.2251 | 119601.5488 | 43.67 | 100%
[5 empty] | 43.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7410.4915 | 119638.1398 | 43.68 | 100%
[5 empty] | 43.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7412.758 | 119674.7307 | 43.69 | 100%
[5 empty] | 43.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7415.0245 | 119711.3217 | 43.7 | 100%
[5 empty] | 43.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7417.291 | 119747.9126 | 43.71 | 100%
[5 empty] | 43.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7419.5574 | 119784.5035 | 43.72 | 100%
[5 empty] | 43.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7421.8239 | 119821.0945 | 43.73 | 100%
[5 empty] | 43.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7424.0904 | 119857.6854 | 43.74 | 100%
[5 empty] | 43.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7426.3569 | 119894.2764 | 43.75 | 100%
[5 empty] | 43.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7428.6233 | 119930.8673 | 43.76 | 100%
[5 empty] | 43.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7430.8898 | 119967.4583 | 43.77 | 100%
[5 empty] | 43.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7433.1563 | 120004.0492 | 43.78 | 100%
[5 empty] | 43.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7435.4228 | 120040.6401 | 43.79 | 100%
[5 empty] | 43.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7437.6892 | 120077.2311 | 43.8 | 100%
[5 empty] | 43.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7439.9557 | 120113.822 | 43.81 | 100%
[5 empty] | 43.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7442.2222 | 120150.413 | 43.82 | 100%
[5 empty] | 43.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7444.4887 | 120187.0039 | 43.83 | 100%
[5 empty] | 43.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7446.7551 | 120223.5949 | 43.84 | 100%
[5 empty] | 43.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7449.0216 | 120260.1858 | 43.85 | 100%
[5 empty] | 43.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7451.2881 | 120296.7768 | 43.86 | 100%
[5 empty] | 43.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7453.5546 | 120333.3677 | 43.87 | 100%
[5 empty] | 43.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7455.821 | 120369.9586 | 43.88 | 100%
[5 empty] | 43.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7458.0875 | 120406.5496 | 43.89 | 100%
[5 empty] | 43.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7460.354 | 120443.1405 | 43.9 | 100%
[5 empty] | 43.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7462.6205 | 120479.7315 | 43.91 | 100%
[5 empty] | 43.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7464.8869 | 120516.3224 | 43.92 | 100%
[5 empty] | 43.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7467.1534 | 120552.9134 | 43.93 | 100%
[5 empty] | 43.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7469.4199 | 120589.5043 | 43.94 | 100%
[5 empty] | 43.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7471.6864 | 120626.0952 | 43.95 | 100%
[5 empty] | 43.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7473.9528 | 120662.6862 | 43.96 | 100%
[5 empty] | 43.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7476.2193 | 120699.2771 | 43.97 | 100%
[5 empty] | 43.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7478.4858 | 120735.8681 | 43.98 | 100%
[5 empty] | 43.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7480.7523 | 120772.459 | 43.99 | 100%
[5 empty] | 44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7483.0187 | 120809.05 | 44 | 100%
[5 empty] | 44.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7485.2852 | 120845.6409 | 44.01 | 100%
[5 empty] | 44.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7487.5517 | 120882.2319 | 44.02 | 100%
[5 empty] | 44.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7489.8182 | 120918.8228 | 44.03 | 100%
[5 empty] | 44.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7492.0846 | 120955.4137 | 44.04 | 100%
[5 empty] | 44.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7494.3511 | 120992.0047 | 44.05 | 100%
[5 empty] | 44.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7496.6176 | 121028.5956 | 44.06 | 100%
[5 empty] | 44.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7498.8841 | 121065.1866 | 44.07 | 100%
[5 empty] | 44.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7501.1505 | 121101.7775 | 44.08 | 100%
[5 empty] | 44.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7503.417 | 121138.3685 | 44.09 | 100%
[5 empty] | 44.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7505.6835 | 121174.9594 | 44.1 | 100%
[5 empty] | 44.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7507.95 | 121211.5503 | 44.11 | 100%
[5 empty] | 44.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7510.2164 | 121248.1413 | 44.12 | 100%
[5 empty] | 44.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7512.4829 | 121284.7322 | 44.13 | 100%
[5 empty] | 44.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7514.7494 | 121321.3232 | 44.14 | 100%
[5 empty] | 44.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7517.0159 | 121357.9141 | 44.15 | 100%
[5 empty] | 44.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7519.2823 | 121394.5051 | 44.16 | 100%
[5 empty] | 44.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7521.5488 | 121431.096 | 44.17 | 100%
[5 empty] | 44.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7523.8153 | 121467.6869 | 44.18 | 100%
[5 empty] | 44.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7526.0818 | 121504.2779 | 44.19 | 100%
[5 empty] | 44.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7528.3482 | 121540.8688 | 44.2 | 100%
[5 empty] | 44.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7530.6147 | 121577.4598 | 44.21 | 100%
[5 empty] | 44.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7532.8812 | 121614.0507 | 44.22 | 100%
[5 empty] | 44.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7535.1477 | 121650.6417 | 44.23 | 100%
[5 empty] | 44.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7537.4141 | 121687.2326 | 44.24 | 100%
[5 empty] | 44.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7539.6806 | 121723.8236 | 44.25 | 100%
[5 empty] | 44.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7541.9471 | 121760.4145 | 44.26 | 100%
[5 empty] | 44.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7544.2136 | 121797.0054 | 44.27 | 100%
[5 empty] | 44.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7546.48 | 121833.5964 | 44.28 | 100%
[5 empty] | 44.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7548.7465 | 121870.1873 | 44.29 | 100%
[5 empty] | 44.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7551.013 | 121906.7783 | 44.3 | 100%
[5 empty] | 44.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7553.2795 | 121943.3692 | 44.31 | 100%
[5 empty] | 44.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7555.5459 | 121979.9602 | 44.32 | 100%
[5 empty] | 44.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7557.8124 | 122016.5511 | 44.33 | 100%
[5 empty] | 44.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7560.0789 | 122053.142 | 44.34 | 100%
[5 empty] | 44.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7562.3454 | 122089.733 | 44.35 | 100%
[5 empty] | 44.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7564.6118 | 122126.3239 | 44.36 | 100%
[5 empty] | 44.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7566.8783 | 122162.9149 | 44.37 | 100%
[5 empty] | 44.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7569.1448 | 122199.5058 | 44.38 | 100%
[5 empty] | 44.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7571.4113 | 122236.0968 | 44.39 | 100%
[5 empty] | 44.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7573.6777 | 122272.6877 | 44.4 | 100%
[5 empty] | 44.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7575.9442 | 122309.2787 | 44.41 | 100%
[5 empty] | 44.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7578.2107 | 122345.8696 | 44.42 | 100%
[5 empty] | 44.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7580.4772 | 122382.4605 | 44.43 | 100%
[5 empty] | 44.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7582.7436 | 122419.0515 | 44.44 | 100%
[5 empty] | 44.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7585.0101 | 122455.6424 | 44.45 | 100%
[5 empty] | 44.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7587.2766 | 122492.2334 | 44.46 | 100%
[5 empty] | 44.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7589.5431 | 122528.8243 | 44.47 | 100%
[5 empty] | 44.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7591.8095 | 122565.4153 | 44.48 | 100%
[5 empty] | 44.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7594.076 | 122602.0062 | 44.49 | 100%
[5 empty] | 44.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7596.3425 | 122638.5971 | 44.5 | 100%
[5 empty] | 44.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7598.609 | 122675.1881 | 44.51 | 100%
[5 empty] | 44.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7600.8755 | 122711.779 | 44.52 | 100%
[5 empty] | 44.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7603.1419 | 122748.37 | 44.53 | 100%
[5 empty] | 44.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7605.4084 | 122784.9609 | 44.54 | 100%
[5 empty] | 44.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7607.6749 | 122821.5519 | 44.55 | 100%
[5 empty] | 44.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7609.9414 | 122858.1428 | 44.56 | 100%
[5 empty] | 44.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7612.2078 | 122894.7337 | 44.57 | 100%
[5 empty] | 44.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7614.4743 | 122931.3247 | 44.58 | 100%
[5 empty] | 44.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7616.7408 | 122967.9156 | 44.59 | 100%
[5 empty] | 44.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7619.0073 | 123004.5066 | 44.6 | 100%
[5 empty] | 44.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7621.2737 | 123041.0975 | 44.61 | 100%
[5 empty] | 44.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7623.5402 | 123077.6885 | 44.62 | 100%
[5 empty] | 44.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7625.8067 | 123114.2794 | 44.63 | 100%
[5 empty] | 44.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7628.0732 | 123150.8704 | 44.64 | 100%
[5 empty] | 44.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7630.3396 | 123187.4613 | 44.65 | 100%
[5 empty] | 44.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7632.6061 | 123224.0522 | 44.66 | 100%
[5 empty] | 44.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7634.8726 | 123260.6432 | 44.67 | 100%
[5 empty] | 44.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7637.1391 | 123297.2341 | 44.68 | 100%
[5 empty] | 44.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7639.4055 | 123333.8251 | 44.69 | 100%
[5 empty] | 44.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7641.672 | 123370.416 | 44.7 | 100%
[5 empty] | 44.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7643.9385 | 123407.007 | 44.71 | 100%
[5 empty] | 44.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7646.205 | 123443.5979 | 44.72 | 100%
[5 empty] | 44.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7648.4714 | 123480.1888 | 44.73 | 100%
[5 empty] | 44.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7650.7379 | 123516.7798 | 44.74 | 100%
[5 empty] | 44.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7653.0044 | 123553.3707 | 44.75 | 100%
[5 empty] | 44.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7655.2709 | 123589.9617 | 44.76 | 100%
[5 empty] | 44.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7657.5373 | 123626.5526 | 44.77 | 100%
[5 empty] | 44.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7659.8038 | 123663.1436 | 44.78 | 100%
[5 empty] | 44.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7662.0703 | 123699.7345 | 44.79 | 100%
[5 empty] | 44.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7664.3368 | 123736.3255 | 44.8 | 100%
[5 empty] | 44.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7666.6032 | 123772.9164 | 44.81 | 100%
[5 empty] | 44.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7668.8697 | 123809.5073 | 44.82 | 100%
[5 empty] | 44.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7671.1362 | 123846.0983 | 44.83 | 100%
[5 empty] | 44.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7673.4027 | 123882.6892 | 44.84 | 100%
[5 empty] | 44.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7675.6691 | 123919.2802 | 44.85 | 100%
[5 empty] | 44.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7677.9356 | 123955.8711 | 44.86 | 100%
[5 empty] | 44.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7680.2021 | 123992.4621 | 44.87 | 100%
[5 empty] | 44.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7682.4686 | 124029.053 | 44.88 | 100%
[5 empty] | 44.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7684.735 | 124065.6439 | 44.89 | 100%
[5 empty] | 44.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7687.0015 | 124102.2349 | 44.9 | 100%
[5 empty] | 44.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7689.268 | 124138.8258 | 44.91 | 100%
[5 empty] | 44.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7691.5345 | 124175.4168 | 44.92 | 100%
[5 empty] | 44.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7693.8009 | 124212.0077 | 44.93 | 100%
[5 empty] | 44.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7696.0674 | 124248.5987 | 44.94 | 100%
[5 empty] | 44.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7698.3339 | 124285.1896 | 44.95 | 100%
[5 empty] | 44.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7700.6004 | 124321.7806 | 44.96 | 100%
[5 empty] | 44.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7702.8668 | 124358.3715 | 44.97 | 100%
[5 empty] | 44.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7705.1333 | 124394.9624 | 44.98 | 100%
[5 empty] | 44.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7707.3998 | 124431.5534 | 44.99 | 100%
[5 empty] | 45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7709.6663 | 124468.1443 | 45 | 100%
[5 empty] | 45.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7711.9327 | 124504.7353 | 45.01 | 100%
[5 empty] | 45.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7714.1992 | 124541.3262 | 45.02 | 100%
[5 empty] | 45.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7716.4657 | 124577.9172 | 45.03 | 100%
[5 empty] | 45.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7718.7322 | 124614.5081 | 45.04 | 100%
[5 empty] | 45.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7720.9986 | 124651.099 | 45.05 | 100%
[5 empty] | 45.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7723.2651 | 124687.69 | 45.06 | 100%
[5 empty] | 45.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7725.5316 | 124724.2809 | 45.07 | 100%
[5 empty] | 45.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7727.7981 | 124760.8719 | 45.08 | 100%
[5 empty] | 45.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7730.0645 | 124797.4628 | 45.09 | 100%
[5 empty] | 45.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7732.331 | 124834.0538 | 45.1 | 100%
[5 empty] | 45.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7734.5975 | 124870.6447 | 45.11 | 100%
[5 empty] | 45.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7736.864 | 124907.2356 | 45.12 | 100%
[5 empty] | 45.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7739.1304 | 124943.8266 | 45.13 | 100%
[5 empty] | 45.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7741.3969 | 124980.4175 | 45.14 | 100%
[5 empty] | 45.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7743.6634 | 125017.0085 | 45.15 | 100%
[5 empty] | 45.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7745.9299 | 125053.5994 | 45.16 | 100%
[5 empty] | 45.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7748.1963 | 125090.1904 | 45.17 | 100%
[5 empty] | 45.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7750.4628 | 125126.7813 | 45.18 | 100%
[5 empty] | 45.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7752.7293 | 125163.3723 | 45.19 | 100%
[5 empty] | 45.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7754.9958 | 125199.9632 | 45.2 | 100%
[5 empty] | 45.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7757.2622 | 125236.5541 | 45.21 | 100%
[5 empty] | 45.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7759.5287 | 125273.1451 | 45.22 | 100%
[5 empty] | 45.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7761.7952 | 125309.736 | 45.23 | 100%
[5 empty] | 45.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7764.0617 | 125346.327 | 45.24 | 100%
[5 empty] | 45.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7766.3281 | 125382.9179 | 45.25 | 100%
[5 empty] | 45.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7768.5946 | 125419.5089 | 45.26 | 100%
[5 empty] | 45.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7770.8611 | 125456.0998 | 45.27 | 100%
[5 empty] | 45.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7773.1276 | 125492.6907 | 45.28 | 100%
[5 empty] | 45.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7775.394 | 125529.2817 | 45.29 | 100%
[5 empty] | 45.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7777.6605 | 125565.8726 | 45.3 | 100%
[5 empty] | 45.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7779.927 | 125602.4636 | 45.31 | 100%
[5 empty] | 45.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7782.1935 | 125639.0545 | 45.32 | 100%
[5 empty] | 45.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7784.4599 | 125675.6455 | 45.33 | 100%
[5 empty] | 45.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7786.7264 | 125712.2364 | 45.34 | 100%
[5 empty] | 45.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7788.9929 | 125748.8274 | 45.35 | 100%
[5 empty] | 45.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7791.2594 | 125785.4183 | 45.36 | 100%
[5 empty] | 45.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7793.5258 | 125822.0092 | 45.37 | 100%
[5 empty] | 45.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7795.7923 | 125858.6002 | 45.38 | 100%
[5 empty] | 45.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7798.0588 | 125895.1911 | 45.39 | 100%
[5 empty] | 45.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7800.3253 | 125931.7821 | 45.4 | 100%
[5 empty] | 45.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7802.5917 | 125968.373 | 45.41 | 100%
[5 empty] | 45.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7804.8582 | 126004.964 | 45.42 | 100%
[5 empty] | 45.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7807.1247 | 126041.5549 | 45.43 | 100%
[5 empty] | 45.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7809.3912 | 126078.1458 | 45.44 | 100%
[5 empty] | 45.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7811.6576 | 126114.7368 | 45.45 | 100%
[5 empty] | 45.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7813.9241 | 126151.3277 | 45.46 | 100%
[5 empty] | 45.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7816.1906 | 126187.9187 | 45.47 | 100%
[5 empty] | 45.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7818.4571 | 126224.5096 | 45.48 | 100%
[5 empty] | 45.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7820.7235 | 126261.1006 | 45.49 | 100%
[5 empty] | 45.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7822.99 | 126297.6915 | 45.5 | 100%
[5 empty] | 45.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7825.2565 | 126334.2825 | 45.51 | 100%
[5 empty] | 45.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7827.523 | 126370.8734 | 45.52 | 100%
[5 empty] | 45.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7829.7894 | 126407.4643 | 45.53 | 100%
[5 empty] | 45.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7832.0559 | 126444.0553 | 45.54 | 100%
[5 empty] | 45.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7834.3224 | 126480.6462 | 45.55 | 100%
[5 empty] | 45.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7836.5889 | 126517.2372 | 45.56 | 100%
[5 empty] | 45.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7838.8553 | 126553.8281 | 45.57 | 100%
[5 empty] | 45.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7841.1218 | 126590.4191 | 45.58 | 100%
[5 empty] | 45.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7843.3883 | 126627.01 | 45.59 | 100%
[5 empty] | 45.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7845.6548 | 126663.6009 | 45.6 | 100%
[5 empty] | 45.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7847.9212 | 126700.1919 | 45.61 | 100%
[5 empty] | 45.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7850.1877 | 126736.7828 | 45.62 | 100%
[5 empty] | 45.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7852.4542 | 126773.3738 | 45.63 | 100%
[5 empty] | 45.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7854.7207 | 126809.9647 | 45.64 | 100%
[5 empty] | 45.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7856.9871 | 126846.5557 | 45.65 | 100%
[5 empty] | 45.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7859.2536 | 126883.1466 | 45.66 | 100%
[5 empty] | 45.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7861.5201 | 126919.7375 | 45.67 | 100%
[5 empty] | 45.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7863.7866 | 126956.3285 | 45.68 | 100%
[5 empty] | 45.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7866.053 | 126992.9194 | 45.69 | 100%
[5 empty] | 45.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7868.3195 | 127029.5104 | 45.7 | 100%
[5 empty] | 45.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7870.586 | 127066.1013 | 45.71 | 100%
[5 empty] | 45.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7872.8525 | 127102.6923 | 45.72 | 100%
[5 empty] | 45.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7875.119 | 127139.2832 | 45.73 | 100%
[5 empty] | 45.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7877.3854 | 127175.8742 | 45.74 | 100%
[5 empty] | 45.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7879.6519 | 127212.4651 | 45.75 | 100%
[5 empty] | 45.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7881.9184 | 127249.056 | 45.76 | 100%
[5 empty] | 45.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7884.1849 | 127285.647 | 45.77 | 100%
[5 empty] | 45.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7886.4513 | 127322.2379 | 45.78 | 100%
[5 empty] | 45.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7888.7178 | 127358.8289 | 45.79 | 100%
[5 empty] | 45.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7890.9843 | 127395.4198 | 45.8 | 100%
[5 empty] | 45.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7893.2508 | 127432.0108 | 45.81 | 100%
[5 empty] | 45.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7895.5172 | 127468.6017 | 45.82 | 100%
[5 empty] | 45.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7897.7837 | 127505.1926 | 45.83 | 100%
[5 empty] | 45.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7900.0502 | 127541.7836 | 45.84 | 100%
[5 empty] | 45.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7902.3167 | 127578.3745 | 45.85 | 100%
[5 empty] | 45.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7904.5831 | 127614.9655 | 45.86 | 100%
[5 empty] | 45.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7906.8496 | 127651.5564 | 45.87 | 100%
[5 empty] | 45.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7909.1161 | 127688.1474 | 45.88 | 100%
[5 empty] | 45.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7911.3826 | 127724.7383 | 45.89 | 100%
[5 empty] | 45.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7913.649 | 127761.3293 | 45.9 | 100%
[5 empty] | 45.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7915.9155 | 127797.9202 | 45.91 | 100%
[5 empty] | 45.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7918.182 | 127834.5111 | 45.92 | 100%
[5 empty] | 45.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7920.4485 | 127871.1021 | 45.93 | 100%
[5 empty] | 45.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7922.7149 | 127907.693 | 45.94 | 100%
[5 empty] | 45.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7924.9814 | 127944.284 | 45.95 | 100%
[5 empty] | 45.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7927.2479 | 127980.8749 | 45.96 | 100%
[5 empty] | 45.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7929.5144 | 128017.4659 | 45.97 | 100%
[5 empty] | 45.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7931.7808 | 128054.0568 | 45.98 | 100%
[5 empty] | 45.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7934.0473 | 128090.6477 | 45.99 | 100%
[5 empty] | 46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7936.3138 | 128127.2387 | 46 | 100%
[5 empty] | 46.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7938.5803 | 128163.8296 | 46.01 | 100%
[5 empty] | 46.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7940.8467 | 128200.4206 | 46.02 | 100%
[5 empty] | 46.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7943.1132 | 128237.0115 | 46.03 | 100%
[5 empty] | 46.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7945.3797 | 128273.6025 | 46.04 | 100%
[5 empty] | 46.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7947.6462 | 128310.1934 | 46.05 | 100%
[5 empty] | 46.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7949.9126 | 128346.7844 | 46.06 | 100%
[5 empty] | 46.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7952.1791 | 128383.3753 | 46.07 | 100%
[5 empty] | 46.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7954.4456 | 128419.9662 | 46.08 | 100%
[5 empty] | 46.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7956.7121 | 128456.5572 | 46.09 | 100%
[5 empty] | 46.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7958.9785 | 128493.1481 | 46.1 | 100%
[5 empty] | 46.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7961.245 | 128529.7391 | 46.11 | 100%
[5 empty] | 46.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7963.5115 | 128566.33 | 46.12 | 100%
[5 empty] | 46.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7965.778 | 128602.921 | 46.13 | 100%
[5 empty] | 46.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7968.0444 | 128639.5119 | 46.14 | 100%
[5 empty] | 46.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7970.3109 | 128676.1028 | 46.15 | 100%
[5 empty] | 46.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7972.5774 | 128712.6938 | 46.16 | 100%
[5 empty] | 46.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7974.8439 | 128749.2847 | 46.17 | 100%
[5 empty] | 46.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7977.1103 | 128785.8757 | 46.18 | 100%
[5 empty] | 46.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7979.3768 | 128822.4666 | 46.19 | 100%
[5 empty] | 46.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7981.6433 | 128859.0576 | 46.2 | 100%
[5 empty] | 46.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7983.9098 | 128895.6485 | 46.21 | 100%
[5 empty] | 46.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7986.1762 | 128932.2394 | 46.22 | 100%
[5 empty] | 46.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7988.4427 | 128968.8304 | 46.23 | 100%
[5 empty] | 46.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7990.7092 | 129005.4213 | 46.24 | 100%
[5 empty] | 46.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7992.9757 | 129042.0123 | 46.25 | 100%
[5 empty] | 46.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7995.2421 | 129078.6032 | 46.26 | 100%
[5 empty] | 46.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7997.5086 | 129115.1942 | 46.27 | 100%
[5 empty] | 46.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 7999.7751 | 129151.7851 | 46.28 | 100%
[5 empty] | 46.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8002.0416 | 129188.3761 | 46.29 | 100%
[5 empty] | 46.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8004.308 | 129224.967 | 46.3 | 100%
[5 empty] | 46.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8006.5745 | 129261.5579 | 46.31 | 100%
[5 empty] | 46.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8008.841 | 129298.1489 | 46.32 | 100%
[5 empty] | 46.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8011.1075 | 129334.7398 | 46.33 | 100%
[5 empty] | 46.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8013.3739 | 129371.3308 | 46.34 | 100%
[5 empty] | 46.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8015.6404 | 129407.9217 | 46.35 | 100%
[5 empty] | 46.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8017.9069 | 129444.5127 | 46.36 | 100%
[5 empty] | 46.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8020.1734 | 129481.1036 | 46.37 | 100%
[5 empty] | 46.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8022.4398 | 129517.6945 | 46.38 | 100%
[5 empty] | 46.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8024.7063 | 129554.2855 | 46.39 | 100%
[5 empty] | 46.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8026.9728 | 129590.8764 | 46.4 | 100%
[5 empty] | 46.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8029.2393 | 129627.4674 | 46.41 | 100%
[5 empty] | 46.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8031.5057 | 129664.0583 | 46.42 | 100%
[5 empty] | 46.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8033.7722 | 129700.6493 | 46.43 | 100%
[5 empty] | 46.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8036.0387 | 129737.2402 | 46.44 | 100%
[5 empty] | 46.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8038.3052 | 129773.8312 | 46.45 | 100%
[5 empty] | 46.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8040.5716 | 129810.4221 | 46.46 | 100%
[5 empty] | 46.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8042.8381 | 129847.013 | 46.47 | 100%
[5 empty] | 46.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8045.1046 | 129883.604 | 46.48 | 100%
[5 empty] | 46.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8047.3711 | 129920.1949 | 46.49 | 100%
[5 empty] | 46.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8049.6375 | 129956.7859 | 46.5 | 100%
[5 empty] | 46.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8051.904 | 129993.3768 | 46.51 | 100%
[5 empty] | 46.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8054.1705 | 130029.9678 | 46.52 | 100%
[5 empty] | 46.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8056.437 | 130066.5587 | 46.53 | 100%
[5 empty] | 46.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8058.7034 | 130103.1496 | 46.54 | 100%
[5 empty] | 46.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8060.9699 | 130139.7406 | 46.55 | 100%
[5 empty] | 46.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8063.2364 | 130176.3315 | 46.56 | 100%
[5 empty] | 46.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8065.5029 | 130212.9225 | 46.57 | 100%
[5 empty] | 46.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8067.7693 | 130249.5134 | 46.58 | 100%
[5 empty] | 46.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8070.0358 | 130286.1044 | 46.59 | 100%
[5 empty] | 46.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8072.3023 | 130322.6953 | 46.6 | 100%
[5 empty] | 46.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8074.5688 | 130359.2862 | 46.61 | 100%
[5 empty] | 46.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8076.8352 | 130395.8772 | 46.62 | 100%
[5 empty] | 46.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8079.1017 | 130432.4681 | 46.63 | 100%
[5 empty] | 46.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8081.3682 | 130469.0591 | 46.64 | 100%
[5 empty] | 46.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8083.6347 | 130505.65 | 46.65 | 100%
[5 empty] | 46.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8085.9011 | 130542.241 | 46.66 | 100%
[5 empty] | 46.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8088.1676 | 130578.8319 | 46.67 | 100%
[5 empty] | 46.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8090.4341 | 130615.4229 | 46.68 | 100%
[5 empty] | 46.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8092.7006 | 130652.0138 | 46.69 | 100%
[5 empty] | 46.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8094.967 | 130688.6047 | 46.7 | 100%
[5 empty] | 46.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8097.2335 | 130725.1957 | 46.71 | 100%
[5 empty] | 46.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8099.5 | 130761.7866 | 46.72 | 100%
[5 empty] | 46.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8101.7665 | 130798.3776 | 46.73 | 100%
[5 empty] | 46.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8104.0329 | 130834.9685 | 46.74 | 100%
[5 empty] | 46.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8106.2994 | 130871.5595 | 46.75 | 100%
[5 empty] | 46.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8108.5659 | 130908.1504 | 46.76 | 100%
[5 empty] | 46.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8110.8324 | 130944.7413 | 46.77 | 100%
[5 empty] | 46.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8113.0988 | 130981.3323 | 46.78 | 100%
[5 empty] | 46.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8115.3653 | 131017.9232 | 46.79 | 100%
[5 empty] | 46.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8117.6318 | 131054.5142 | 46.8 | 100%
[5 empty] | 46.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8119.8983 | 131091.1051 | 46.81 | 100%
[5 empty] | 46.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8122.1647 | 131127.6961 | 46.82 | 100%
[5 empty] | 46.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8124.4312 | 131164.287 | 46.83 | 100%
[5 empty] | 46.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8126.6977 | 131200.878 | 46.84 | 100%
[5 empty] | 46.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8128.9642 | 131237.4689 | 46.85 | 100%
[5 empty] | 46.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8131.2306 | 131274.0598 | 46.86 | 100%
[5 empty] | 46.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8133.4971 | 131310.6508 | 46.87 | 100%
[5 empty] | 46.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8135.7636 | 131347.2417 | 46.88 | 100%
[5 empty] | 46.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8138.0301 | 131383.8327 | 46.89 | 100%
[5 empty] | 46.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8140.2966 | 131420.4236 | 46.9 | 100%
[5 empty] | 46.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8142.563 | 131457.0146 | 46.91 | 100%
[5 empty] | 46.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8144.8295 | 131493.6055 | 46.92 | 100%
[5 empty] | 46.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8147.096 | 131530.1964 | 46.93 | 100%
[5 empty] | 46.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8149.3625 | 131566.7874 | 46.94 | 100%
[5 empty] | 46.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8151.6289 | 131603.3783 | 46.95 | 100%
[5 empty] | 46.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8153.8954 | 131639.9693 | 46.96 | 100%
[5 empty] | 46.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8156.1619 | 131676.5602 | 46.97 | 100%
[5 empty] | 46.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8158.4284 | 131713.1512 | 46.98 | 100%
[5 empty] | 46.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8160.6948 | 131749.7421 | 46.99 | 100%
[5 empty] | 47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8162.9613 | 131786.3331 | 47 | 100%
[5 empty] | 47.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8165.2278 | 131822.924 | 47.01 | 100%
[5 empty] | 47.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8167.4943 | 131859.5149 | 47.02 | 100%
[5 empty] | 47.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8169.7607 | 131896.1059 | 47.03 | 100%
[5 empty] | 47.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8172.0272 | 131932.6968 | 47.04 | 100%
[5 empty] | 47.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8174.2937 | 131969.2878 | 47.05 | 100%
[5 empty] | 47.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8176.5602 | 132005.8787 | 47.06 | 100%
[5 empty] | 47.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8178.8266 | 132042.4697 | 47.07 | 100%
[5 empty] | 47.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8181.0931 | 132079.0606 | 47.08 | 100%
[5 empty] | 47.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8183.3596 | 132115.6515 | 47.09 | 100%
[5 empty] | 47.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8185.6261 | 132152.2425 | 47.1 | 100%
[5 empty] | 47.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8187.8925 | 132188.8334 | 47.11 | 100%
[5 empty] | 47.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8190.159 | 132225.4244 | 47.12 | 100%
[5 empty] | 47.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8192.4255 | 132262.0153 | 47.13 | 100%
[5 empty] | 47.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8194.692 | 132298.6063 | 47.14 | 100%
[5 empty] | 47.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8196.9584 | 132335.1972 | 47.15 | 100%
[5 empty] | 47.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8199.2249 | 132371.7881 | 47.16 | 100%
[5 empty] | 47.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8201.4914 | 132408.3791 | 47.17 | 100%
[5 empty] | 47.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8203.7579 | 132444.97 | 47.18 | 100%
[5 empty] | 47.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8206.0243 | 132481.561 | 47.19 | 100%
[5 empty] | 47.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8208.2908 | 132518.1519 | 47.2 | 100%
[5 empty] | 47.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8210.5573 | 132554.7429 | 47.21 | 100%
[5 empty] | 47.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8212.8238 | 132591.3338 | 47.22 | 100%
[5 empty] | 47.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8215.0902 | 132627.9248 | 47.23 | 100%
[5 empty] | 47.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8217.3567 | 132664.5157 | 47.24 | 100%
[5 empty] | 47.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8219.6232 | 132701.1066 | 47.25 | 100%
[5 empty] | 47.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8221.8897 | 132737.6976 | 47.26 | 100%
[5 empty] | 47.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8224.1561 | 132774.2885 | 47.27 | 100%
[5 empty] | 47.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8226.4226 | 132810.8795 | 47.28 | 100%
[5 empty] | 47.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8228.6891 | 132847.4704 | 47.29 | 100%
[5 empty] | 47.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8230.9556 | 132884.0614 | 47.3 | 100%
[5 empty] | 47.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8233.222 | 132920.6523 | 47.31 | 100%
[5 empty] | 47.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8235.4885 | 132957.2432 | 47.32 | 100%
[5 empty] | 47.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8237.755 | 132993.8342 | 47.33 | 100%
[5 empty] | 47.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8240.0215 | 133030.4251 | 47.34 | 100%
[5 empty] | 47.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8242.2879 | 133067.0161 | 47.35 | 100%
[5 empty] | 47.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8244.5544 | 133103.607 | 47.36 | 100%
[5 empty] | 47.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8246.8209 | 133140.198 | 47.37 | 100%
[5 empty] | 47.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8249.0874 | 133176.7889 | 47.38 | 100%
[5 empty] | 47.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8251.3538 | 133213.3799 | 47.39 | 100%
[5 empty] | 47.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8253.6203 | 133249.9708 | 47.4 | 100%
[5 empty] | 47.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8255.8868 | 133286.5617 | 47.41 | 100%
[5 empty] | 47.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8258.1533 | 133323.1527 | 47.42 | 100%
[5 empty] | 47.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8260.4197 | 133359.7436 | 47.43 | 100%
[5 empty] | 47.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8262.6862 | 133396.3346 | 47.44 | 100%
[5 empty] | 47.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8264.9527 | 133432.9255 | 47.45 | 100%
[5 empty] | 47.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8267.2192 | 133469.5165 | 47.46 | 100%
[5 empty] | 47.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8269.4856 | 133506.1074 | 47.47 | 100%
[5 empty] | 47.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8271.7521 | 133542.6983 | 47.48 | 100%
[5 empty] | 47.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8274.0186 | 133579.2893 | 47.49 | 100%
[5 empty] | 47.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8276.2851 | 133615.8802 | 47.5 | 100%
[5 empty] | 47.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8278.5515 | 133652.4712 | 47.51 | 100%
[5 empty] | 47.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8280.818 | 133689.0621 | 47.52 | 100%
[5 empty] | 47.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8283.0845 | 133725.6531 | 47.53 | 100%
[5 empty] | 47.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8285.351 | 133762.244 | 47.54 | 100%
[5 empty] | 47.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8287.6174 | 133798.835 | 47.55 | 100%
[5 empty] | 47.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8289.8839 | 133835.4259 | 47.56 | 100%
[5 empty] | 47.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8292.1504 | 133872.0168 | 47.57 | 100%
[5 empty] | 47.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8294.4169 | 133908.6078 | 47.58 | 100%
[5 empty] | 47.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8296.6833 | 133945.1987 | 47.59 | 100%
[5 empty] | 47.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8298.9498 | 133981.7897 | 47.6 | 100%
[5 empty] | 47.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8301.2163 | 134018.3806 | 47.61 | 100%
[5 empty] | 47.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8303.4828 | 134054.9716 | 47.62 | 100%
[5 empty] | 47.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8305.7492 | 134091.5625 | 47.63 | 100%
[5 empty] | 47.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8308.0157 | 134128.1534 | 47.64 | 100%
[5 empty] | 47.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8310.2822 | 134164.7444 | 47.65 | 100%
[5 empty] | 47.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8312.5487 | 134201.3353 | 47.66 | 100%
[5 empty] | 47.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8314.8151 | 134237.9263 | 47.67 | 100%
[5 empty] | 47.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8317.0816 | 134274.5172 | 47.68 | 100%
[5 empty] | 47.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8319.3481 | 134311.1082 | 47.69 | 100%
[5 empty] | 47.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8321.6146 | 134347.6991 | 47.7 | 100%
[5 empty] | 47.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8323.881 | 134384.29 | 47.71 | 100%
[5 empty] | 47.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8326.1475 | 134420.881 | 47.72 | 100%
[5 empty] | 47.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8328.414 | 134457.4719 | 47.73 | 100%
[5 empty] | 47.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8330.6805 | 134494.0629 | 47.74 | 100%
[5 empty] | 47.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8332.9469 | 134530.6538 | 47.75 | 100%
[5 empty] | 47.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8335.2134 | 134567.2448 | 47.76 | 100%
[5 empty] | 47.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8337.4799 | 134603.8357 | 47.77 | 100%
[5 empty] | 47.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8339.7464 | 134640.4267 | 47.78 | 100%
[5 empty] | 47.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8342.0128 | 134677.0176 | 47.79 | 100%
[5 empty] | 47.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8344.2793 | 134713.6085 | 47.8 | 100%
[5 empty] | 47.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8346.5458 | 134750.1995 | 47.81 | 100%
[5 empty] | 47.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8348.8123 | 134786.7904 | 47.82 | 100%
[5 empty] | 47.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8351.0787 | 134823.3814 | 47.83 | 100%
[5 empty] | 47.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8353.3452 | 134859.9723 | 47.84 | 100%
[5 empty] | 47.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8355.6117 | 134896.5633 | 47.85 | 100%
[5 empty] | 47.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8357.8782 | 134933.1542 | 47.86 | 100%
[5 empty] | 47.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8360.1446 | 134969.7451 | 47.87 | 100%
[5 empty] | 47.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8362.4111 | 135006.3361 | 47.88 | 100%
[5 empty] | 47.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8364.6776 | 135042.927 | 47.89 | 100%
[5 empty] | 47.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8366.9441 | 135079.518 | 47.9 | 100%
[5 empty] | 47.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8369.2105 | 135116.1089 | 47.91 | 100%
[5 empty] | 47.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8371.477 | 135152.6999 | 47.92 | 100%
[5 empty] | 47.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8373.7435 | 135189.2908 | 47.93 | 100%
[5 empty] | 47.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8376.01 | 135225.8818 | 47.94 | 100%
[5 empty] | 47.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8378.2764 | 135262.4727 | 47.95 | 100%
[5 empty] | 47.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8380.5429 | 135299.0636 | 47.96 | 100%
[5 empty] | 47.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8382.8094 | 135335.6546 | 47.97 | 100%
[5 empty] | 47.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8385.0759 | 135372.2455 | 47.98 | 100%
[5 empty] | 47.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8387.3423 | 135408.8365 | 47.99 | 100%
[5 empty] | 48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8389.6088 | 135445.4274 | 48 | 100%
[5 empty] | 48.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8391.8753 | 135482.0184 | 48.01 | 100%
[5 empty] | 48.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8394.1418 | 135518.6093 | 48.02 | 100%
[5 empty] | 48.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8396.4082 | 135555.2002 | 48.03 | 100%
[5 empty] | 48.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8398.6747 | 135591.7912 | 48.04 | 100%
[5 empty] | 48.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8400.9412 | 135628.3821 | 48.05 | 100%
[5 empty] | 48.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8403.2077 | 135664.9731 | 48.06 | 100%
[5 empty] | 48.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8405.4741 | 135701.564 | 48.07 | 100%
[5 empty] | 48.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8407.7406 | 135738.155 | 48.08 | 100%
[5 empty] | 48.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8410.0071 | 135774.7459 | 48.09 | 100%
[5 empty] | 48.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8412.2736 | 135811.3368 | 48.1 | 100%
[5 empty] | 48.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8414.5401 | 135847.9278 | 48.11 | 100%
[5 empty] | 48.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8416.8065 | 135884.5187 | 48.12 | 100%
[5 empty] | 48.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8419.073 | 135921.1097 | 48.13 | 100%
[5 empty] | 48.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8421.3395 | 135957.7006 | 48.14 | 100%
[5 empty] | 48.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8423.606 | 135994.2916 | 48.15 | 100%
[5 empty] | 48.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8425.8724 | 136030.8825 | 48.16 | 100%
[5 empty] | 48.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8428.1389 | 136067.4735 | 48.17 | 100%
[5 empty] | 48.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8430.4054 | 136104.0644 | 48.18 | 100%
[5 empty] | 48.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8432.6719 | 136140.6553 | 48.19 | 100%
[5 empty] | 48.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8434.9383 | 136177.2463 | 48.2 | 100%
[5 empty] | 48.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8437.2048 | 136213.8372 | 48.21 | 100%
[5 empty] | 48.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8439.4713 | 136250.4282 | 48.22 | 100%
[5 empty] | 48.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8441.7378 | 136287.0191 | 48.23 | 100%
[5 empty] | 48.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8444.0042 | 136323.6101 | 48.24 | 100%
[5 empty] | 48.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8446.2707 | 136360.201 | 48.25 | 100%
[5 empty] | 48.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8448.5372 | 136396.7919 | 48.26 | 100%
[5 empty] | 48.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8450.8037 | 136433.3829 | 48.27 | 100%
[5 empty] | 48.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8453.0701 | 136469.9738 | 48.28 | 100%
[5 empty] | 48.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8455.3366 | 136506.5648 | 48.29 | 100%
[5 empty] | 48.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8457.6031 | 136543.1557 | 48.3 | 100%
[5 empty] | 48.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8459.8696 | 136579.7467 | 48.31 | 100%
[5 empty] | 48.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8462.136 | 136616.3376 | 48.32 | 100%
[5 empty] | 48.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8464.4025 | 136652.9286 | 48.33 | 100%
[5 empty] | 48.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8466.669 | 136689.5195 | 48.34 | 100%
[5 empty] | 48.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8468.9355 | 136726.1104 | 48.35 | 100%
[5 empty] | 48.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8471.2019 | 136762.7014 | 48.36 | 100%
[5 empty] | 48.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8473.4684 | 136799.2923 | 48.37 | 100%
[5 empty] | 48.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8475.7349 | 136835.8833 | 48.38 | 100%
[5 empty] | 48.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8478.0014 | 136872.4742 | 48.39 | 100%
[5 empty] | 48.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8480.2678 | 136909.0652 | 48.4 | 100%
[5 empty] | 48.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8482.5343 | 136945.6561 | 48.41 | 100%
[5 empty] | 48.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8484.8008 | 136982.247 | 48.42 | 100%
[5 empty] | 48.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8487.0673 | 137018.838 | 48.43 | 100%
[5 empty] | 48.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8489.3337 | 137055.4289 | 48.44 | 100%
[5 empty] | 48.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8491.6002 | 137092.0199 | 48.45 | 100%
[5 empty] | 48.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8493.8667 | 137128.6108 | 48.46 | 100%
[5 empty] | 48.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8496.1332 | 137165.2018 | 48.47 | 100%
[5 empty] | 48.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8498.3996 | 137201.7927 | 48.48 | 100%
[5 empty] | 48.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8500.6661 | 137238.3837 | 48.49 | 100%
[5 empty] | 48.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8502.9326 | 137274.9746 | 48.5 | 100%
[5 empty] | 48.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8505.1991 | 137311.5655 | 48.51 | 100%
[5 empty] | 48.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8507.4655 | 137348.1565 | 48.52 | 100%
[5 empty] | 48.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8509.732 | 137384.7474 | 48.53 | 100%
[5 empty] | 48.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8511.9985 | 137421.3384 | 48.54 | 100%
[5 empty] | 48.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8514.265 | 137457.9293 | 48.55 | 100%
[5 empty] | 48.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8516.5314 | 137494.5203 | 48.56 | 100%
[5 empty] | 48.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8518.7979 | 137531.1112 | 48.57 | 100%
[5 empty] | 48.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8521.0644 | 137567.7021 | 48.58 | 100%
[5 empty] | 48.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8523.3309 | 137604.2931 | 48.59 | 100%
[5 empty] | 48.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8525.5973 | 137640.884 | 48.6 | 100%
[5 empty] | 48.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8527.8638 | 137677.475 | 48.61 | 100%
[5 empty] | 48.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8530.1303 | 137714.0659 | 48.62 | 100%
[5 empty] | 48.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8532.3968 | 137750.6569 | 48.63 | 100%
[5 empty] | 48.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8534.6632 | 137787.2478 | 48.64 | 100%
[5 empty] | 48.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8536.9297 | 137823.8387 | 48.65 | 100%
[5 empty] | 48.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8539.1962 | 137860.4297 | 48.66 | 100%
[5 empty] | 48.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8541.4627 | 137897.0206 | 48.67 | 100%
[5 empty] | 48.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8543.7291 | 137933.6116 | 48.68 | 100%
[5 empty] | 48.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8545.9956 | 137970.2025 | 48.69 | 100%
[5 empty] | 48.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8548.2621 | 138006.7935 | 48.7 | 100%
[5 empty] | 48.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8550.5286 | 138043.3844 | 48.71 | 100%
[5 empty] | 48.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8552.795 | 138079.9754 | 48.72 | 100%
[5 empty] | 48.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8555.0615 | 138116.5663 | 48.73 | 100%
[5 empty] | 48.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8557.328 | 138153.1572 | 48.74 | 100%
[5 empty] | 48.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8559.5945 | 138189.7482 | 48.75 | 100%
[5 empty] | 48.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8561.8609 | 138226.3391 | 48.76 | 100%
[5 empty] | 48.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8564.1274 | 138262.9301 | 48.77 | 100%
[5 empty] | 48.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8566.3939 | 138299.521 | 48.78 | 100%
[5 empty] | 48.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8568.6604 | 138336.112 | 48.79 | 100%
[5 empty] | 48.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8570.9268 | 138372.7029 | 48.8 | 100%
[5 empty] | 48.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8573.1933 | 138409.2938 | 48.81 | 100%
[5 empty] | 48.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8575.4598 | 138445.8848 | 48.82 | 100%
[5 empty] | 48.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8577.7263 | 138482.4757 | 48.83 | 100%
[5 empty] | 48.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8579.9927 | 138519.0667 | 48.84 | 100%
[5 empty] | 48.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8582.2592 | 138555.6576 | 48.85 | 100%
[5 empty] | 48.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8584.5257 | 138592.2486 | 48.86 | 100%
[5 empty] | 48.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8586.7922 | 138628.8395 | 48.87 | 100%
[5 empty] | 48.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8589.0586 | 138665.4305 | 48.88 | 100%
[5 empty] | 48.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8591.3251 | 138702.0214 | 48.89 | 100%
[5 empty] | 48.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8593.5916 | 138738.6123 | 48.9 | 100%
[5 empty] | 48.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8595.8581 | 138775.2033 | 48.91 | 100%
[5 empty] | 48.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8598.1245 | 138811.7942 | 48.92 | 100%
[5 empty] | 48.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8600.391 | 138848.3852 | 48.93 | 100%
[5 empty] | 48.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8602.6575 | 138884.9761 | 48.94 | 100%
[5 empty] | 48.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8604.924 | 138921.5671 | 48.95 | 100%
[5 empty] | 48.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8607.1904 | 138958.158 | 48.96 | 100%
[5 empty] | 48.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8609.4569 | 138994.7489 | 48.97 | 100%
[5 empty] | 48.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8611.7234 | 139031.3399 | 48.98 | 100%
[5 empty] | 48.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8613.9899 | 139067.9308 | 48.99 | 100%
[5 empty] | 49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8616.2563 | 139104.5218 | 49 | 100%
[5 empty] | 49.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8618.5228 | 139141.1127 | 49.01 | 100%
[5 empty] | 49.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8620.7893 | 139177.7037 | 49.02 | 100%
[5 empty] | 49.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8623.0558 | 139214.2946 | 49.03 | 100%
[5 empty] | 49.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8625.3222 | 139250.8856 | 49.04 | 100%
[5 empty] | 49.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8627.5887 | 139287.4765 | 49.05 | 100%
[5 empty] | 49.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8629.8552 | 139324.0674 | 49.06 | 100%
[5 empty] | 49.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8632.1217 | 139360.6584 | 49.07 | 100%
[5 empty] | 49.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8634.3881 | 139397.2493 | 49.08 | 100%
[5 empty] | 49.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8636.6546 | 139433.8403 | 49.09 | 100%
[5 empty] | 49.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8638.9211 | 139470.4312 | 49.1 | 100%
[5 empty] | 49.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8641.1876 | 139507.0222 | 49.11 | 100%
[5 empty] | 49.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8643.454 | 139543.6131 | 49.12 | 100%
[5 empty] | 49.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8645.7205 | 139580.204 | 49.13 | 100%
[5 empty] | 49.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8647.987 | 139616.795 | 49.14 | 100%
[5 empty] | 49.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8650.2535 | 139653.3859 | 49.15 | 100%
[5 empty] | 49.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8652.5199 | 139689.9769 | 49.16 | 100%
[5 empty] | 49.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8654.7864 | 139726.5678 | 49.17 | 100%
[5 empty] | 49.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8657.0529 | 139763.1588 | 49.18 | 100%
[5 empty] | 49.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8659.3194 | 139799.7497 | 49.19 | 100%
[5 empty] | 49.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8661.5858 | 139836.3406 | 49.2 | 100%
[5 empty] | 49.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8663.8523 | 139872.9316 | 49.21 | 100%
[5 empty] | 49.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8666.1188 | 139909.5225 | 49.22 | 100%
[5 empty] | 49.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8668.3853 | 139946.1135 | 49.23 | 100%
[5 empty] | 49.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8670.6517 | 139982.7044 | 49.24 | 100%
[5 empty] | 49.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8672.9182 | 140019.2954 | 49.25 | 100%
[5 empty] | 49.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8675.1847 | 140055.8863 | 49.26 | 100%
[5 empty] | 49.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8677.4512 | 140092.4773 | 49.27 | 100%
[5 empty] | 49.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8679.7176 | 140129.0682 | 49.28 | 100%
[5 empty] | 49.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8681.9841 | 140165.6591 | 49.29 | 100%
[5 empty] | 49.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8684.2506 | 140202.2501 | 49.3 | 100%
[5 empty] | 49.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8686.5171 | 140238.841 | 49.31 | 100%
[5 empty] | 49.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8688.7836 | 140275.432 | 49.32 | 100%
[5 empty] | 49.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8691.05 | 140312.0229 | 49.33 | 100%
[5 empty] | 49.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8693.3165 | 140348.6139 | 49.34 | 100%
[5 empty] | 49.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8695.583 | 140385.2048 | 49.35 | 100%
[5 empty] | 49.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8697.8495 | 140421.7957 | 49.36 | 100%
[5 empty] | 49.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8700.1159 | 140458.3867 | 49.37 | 100%
[5 empty] | 49.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8702.3824 | 140494.9776 | 49.38 | 100%
[5 empty] | 49.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8704.6489 | 140531.5686 | 49.39 | 100%
[5 empty] | 49.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8706.9154 | 140568.1595 | 49.4 | 100%
[5 empty] | 49.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8709.1818 | 140604.7505 | 49.41 | 100%
[5 empty] | 49.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8711.4483 | 140641.3414 | 49.42 | 100%
[5 empty] | 49.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8713.7148 | 140677.9324 | 49.43 | 100%
[5 empty] | 49.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8715.9813 | 140714.5233 | 49.44 | 100%
[5 empty] | 49.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8718.2477 | 140751.1142 | 49.45 | 100%
[5 empty] | 49.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8720.5142 | 140787.7052 | 49.46 | 100%
[5 empty] | 49.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8722.7807 | 140824.2961 | 49.47 | 100%
[5 empty] | 49.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8725.0472 | 140860.8871 | 49.48 | 100%
[5 empty] | 49.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8727.3136 | 140897.478 | 49.49 | 100%
[5 empty] | 49.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8729.5801 | 140934.069 | 49.5 | 100%
[5 empty] | 49.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8731.8466 | 140970.6599 | 49.51 | 100%
[5 empty] | 49.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8734.1131 | 141007.2508 | 49.52 | 100%
[5 empty] | 49.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8736.3795 | 141043.8418 | 49.53 | 100%
[5 empty] | 49.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8738.646 | 141080.4327 | 49.54 | 100%
[5 empty] | 49.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8740.9125 | 141117.0237 | 49.55 | 100%
[5 empty] | 49.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8743.179 | 141153.6146 | 49.56 | 100%
[5 empty] | 49.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8745.4454 | 141190.2056 | 49.57 | 100%
[5 empty] | 49.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8747.7119 | 141226.7965 | 49.58 | 100%
[5 empty] | 49.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8749.9784 | 141263.3875 | 49.59 | 100%
[5 empty] | 49.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8752.2449 | 141299.9784 | 49.6 | 100%
[5 empty] | 49.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8754.5113 | 141336.5693 | 49.61 | 100%
[5 empty] | 49.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8756.7778 | 141373.1603 | 49.62 | 100%
[5 empty] | 49.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8759.0443 | 141409.7512 | 49.63 | 100%
[5 empty] | 49.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8761.3108 | 141446.3422 | 49.64 | 100%
[5 empty] | 49.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8763.5772 | 141482.9331 | 49.65 | 100%
[5 empty] | 49.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8765.8437 | 141519.5241 | 49.66 | 100%
[5 empty] | 49.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8768.1102 | 141556.115 | 49.67 | 100%
[5 empty] | 49.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8770.3767 | 141592.7059 | 49.68 | 100%
[5 empty] | 49.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8772.6431 | 141629.2969 | 49.69 | 100%
[5 empty] | 49.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8774.9096 | 141665.8878 | 49.7 | 100%
[5 empty] | 49.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8777.1761 | 141702.4788 | 49.71 | 100%
[5 empty] | 49.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8779.4426 | 141739.0697 | 49.72 | 100%
[5 empty] | 49.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8781.709 | 141775.6607 | 49.73 | 100%
[5 empty] | 49.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8783.9755 | 141812.2516 | 49.74 | 100%
[5 empty] | 49.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8786.242 | 141848.8425 | 49.75 | 100%
[5 empty] | 49.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8788.5085 | 141885.4335 | 49.76 | 100%
[5 empty] | 49.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8790.7749 | 141922.0244 | 49.77 | 100%
[5 empty] | 49.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8793.0414 | 141958.6154 | 49.78 | 100%
[5 empty] | 49.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8795.3079 | 141995.2063 | 49.79 | 100%
[5 empty] | 49.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8797.5744 | 142031.7973 | 49.8 | 100%
[5 empty] | 49.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8799.8408 | 142068.3882 | 49.81 | 100%
[5 empty] | 49.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8802.1073 | 142104.9792 | 49.82 | 100%
[5 empty] | 49.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8804.3738 | 142141.5701 | 49.83 | 100%
[5 empty] | 49.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8806.6403 | 142178.161 | 49.84 | 100%
[5 empty] | 49.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8808.9067 | 142214.752 | 49.85 | 100%
[5 empty] | 49.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8811.1732 | 142251.3429 | 49.86 | 100%
[5 empty] | 49.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8813.4397 | 142287.9339 | 49.87 | 100%
[5 empty] | 49.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8815.7062 | 142324.5248 | 49.88 | 100%
[5 empty] | 49.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8817.9726 | 142361.1158 | 49.89 | 100%
[5 empty] | 49.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8820.2391 | 142397.7067 | 49.9 | 100%
[5 empty] | 49.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8822.5056 | 142434.2976 | 49.91 | 100%
[5 empty] | 49.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8824.7721 | 142470.8886 | 49.92 | 100%
[5 empty] | 49.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8827.0385 | 142507.4795 | 49.93 | 100%
[5 empty] | 49.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8829.305 | 142544.0705 | 49.94 | 100%
[5 empty] | 49.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8831.5715 | 142580.6614 | 49.95 | 100%
[5 empty] | 49.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8833.838 | 142617.2524 | 49.96 | 100%
[5 empty] | 49.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8836.1044 | 142653.8433 | 49.97 | 100%
[5 empty] | 49.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8838.3709 | 142690.4343 | 49.98 | 100%
[5 empty] | 49.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8840.6374 | 142727.0252 | 49.99 | 100%
[5 empty] | 50 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8842.9039 | 142763.6161 | 50 | 100%
[5 empty] | 50.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8845.1703 | 142800.2071 | 50.01 | 100%
[5 empty] | 50.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8847.4368 | 142836.798 | 50.02 | 100%
[5 empty] | 50.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8849.7033 | 142873.389 | 50.03 | 100%
[5 empty] | 50.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8851.9698 | 142909.9799 | 50.04 | 100%
[5 empty] | 50.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8854.2362 | 142946.5709 | 50.05 | 100%
[5 empty] | 50.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8856.5027 | 142983.1618 | 50.06 | 100%
[5 empty] | 50.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8858.7692 | 143019.7527 | 50.07 | 100%
[5 empty] | 50.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8861.0357 | 143056.3437 | 50.08 | 100%
[5 empty] | 50.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8863.3021 | 143092.9346 | 50.09 | 100%
[5 empty] | 50.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8865.5686 | 143129.5256 | 50.1 | 100%
[5 empty] | 50.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8867.8351 | 143166.1165 | 50.11 | 100%
[5 empty] | 50.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8870.1016 | 143202.7075 | 50.12 | 100%
[5 empty] | 50.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8872.368 | 143239.2984 | 50.13 | 100%
[5 empty] | 50.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8874.6345 | 143275.8893 | 50.14 | 100%
[5 empty] | 50.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8876.901 | 143312.4803 | 50.15 | 100%
[5 empty] | 50.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8879.1675 | 143349.0712 | 50.16 | 100%
[5 empty] | 50.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8881.4339 | 143385.6622 | 50.17 | 100%
[5 empty] | 50.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8883.7004 | 143422.2531 | 50.18 | 100%
[5 empty] | 50.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8885.9669 | 143458.8441 | 50.19 | 100%
[5 empty] | 50.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8888.2334 | 143495.435 | 50.2 | 100%
[5 empty] | 50.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8890.4998 | 143532.026 | 50.21 | 100%
[5 empty] | 50.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8892.7663 | 143568.6169 | 50.22 | 100%
[5 empty] | 50.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8895.0328 | 143605.2078 | 50.23 | 100%
[5 empty] | 50.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8897.2993 | 143641.7988 | 50.24 | 100%
[5 empty] | 50.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8899.5657 | 143678.3897 | 50.25 | 100%
[5 empty] | 50.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8901.8322 | 143714.9807 | 50.26 | 100%
[5 empty] | 50.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8904.0987 | 143751.5716 | 50.27 | 100%
[5 empty] | 50.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8906.3652 | 143788.1626 | 50.28 | 100%
[5 empty] | 50.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8908.6316 | 143824.7535 | 50.29 | 100%
[5 empty] | 50.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8910.8981 | 143861.3444 | 50.3 | 100%
[5 empty] | 50.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8913.1646 | 143897.9354 | 50.31 | 100%
[5 empty] | 50.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8915.4311 | 143934.5263 | 50.32 | 100%
[5 empty] | 50.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8917.6975 | 143971.1173 | 50.33 | 100%
[5 empty] | 50.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8919.964 | 144007.7082 | 50.34 | 100%
[5 empty] | 50.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8922.2305 | 144044.2992 | 50.35 | 100%
[5 empty] | 50.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8924.497 | 144080.8901 | 50.36 | 100%
[5 empty] | 50.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8926.7634 | 144117.4811 | 50.37 | 100%
[5 empty] | 50.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8929.0299 | 144154.072 | 50.38 | 100%
[5 empty] | 50.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8931.2964 | 144190.6629 | 50.39 | 100%
[5 empty] | 50.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8933.5629 | 144227.2539 | 50.4 | 100%
[5 empty] | 50.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8935.8293 | 144263.8448 | 50.41 | 100%
[5 empty] | 50.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8938.0958 | 144300.4358 | 50.42 | 100%
[5 empty] | 50.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8940.3623 | 144337.0267 | 50.43 | 100%
[5 empty] | 50.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8942.6288 | 144373.6177 | 50.44 | 100%
[5 empty] | 50.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8944.8952 | 144410.2086 | 50.45 | 100%
[5 empty] | 50.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8947.1617 | 144446.7995 | 50.46 | 100%
[5 empty] | 50.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8949.4282 | 144483.3905 | 50.47 | 100%
[5 empty] | 50.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8951.6947 | 144519.9814 | 50.48 | 100%
[5 empty] | 50.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8953.9612 | 144556.5724 | 50.49 | 100%
[5 empty] | 50.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8956.2276 | 144593.1633 | 50.5 | 100%
[5 empty] | 50.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8958.4941 | 144629.7543 | 50.51 | 100%
[5 empty] | 50.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8960.7606 | 144666.3452 | 50.52 | 100%
[5 empty] | 50.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8963.0271 | 144702.9362 | 50.53 | 100%
[5 empty] | 50.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8965.2935 | 144739.5271 | 50.54 | 100%
[5 empty] | 50.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8967.56 | 144776.118 | 50.55 | 100%
[5 empty] | 50.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8969.8265 | 144812.709 | 50.56 | 100%
[5 empty] | 50.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8972.093 | 144849.2999 | 50.57 | 100%
[5 empty] | 50.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8974.3594 | 144885.8909 | 50.58 | 100%
[5 empty] | 50.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8976.6259 | 144922.4818 | 50.59 | 100%
[5 empty] | 50.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8978.8924 | 144959.0728 | 50.6 | 100%
[5 empty] | 50.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8981.1589 | 144995.6637 | 50.61 | 100%
[5 empty] | 50.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8983.4253 | 145032.2546 | 50.62 | 100%
[5 empty] | 50.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8985.6918 | 145068.8456 | 50.63 | 100%
[5 empty] | 50.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8987.9583 | 145105.4365 | 50.64 | 100%
[5 empty] | 50.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8990.2248 | 145142.0275 | 50.65 | 100%
[5 empty] | 50.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8992.4912 | 145178.6184 | 50.66 | 100%
[5 empty] | 50.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8994.7577 | 145215.2094 | 50.67 | 100%
[5 empty] | 50.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8997.0242 | 145251.8003 | 50.68 | 100%
[5 empty] | 50.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 8999.2907 | 145288.3912 | 50.69 | 100%
[5 empty] | 50.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9001.5571 | 145324.9822 | 50.7 | 100%
[5 empty] | 50.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9003.8236 | 145361.5731 | 50.71 | 100%
[5 empty] | 50.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9006.0901 | 145398.1641 | 50.72 | 100%
[5 empty] | 50.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9008.3566 | 145434.755 | 50.73 | 100%
[5 empty] | 50.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9010.623 | 145471.346 | 50.74 | 100%
[5 empty] | 50.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9012.8895 | 145507.9369 | 50.75 | 100%
[5 empty] | 50.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9015.156 | 145544.5279 | 50.76 | 100%
[5 empty] | 50.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9017.4225 | 145581.1188 | 50.77 | 100%
[5 empty] | 50.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9019.6889 | 145617.7097 | 50.78 | 100%
[5 empty] | 50.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9021.9554 | 145654.3007 | 50.79 | 100%
[5 empty] | 50.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9024.2219 | 145690.8916 | 50.8 | 100%
[5 empty] | 50.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9026.4884 | 145727.4826 | 50.81 | 100%
[5 empty] | 50.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9028.7548 | 145764.0735 | 50.82 | 100%
[5 empty] | 50.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9031.0213 | 145800.6645 | 50.83 | 100%
[5 empty] | 50.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9033.2878 | 145837.2554 | 50.84 | 100%
[5 empty] | 50.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9035.5543 | 145873.8463 | 50.85 | 100%
[5 empty] | 50.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9037.8207 | 145910.4373 | 50.86 | 100%
[5 empty] | 50.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9040.0872 | 145947.0282 | 50.87 | 100%
[5 empty] | 50.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9042.3537 | 145983.6192 | 50.88 | 100%
[5 empty] | 50.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9044.6202 | 146020.2101 | 50.89 | 100%
[5 empty] | 50.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9046.8866 | 146056.8011 | 50.9 | 100%
[5 empty] | 50.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9049.1531 | 146093.392 | 50.91 | 100%
[5 empty] | 50.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9051.4196 | 146129.983 | 50.92 | 100%
[5 empty] | 50.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9053.6861 | 146166.5739 | 50.93 | 100%
[5 empty] | 50.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9055.9525 | 146203.1648 | 50.94 | 100%
[5 empty] | 50.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9058.219 | 146239.7558 | 50.95 | 100%
[5 empty] | 50.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9060.4855 | 146276.3467 | 50.96 | 100%
[5 empty] | 50.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9062.752 | 146312.9377 | 50.97 | 100%
[5 empty] | 50.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9065.0184 | 146349.5286 | 50.98 | 100%
[5 empty] | 50.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9067.2849 | 146386.1196 | 50.99 | 100%
[5 empty] | 51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9069.5514 | 146422.7105 | 51 | 100%
[5 empty] | 51.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9071.8179 | 146459.3014 | 51.01 | 100%
[5 empty] | 51.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9074.0843 | 146495.8924 | 51.02 | 100%
[5 empty] | 51.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9076.3508 | 146532.4833 | 51.03 | 100%
[5 empty] | 51.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9078.6173 | 146569.0743 | 51.04 | 100%
[5 empty] | 51.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9080.8838 | 146605.6652 | 51.05 | 100%
[5 empty] | 51.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9083.1502 | 146642.2562 | 51.06 | 100%
[5 empty] | 51.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9085.4167 | 146678.8471 | 51.07 | 100%
[5 empty] | 51.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9087.6832 | 146715.4381 | 51.08 | 100%
[5 empty] | 51.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9089.9497 | 146752.029 | 51.09 | 100%
[5 empty] | 51.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9092.2161 | 146788.6199 | 51.1 | 100%
[5 empty] | 51.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9094.4826 | 146825.2109 | 51.11 | 100%
[5 empty] | 51.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9096.7491 | 146861.8018 | 51.12 | 100%
[5 empty] | 51.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9099.0156 | 146898.3928 | 51.13 | 100%
[5 empty] | 51.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9101.282 | 146934.9837 | 51.14 | 100%
[5 empty] | 51.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9103.5485 | 146971.5747 | 51.15 | 100%
[5 empty] | 51.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9105.815 | 147008.1656 | 51.16 | 100%
[5 empty] | 51.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9108.0815 | 147044.7565 | 51.17 | 100%
[5 empty] | 51.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9110.3479 | 147081.3475 | 51.18 | 100%
[5 empty] | 51.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9112.6144 | 147117.9384 | 51.19 | 100%
[5 empty] | 51.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9114.8809 | 147154.5294 | 51.2 | 100%
[5 empty] | 51.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9117.1474 | 147191.1203 | 51.21 | 100%
[5 empty] | 51.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9119.4138 | 147227.7113 | 51.22 | 100%
[5 empty] | 51.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9121.6803 | 147264.3022 | 51.23 | 100%
[5 empty] | 51.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9123.9468 | 147300.8931 | 51.24 | 100%
[5 empty] | 51.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9126.2133 | 147337.4841 | 51.25 | 100%
[5 empty] | 51.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9128.4797 | 147374.075 | 51.26 | 100%
[5 empty] | 51.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9130.7462 | 147410.666 | 51.27 | 100%
[5 empty] | 51.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9133.0127 | 147447.2569 | 51.28 | 100%
[5 empty] | 51.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9135.2792 | 147483.8479 | 51.29 | 100%
[5 empty] | 51.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9137.5456 | 147520.4388 | 51.3 | 100%
[5 empty] | 51.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9139.8121 | 147557.0298 | 51.31 | 100%
[5 empty] | 51.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9142.0786 | 147593.6207 | 51.32 | 100%
[5 empty] | 51.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9144.3451 | 147630.2116 | 51.33 | 100%
[5 empty] | 51.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9146.6115 | 147666.8026 | 51.34 | 100%
[5 empty] | 51.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9148.878 | 147703.3935 | 51.35 | 100%
[5 empty] | 51.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9151.1445 | 147739.9845 | 51.36 | 100%
[5 empty] | 51.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9153.411 | 147776.5754 | 51.37 | 100%
[5 empty] | 51.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9155.6774 | 147813.1664 | 51.38 | 100%
[5 empty] | 51.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9157.9439 | 147849.7573 | 51.39 | 100%
[5 empty] | 51.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9160.2104 | 147886.3482 | 51.4 | 100%
[5 empty] | 51.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9162.4769 | 147922.9392 | 51.41 | 100%
[5 empty] | 51.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9164.7433 | 147959.5301 | 51.42 | 100%
[5 empty] | 51.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9167.0098 | 147996.1211 | 51.43 | 100%
[5 empty] | 51.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9169.2763 | 148032.712 | 51.44 | 100%
[5 empty] | 51.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9171.5428 | 148069.303 | 51.45 | 100%
[5 empty] | 51.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9173.8092 | 148105.8939 | 51.46 | 100%
[5 empty] | 51.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9176.0757 | 148142.4849 | 51.47 | 100%
[5 empty] | 51.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9178.3422 | 148179.0758 | 51.48 | 100%
[5 empty] | 51.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9180.6087 | 148215.6667 | 51.49 | 100%
[5 empty] | 51.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9182.8751 | 148252.2577 | 51.5 | 100%
[5 empty] | 51.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9185.1416 | 148288.8486 | 51.51 | 100%
[5 empty] | 51.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9187.4081 | 148325.4396 | 51.52 | 100%
[5 empty] | 51.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9189.6746 | 148362.0305 | 51.53 | 100%
[5 empty] | 51.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9191.941 | 148398.6215 | 51.54 | 100%
[5 empty] | 51.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9194.2075 | 148435.2124 | 51.55 | 100%
[5 empty] | 51.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9196.474 | 148471.8033 | 51.56 | 100%
[5 empty] | 51.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9198.7405 | 148508.3943 | 51.57 | 100%
[5 empty] | 51.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9201.0069 | 148544.9852 | 51.58 | 100%
[5 empty] | 51.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9203.2734 | 148581.5762 | 51.59 | 100%
[5 empty] | 51.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9205.5399 | 148618.1671 | 51.6 | 100%
[5 empty] | 51.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9207.8064 | 148654.7581 | 51.61 | 100%
[5 empty] | 51.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9210.0728 | 148691.349 | 51.62 | 100%
[5 empty] | 51.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9212.3393 | 148727.9399 | 51.63 | 100%
[5 empty] | 51.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9214.6058 | 148764.5309 | 51.64 | 100%
[5 empty] | 51.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9216.8723 | 148801.1218 | 51.65 | 100%
[5 empty] | 51.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9219.1387 | 148837.7128 | 51.66 | 100%
[5 empty] | 51.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9221.4052 | 148874.3037 | 51.67 | 100%
[5 empty] | 51.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9223.6717 | 148910.8947 | 51.68 | 100%
[5 empty] | 51.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9225.9382 | 148947.4856 | 51.69 | 100%
[5 empty] | 51.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9228.2047 | 148984.0766 | 51.7 | 100%
[5 empty] | 51.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9230.4711 | 149020.6675 | 51.71 | 100%
[5 empty] | 51.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9232.7376 | 149057.2584 | 51.72 | 100%
[5 empty] | 51.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9235.0041 | 149093.8494 | 51.73 | 100%
[5 empty] | 51.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9237.2706 | 149130.4403 | 51.74 | 100%
[5 empty] | 51.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9239.537 | 149167.0313 | 51.75 | 100%
[5 empty] | 51.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9241.8035 | 149203.6222 | 51.76 | 100%
[5 empty] | 51.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9244.07 | 149240.2132 | 51.77 | 100%
[5 empty] | 51.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9246.3365 | 149276.8041 | 51.78 | 100%
[5 empty] | 51.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9248.6029 | 149313.395 | 51.79 | 100%
[5 empty] | 51.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9250.8694 | 149349.986 | 51.8 | 100%
[5 empty] | 51.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9253.1359 | 149386.5769 | 51.81 | 100%
[5 empty] | 51.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9255.4024 | 149423.1679 | 51.82 | 100%
[5 empty] | 51.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9257.6688 | 149459.7588 | 51.83 | 100%
[5 empty] | 51.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9259.9353 | 149496.3498 | 51.84 | 100%
[5 empty] | 51.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9262.2018 | 149532.9407 | 51.85 | 100%
[5 empty] | 51.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9264.4683 | 149569.5317 | 51.86 | 100%
[5 empty] | 51.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9266.7347 | 149606.1226 | 51.87 | 100%
[5 empty] | 51.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9269.0012 | 149642.7135 | 51.88 | 100%
[5 empty] | 51.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9271.2677 | 149679.3045 | 51.89 | 100%
[5 empty] | 51.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9273.5342 | 149715.8954 | 51.9 | 100%
[5 empty] | 51.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9275.8006 | 149752.4864 | 51.91 | 100%
[5 empty] | 51.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9278.0671 | 149789.0773 | 51.92 | 100%
[5 empty] | 51.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9280.3336 | 149825.6683 | 51.93 | 100%
[5 empty] | 51.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9282.6001 | 149862.2592 | 51.94 | 100%
[5 empty] | 51.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9284.8665 | 149898.8501 | 51.95 | 100%
[5 empty] | 51.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9287.133 | 149935.4411 | 51.96 | 100%
[5 empty] | 51.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9289.3995 | 149972.032 | 51.97 | 100%
[5 empty] | 51.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9291.666 | 150008.623 | 51.98 | 100%
[5 empty] | 51.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9293.9324 | 150045.2139 | 51.99 | 100%
[5 empty] | 52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9296.1989 | 150081.8049 | 52 | 100%
[5 empty] | 52.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9298.4654 | 150118.3958 | 52.01 | 100%
[5 empty] | 52.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9300.7319 | 150154.9868 | 52.02 | 100%
[5 empty] | 52.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9302.9983 | 150191.5777 | 52.03 | 100%
[5 empty] | 52.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9305.2648 | 150228.1686 | 52.04 | 100%
[5 empty] | 52.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9307.5313 | 150264.7596 | 52.05 | 100%
[5 empty] | 52.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9309.7978 | 150301.3505 | 52.06 | 100%
[5 empty] | 52.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9312.0642 | 150337.9415 | 52.07 | 100%
[5 empty] | 52.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9314.3307 | 150374.5324 | 52.08 | 100%
[5 empty] | 52.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9316.5972 | 150411.1234 | 52.09 | 100%
[5 empty] | 52.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9318.8637 | 150447.7143 | 52.1 | 100%
[5 empty] | 52.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9321.1301 | 150484.3052 | 52.11 | 100%
[5 empty] | 52.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9323.3966 | 150520.8962 | 52.12 | 100%
[5 empty] | 52.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9325.6631 | 150557.4871 | 52.13 | 100%
[5 empty] | 52.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9327.9296 | 150594.0781 | 52.14 | 100%
[5 empty] | 52.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9330.196 | 150630.669 | 52.15 | 100%
[5 empty] | 52.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9332.4625 | 150667.26 | 52.16 | 100%
[5 empty] | 52.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9334.729 | 150703.8509 | 52.17 | 100%
[5 empty] | 52.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9336.9955 | 150740.4418 | 52.18 | 100%
[5 empty] | 52.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9339.2619 | 150777.0328 | 52.19 | 100%
[5 empty] | 52.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9341.5284 | 150813.6237 | 52.2 | 100%
[5 empty] | 52.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9343.7949 | 150850.2147 | 52.21 | 100%
[5 empty] | 52.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9346.0614 | 150886.8056 | 52.22 | 100%
[5 empty] | 52.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9348.3278 | 150923.3966 | 52.23 | 100%
[5 empty] | 52.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9350.5943 | 150959.9875 | 52.24 | 100%
[5 empty] | 52.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9352.8608 | 150996.5785 | 52.25 | 100%
[5 empty] | 52.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9355.1273 | 151033.1694 | 52.26 | 100%
[5 empty] | 52.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9357.3937 | 151069.7603 | 52.27 | 100%
[5 empty] | 52.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9359.6602 | 151106.3513 | 52.28 | 100%
[5 empty] | 52.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9361.9267 | 151142.9422 | 52.29 | 100%
[5 empty] | 52.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9364.1932 | 151179.5332 | 52.3 | 100%
[5 empty] | 52.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9366.4596 | 151216.1241 | 52.31 | 100%
[5 empty] | 52.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9368.7261 | 151252.7151 | 52.32 | 100%
[5 empty] | 52.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9370.9926 | 151289.306 | 52.33 | 100%
[5 empty] | 52.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9373.2591 | 151325.8969 | 52.34 | 100%
[5 empty] | 52.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9375.5255 | 151362.4879 | 52.35 | 100%
[5 empty] | 52.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9377.792 | 151399.0788 | 52.36 | 100%
[5 empty] | 52.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9380.0585 | 151435.6698 | 52.37 | 100%
[5 empty] | 52.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9382.325 | 151472.2607 | 52.38 | 100%
[5 empty] | 52.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9384.5914 | 151508.8517 | 52.39 | 100%
[5 empty] | 52.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9386.8579 | 151545.4426 | 52.4 | 100%
[5 empty] | 52.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9389.1244 | 151582.0336 | 52.41 | 100%
[5 empty] | 52.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9391.3909 | 151618.6245 | 52.42 | 100%
[5 empty] | 52.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9393.6573 | 151655.2154 | 52.43 | 100%
[5 empty] | 52.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9395.9238 | 151691.8064 | 52.44 | 100%
[5 empty] | 52.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9398.1903 | 151728.3973 | 52.45 | 100%
[5 empty] | 52.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9400.4568 | 151764.9883 | 52.46 | 100%
[5 empty] | 52.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9402.7232 | 151801.5792 | 52.47 | 100%
[5 empty] | 52.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9404.9897 | 151838.1702 | 52.48 | 100%
[5 empty] | 52.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9407.2562 | 151874.7611 | 52.49 | 100%
[5 empty] | 52.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9409.5227 | 151911.352 | 52.5 | 100%
[5 empty] | 52.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9411.7891 | 151947.943 | 52.51 | 100%
[5 empty] | 52.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9414.0556 | 151984.5339 | 52.52 | 100%
[5 empty] | 52.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9416.3221 | 152021.1249 | 52.53 | 100%
[5 empty] | 52.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9418.5886 | 152057.7158 | 52.54 | 100%
[5 empty] | 52.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9420.855 | 152094.3068 | 52.55 | 100%
[5 empty] | 52.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9423.1215 | 152130.8977 | 52.56 | 100%
[5 empty] | 52.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9425.388 | 152167.4887 | 52.57 | 100%
[5 empty] | 52.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9427.6545 | 152204.0796 | 52.58 | 100%
[5 empty] | 52.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9429.9209 | 152240.6705 | 52.59 | 100%
[5 empty] | 52.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9432.1874 | 152277.2615 | 52.6 | 100%
[5 empty] | 52.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9434.4539 | 152313.8524 | 52.61 | 100%
[5 empty] | 52.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9436.7204 | 152350.4434 | 52.62 | 100%
[5 empty] | 52.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9438.9868 | 152387.0343 | 52.63 | 100%
[5 empty] | 52.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9441.2533 | 152423.6253 | 52.64 | 100%
[5 empty] | 52.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9443.5198 | 152460.2162 | 52.65 | 100%
[5 empty] | 52.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9445.7863 | 152496.8071 | 52.66 | 100%
[5 empty] | 52.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9448.0527 | 152533.3981 | 52.67 | 100%
[5 empty] | 52.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9450.3192 | 152569.989 | 52.68 | 100%
[5 empty] | 52.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9452.5857 | 152606.58 | 52.69 | 100%
[5 empty] | 52.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9454.8522 | 152643.1709 | 52.7 | 100%
[5 empty] | 52.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9457.1186 | 152679.7619 | 52.71 | 100%
[5 empty] | 52.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9459.3851 | 152716.3528 | 52.72 | 100%
[5 empty] | 52.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9461.6516 | 152752.9437 | 52.73 | 100%
[5 empty] | 52.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9463.9181 | 152789.5347 | 52.74 | 100%
[5 empty] | 52.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9466.1845 | 152826.1256 | 52.75 | 100%
[5 empty] | 52.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9468.451 | 152862.7166 | 52.76 | 100%
[5 empty] | 52.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9470.7175 | 152899.3075 | 52.77 | 100%
[5 empty] | 52.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9472.984 | 152935.8985 | 52.78 | 100%
[5 empty] | 52.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9475.2504 | 152972.4894 | 52.79 | 100%
[5 empty] | 52.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9477.5169 | 153009.0804 | 52.8 | 100%
[5 empty] | 52.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9479.7834 | 153045.6713 | 52.81 | 100%
[5 empty] | 52.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9482.0499 | 153082.2622 | 52.82 | 100%
[5 empty] | 52.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9484.3163 | 153118.8532 | 52.83 | 100%
[5 empty] | 52.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9486.5828 | 153155.4441 | 52.84 | 100%
[5 empty] | 52.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9488.8493 | 153192.0351 | 52.85 | 100%
[5 empty] | 52.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9491.1158 | 153228.626 | 52.86 | 100%
[5 empty] | 52.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9493.3823 | 153265.217 | 52.87 | 100%
[5 empty] | 52.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9495.6487 | 153301.8079 | 52.88 | 100%
[5 empty] | 52.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9497.9152 | 153338.3988 | 52.89 | 100%
[5 empty] | 52.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9500.1817 | 153374.9898 | 52.9 | 100%
[5 empty] | 52.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9502.4482 | 153411.5807 | 52.91 | 100%
[5 empty] | 52.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9504.7146 | 153448.1717 | 52.92 | 100%
[5 empty] | 52.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9506.9811 | 153484.7626 | 52.93 | 100%
[5 empty] | 52.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9509.2476 | 153521.3536 | 52.94 | 100%
[5 empty] | 52.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9511.5141 | 153557.9445 | 52.95 | 100%
[5 empty] | 52.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9513.7805 | 153594.5355 | 52.96 | 100%
[5 empty] | 52.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9516.047 | 153631.1264 | 52.97 | 100%
[5 empty] | 52.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9518.3135 | 153667.7173 | 52.98 | 100%
[5 empty] | 52.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9520.58 | 153704.3083 | 52.99 | 100%
[5 empty] | 53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9522.8464 | 153740.8992 | 53 | 100%
[5 empty] | 53.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9525.1129 | 153777.4902 | 53.01 | 100%
[5 empty] | 53.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9527.3794 | 153814.0811 | 53.02 | 100%
[5 empty] | 53.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9529.6459 | 153850.6721 | 53.03 | 100%
[5 empty] | 53.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9531.9123 | 153887.263 | 53.04 | 100%
[5 empty] | 53.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9534.1788 | 153923.8539 | 53.05 | 100%
[5 empty] | 53.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9536.4453 | 153960.4449 | 53.06 | 100%
[5 empty] | 53.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9538.7118 | 153997.0358 | 53.07 | 100%
[5 empty] | 53.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9540.9782 | 154033.6268 | 53.08 | 100%
[5 empty] | 53.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9543.2447 | 154070.2177 | 53.09 | 100%
[5 empty] | 53.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9545.5112 | 154106.8087 | 53.1 | 100%
[5 empty] | 53.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9547.7777 | 154143.3996 | 53.11 | 100%
[5 empty] | 53.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9550.0441 | 154179.9906 | 53.12 | 100%
[5 empty] | 53.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9552.3106 | 154216.5815 | 53.13 | 100%
[5 empty] | 53.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9554.5771 | 154253.1724 | 53.14 | 100%
[5 empty] | 53.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9556.8436 | 154289.7634 | 53.15 | 100%
[5 empty] | 53.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9559.11 | 154326.3543 | 53.16 | 100%
[5 empty] | 53.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9561.3765 | 154362.9453 | 53.17 | 100%
[5 empty] | 53.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9563.643 | 154399.5362 | 53.18 | 100%
[5 empty] | 53.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9565.9095 | 154436.1272 | 53.19 | 100%
[5 empty] | 53.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9568.1759 | 154472.7181 | 53.2 | 100%
[5 empty] | 53.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9570.4424 | 154509.309 | 53.21 | 100%
[5 empty] | 53.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9572.7089 | 154545.9 | 53.22 | 100%
[5 empty] | 53.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9574.9754 | 154582.4909 | 53.23 | 100%
[5 empty] | 53.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9577.2418 | 154619.0819 | 53.24 | 100%
[5 empty] | 53.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9579.5083 | 154655.6728 | 53.25 | 100%
[5 empty] | 53.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9581.7748 | 154692.2638 | 53.26 | 100%
[5 empty] | 53.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9584.0413 | 154728.8547 | 53.27 | 100%
[5 empty] | 53.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9586.3077 | 154765.4456 | 53.28 | 100%
[5 empty] | 53.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9588.5742 | 154802.0366 | 53.29 | 100%
[5 empty] | 53.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9590.8407 | 154838.6275 | 53.3 | 100%
[5 empty] | 53.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9593.1072 | 154875.2185 | 53.31 | 100%
[5 empty] | 53.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9595.3736 | 154911.8094 | 53.32 | 100%
[5 empty] | 53.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9597.6401 | 154948.4004 | 53.33 | 100%
[5 empty] | 53.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9599.9066 | 154984.9913 | 53.34 | 100%
[5 empty] | 53.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9602.1731 | 155021.5823 | 53.35 | 100%
[5 empty] | 53.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9604.4395 | 155058.1732 | 53.36 | 100%
[5 empty] | 53.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9606.706 | 155094.7641 | 53.37 | 100%
[5 empty] | 53.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9608.9725 | 155131.3551 | 53.38 | 100%
[5 empty] | 53.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9611.239 | 155167.946 | 53.39 | 100%
[5 empty] | 53.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9613.5054 | 155204.537 | 53.4 | 100%
[5 empty] | 53.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9615.7719 | 155241.1279 | 53.41 | 100%
[5 empty] | 53.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9618.0384 | 155277.7189 | 53.42 | 100%
[5 empty] | 53.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9620.3049 | 155314.3098 | 53.43 | 100%
[5 empty] | 53.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9622.5713 | 155350.9007 | 53.44 | 100%
[5 empty] | 53.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9624.8378 | 155387.4917 | 53.45 | 100%
[5 empty] | 53.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9627.1043 | 155424.0826 | 53.46 | 100%
[5 empty] | 53.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9629.3708 | 155460.6736 | 53.47 | 100%
[5 empty] | 53.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9631.6372 | 155497.2645 | 53.48 | 100%
[5 empty] | 53.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9633.9037 | 155533.8555 | 53.49 | 100%
[5 empty] | 53.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9636.1702 | 155570.4464 | 53.5 | 100%
[5 empty] | 53.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9638.4367 | 155607.0374 | 53.51 | 100%
[5 empty] | 53.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9640.7031 | 155643.6283 | 53.52 | 100%
[5 empty] | 53.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9642.9696 | 155680.2192 | 53.53 | 100%
[5 empty] | 53.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9645.2361 | 155716.8102 | 53.54 | 100%
[5 empty] | 53.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9647.5026 | 155753.4011 | 53.55 | 100%
[5 empty] | 53.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9649.769 | 155789.9921 | 53.56 | 100%
[5 empty] | 53.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9652.0355 | 155826.583 | 53.57 | 100%
[5 empty] | 53.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9654.302 | 155863.174 | 53.58 | 100%
[5 empty] | 53.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9656.5685 | 155899.7649 | 53.59 | 100%
[5 empty] | 53.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9658.8349 | 155936.3558 | 53.6 | 100%
[5 empty] | 53.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9661.1014 | 155972.9468 | 53.61 | 100%
[5 empty] | 53.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9663.3679 | 156009.5377 | 53.62 | 100%
[5 empty] | 53.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9665.6344 | 156046.1287 | 53.63 | 100%
[5 empty] | 53.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9667.9008 | 156082.7196 | 53.64 | 100%
[5 empty] | 53.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9670.1673 | 156119.3106 | 53.65 | 100%
[5 empty] | 53.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9672.4338 | 156155.9015 | 53.66 | 100%
[5 empty] | 53.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9674.7003 | 156192.4924 | 53.67 | 100%
[5 empty] | 53.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9676.9667 | 156229.0834 | 53.68 | 100%
[5 empty] | 53.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9679.2332 | 156265.6743 | 53.69 | 100%
[5 empty] | 53.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9681.4997 | 156302.2653 | 53.7 | 100%
[5 empty] | 53.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9683.7662 | 156338.8562 | 53.71 | 100%
[5 empty] | 53.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9686.0326 | 156375.4472 | 53.72 | 100%
[5 empty] | 53.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9688.2991 | 156412.0381 | 53.73 | 100%
[5 empty] | 53.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9690.5656 | 156448.6291 | 53.74 | 100%
[5 empty] | 53.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9692.8321 | 156485.22 | 53.75 | 100%
[5 empty] | 53.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9695.0985 | 156521.8109 | 53.76 | 100%
[5 empty] | 53.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9697.365 | 156558.4019 | 53.77 | 100%
[5 empty] | 53.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9699.6315 | 156594.9928 | 53.78 | 100%
[5 empty] | 53.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9701.898 | 156631.5838 | 53.79 | 100%
[5 empty] | 53.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9704.1644 | 156668.1747 | 53.8 | 100%
[5 empty] | 53.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9706.4309 | 156704.7657 | 53.81 | 100%
[5 empty] | 53.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9708.6974 | 156741.3566 | 53.82 | 100%
[5 empty] | 53.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9710.9639 | 156777.9475 | 53.83 | 100%
[5 empty] | 53.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9713.2303 | 156814.5385 | 53.84 | 100%
[5 empty] | 53.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9715.4968 | 156851.1294 | 53.85 | 100%
[5 empty] | 53.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9717.7633 | 156887.7204 | 53.86 | 100%
[5 empty] | 53.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9720.0298 | 156924.3113 | 53.87 | 100%
[5 empty] | 53.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9722.2962 | 156960.9023 | 53.88 | 100%
[5 empty] | 53.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9724.5627 | 156997.4932 | 53.89 | 100%
[5 empty] | 53.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9726.8292 | 157034.0842 | 53.9 | 100%
[5 empty] | 53.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9729.0957 | 157070.6751 | 53.91 | 100%
[5 empty] | 53.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9731.3621 | 157107.266 | 53.92 | 100%
[5 empty] | 53.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9733.6286 | 157143.857 | 53.93 | 100%
[5 empty] | 53.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9735.8951 | 157180.4479 | 53.94 | 100%
[5 empty] | 53.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9738.1616 | 157217.0389 | 53.95 | 100%
[5 empty] | 53.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9740.428 | 157253.6298 | 53.96 | 100%
[5 empty] | 53.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9742.6945 | 157290.2208 | 53.97 | 100%
[5 empty] | 53.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9744.961 | 157326.8117 | 53.98 | 100%
[5 empty] | 53.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9747.2275 | 157363.4026 | 53.99 | 100%
[5 empty] | 54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9749.4939 | 157399.9936 | 54 | 100%
[5 empty] | 54.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9751.7604 | 157436.5845 | 54.01 | 100%
[5 empty] | 54.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9754.0269 | 157473.1755 | 54.02 | 100%
[5 empty] | 54.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9756.2934 | 157509.7664 | 54.03 | 100%
[5 empty] | 54.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9758.5598 | 157546.3574 | 54.04 | 100%
[5 empty] | 54.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9760.8263 | 157582.9483 | 54.05 | 100%
[5 empty] | 54.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9763.0928 | 157619.5393 | 54.06 | 100%
[5 empty] | 54.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9765.3593 | 157656.1302 | 54.07 | 100%
[5 empty] | 54.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9767.6258 | 157692.7211 | 54.08 | 100%
[5 empty] | 54.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9769.8922 | 157729.3121 | 54.09 | 100%
[5 empty] | 54.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9772.1587 | 157765.903 | 54.1 | 100%
[5 empty] | 54.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9774.4252 | 157802.494 | 54.11 | 100%
[5 empty] | 54.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9776.6917 | 157839.0849 | 54.12 | 100%
[5 empty] | 54.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9778.9581 | 157875.6759 | 54.13 | 100%
[5 empty] | 54.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9781.2246 | 157912.2668 | 54.14 | 100%
[5 empty] | 54.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9783.4911 | 157948.8577 | 54.15 | 100%
[5 empty] | 54.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9785.7576 | 157985.4487 | 54.16 | 100%
[5 empty] | 54.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9788.024 | 158022.0396 | 54.17 | 100%
[5 empty] | 54.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9790.2905 | 158058.6306 | 54.18 | 100%
[5 empty] | 54.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9792.557 | 158095.2215 | 54.19 | 100%
[5 empty] | 54.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9794.8235 | 158131.8125 | 54.2 | 100%
[5 empty] | 54.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9797.0899 | 158168.4034 | 54.21 | 100%
[5 empty] | 54.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9799.3564 | 158204.9943 | 54.22 | 100%
[5 empty] | 54.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9801.6229 | 158241.5853 | 54.23 | 100%
[5 empty] | 54.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9803.8894 | 158278.1762 | 54.24 | 100%
[5 empty] | 54.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9806.1558 | 158314.7672 | 54.25 | 100%
[5 empty] | 54.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9808.4223 | 158351.3581 | 54.26 | 100%
[5 empty] | 54.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9810.6888 | 158387.9491 | 54.27 | 100%
[5 empty] | 54.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9812.9553 | 158424.54 | 54.28 | 100%
[5 empty] | 54.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9815.2217 | 158461.131 | 54.29 | 100%
[5 empty] | 54.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9817.4882 | 158497.7219 | 54.3 | 100%
[5 empty] | 54.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9819.7547 | 158534.3128 | 54.31 | 100%
[5 empty] | 54.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9822.0212 | 158570.9038 | 54.32 | 100%
[5 empty] | 54.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9824.2876 | 158607.4947 | 54.33 | 100%
[5 empty] | 54.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9826.5541 | 158644.0857 | 54.34 | 100%
[5 empty] | 54.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9828.8206 | 158680.6766 | 54.35 | 100%
[5 empty] | 54.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9831.0871 | 158717.2676 | 54.36 | 100%
[5 empty] | 54.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9833.3535 | 158753.8585 | 54.37 | 100%
[5 empty] | 54.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9835.62 | 158790.4494 | 54.38 | 100%
[5 empty] | 54.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9837.8865 | 158827.0404 | 54.39 | 100%
[5 empty] | 54.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9840.153 | 158863.6313 | 54.4 | 100%
[5 empty] | 54.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9842.4194 | 158900.2223 | 54.41 | 100%
[5 empty] | 54.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9844.6859 | 158936.8132 | 54.42 | 100%
[5 empty] | 54.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9846.9524 | 158973.4042 | 54.43 | 100%
[5 empty] | 54.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9849.2189 | 159009.9951 | 54.44 | 100%
[5 empty] | 54.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9851.4853 | 159046.5861 | 54.45 | 100%
[5 empty] | 54.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9853.7518 | 159083.177 | 54.46 | 100%
[5 empty] | 54.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9856.0183 | 159119.7679 | 54.47 | 100%
[5 empty] | 54.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9858.2848 | 159156.3589 | 54.48 | 100%
[5 empty] | 54.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9860.5512 | 159192.9498 | 54.49 | 100%
[5 empty] | 54.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9862.8177 | 159229.5408 | 54.5 | 100%
[5 empty] | 54.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9865.0842 | 159266.1317 | 54.51 | 100%
[5 empty] | 54.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9867.3507 | 159302.7227 | 54.52 | 100%
[5 empty] | 54.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9869.6171 | 159339.3136 | 54.53 | 100%
[5 empty] | 54.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9871.8836 | 159375.9045 | 54.54 | 100%
[5 empty] | 54.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9874.1501 | 159412.4955 | 54.55 | 100%
[5 empty] | 54.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9876.4166 | 159449.0864 | 54.56 | 100%
[5 empty] | 54.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9878.683 | 159485.6774 | 54.57 | 100%
[5 empty] | 54.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9880.9495 | 159522.2683 | 54.58 | 100%
[5 empty] | 54.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9883.216 | 159558.8593 | 54.59 | 100%
[5 empty] | 54.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9885.4825 | 159595.4502 | 54.6 | 100%
[5 empty] | 54.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9887.7489 | 159632.0412 | 54.61 | 100%
[5 empty] | 54.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9890.0154 | 159668.6321 | 54.62 | 100%
[5 empty] | 54.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9892.2819 | 159705.223 | 54.63 | 100%
[5 empty] | 54.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9894.5484 | 159741.814 | 54.64 | 100%
[5 empty] | 54.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9896.8148 | 159778.4049 | 54.65 | 100%
[5 empty] | 54.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9899.0813 | 159814.9959 | 54.66 | 100%
[5 empty] | 54.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9901.3478 | 159851.5868 | 54.67 | 100%
[5 empty] | 54.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9903.6143 | 159888.1778 | 54.68 | 100%
[5 empty] | 54.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9905.8807 | 159924.7687 | 54.69 | 100%
[5 empty] | 54.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9908.1472 | 159961.3596 | 54.7 | 100%
[5 empty] | 54.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9910.4137 | 159997.9506 | 54.71 | 100%
[5 empty] | 54.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9912.6802 | 160034.5415 | 54.72 | 100%
[5 empty] | 54.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9914.9466 | 160071.1325 | 54.73 | 100%
[5 empty] | 54.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9917.2131 | 160107.7234 | 54.74 | 100%
[5 empty] | 54.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9919.4796 | 160144.3144 | 54.75 | 100%
[5 empty] | 54.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9921.7461 | 160180.9053 | 54.76 | 100%
[5 empty] | 54.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9924.0125 | 160217.4962 | 54.77 | 100%
[5 empty] | 54.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9926.279 | 160254.0872 | 54.78 | 100%
[5 empty] | 54.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9928.5455 | 160290.6781 | 54.79 | 100%
[5 empty] | 54.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9930.812 | 160327.2691 | 54.8 | 100%
[5 empty] | 54.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9933.0784 | 160363.86 | 54.81 | 100%
[5 empty] | 54.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9935.3449 | 160400.451 | 54.82 | 100%
[5 empty] | 54.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9937.6114 | 160437.0419 | 54.83 | 100%
[5 empty] | 54.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9939.8779 | 160473.6329 | 54.84 | 100%
[5 empty] | 54.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9942.1443 | 160510.2238 | 54.85 | 100%
[5 empty] | 54.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9944.4108 | 160546.8147 | 54.86 | 100%
[5 empty] | 54.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9946.6773 | 160583.4057 | 54.87 | 100%
[5 empty] | 54.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9948.9438 | 160619.9966 | 54.88 | 100%
[5 empty] | 54.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9951.2102 | 160656.5876 | 54.89 | 100%
[5 empty] | 54.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9953.4767 | 160693.1785 | 54.9 | 100%
[5 empty] | 54.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9955.7432 | 160729.7695 | 54.91 | 100%
[5 empty] | 54.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9958.0097 | 160766.3604 | 54.92 | 100%
[5 empty] | 54.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9960.2761 | 160802.9513 | 54.93 | 100%
[5 empty] | 54.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9962.5426 | 160839.5423 | 54.94 | 100%
[5 empty] | 54.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9964.8091 | 160876.1332 | 54.95 | 100%
[5 empty] | 54.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9967.0756 | 160912.7242 | 54.96 | 100%
[5 empty] | 54.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9969.342 | 160949.3151 | 54.97 | 100%
[5 empty] | 54.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9971.6085 | 160985.9061 | 54.98 | 100%
[5 empty] | 54.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9973.875 | 161022.497 | 54.99 | 100%
[5 empty] | 55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9976.1415 | 161059.088 | 55 | 100%
[5 empty] | 55.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9978.4079 | 161095.6789 | 55.01 | 100%
[5 empty] | 55.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9980.6744 | 161132.2698 | 55.02 | 100%
[5 empty] | 55.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9982.9409 | 161168.8608 | 55.03 | 100%
[5 empty] | 55.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9985.2074 | 161205.4517 | 55.04 | 100%
[5 empty] | 55.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9987.4738 | 161242.0427 | 55.05 | 100%
[5 empty] | 55.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9989.7403 | 161278.6336 | 55.06 | 100%
[5 empty] | 55.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9992.0068 | 161315.2246 | 55.07 | 100%
[5 empty] | 55.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9994.2733 | 161351.8155 | 55.08 | 100%
[5 empty] | 55.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9996.5397 | 161388.4064 | 55.09 | 100%
[5 empty] | 55.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 9998.8062 | 161424.9974 | 55.1 | 100%
[5 empty] | 55.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10001.0727 | 161461.5883 | 55.11 | 100%
[5 empty] | 55.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10003.3392 | 161498.1793 | 55.12 | 100%
[5 empty] | 55.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10005.6056 | 161534.7702 | 55.13 | 100%
[5 empty] | 55.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10007.8721 | 161571.3612 | 55.14 | 100%
[5 empty] | 55.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10010.1386 | 161607.9521 | 55.15 | 100%
[5 empty] | 55.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10012.4051 | 161644.543 | 55.16 | 100%
[5 empty] | 55.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10014.6715 | 161681.134 | 55.17 | 100%
[5 empty] | 55.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10016.938 | 161717.7249 | 55.18 | 100%
[5 empty] | 55.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10019.2045 | 161754.3159 | 55.19 | 100%
[5 empty] | 55.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10021.471 | 161790.9068 | 55.2 | 100%
[5 empty] | 55.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10023.7374 | 161827.4978 | 55.21 | 100%
[5 empty] | 55.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10026.0039 | 161864.0887 | 55.22 | 100%
[5 empty] | 55.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10028.2704 | 161900.6797 | 55.23 | 100%
[5 empty] | 55.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10030.5369 | 161937.2706 | 55.24 | 100%
[5 empty] | 55.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10032.8034 | 161973.8615 | 55.25 | 100%
[5 empty] | 55.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10035.0698 | 162010.4525 | 55.26 | 100%
[5 empty] | 55.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10037.3363 | 162047.0434 | 55.27 | 100%
[5 empty] | 55.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10039.6028 | 162083.6344 | 55.28 | 100%
[5 empty] | 55.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10041.8693 | 162120.2253 | 55.29 | 100%
[5 empty] | 55.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10044.1357 | 162156.8163 | 55.3 | 100%
[5 empty] | 55.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10046.4022 | 162193.4072 | 55.31 | 100%
[5 empty] | 55.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10048.6687 | 162229.9981 | 55.32 | 100%
[5 empty] | 55.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10050.9352 | 162266.5891 | 55.33 | 100%
[5 empty] | 55.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10053.2016 | 162303.18 | 55.34 | 100%
[5 empty] | 55.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10055.4681 | 162339.771 | 55.35 | 100%
[5 empty] | 55.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10057.7346 | 162376.3619 | 55.36 | 100%
[5 empty] | 55.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10060.0011 | 162412.9529 | 55.37 | 100%
[5 empty] | 55.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10062.2675 | 162449.5438 | 55.38 | 100%
[5 empty] | 55.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10064.534 | 162486.1348 | 55.39 | 100%
[5 empty] | 55.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10066.8005 | 162522.7257 | 55.4 | 100%
[5 empty] | 55.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10069.067 | 162559.3166 | 55.41 | 100%
[5 empty] | 55.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10071.3334 | 162595.9076 | 55.42 | 100%
[5 empty] | 55.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10073.5999 | 162632.4985 | 55.43 | 100%
[5 empty] | 55.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10075.8664 | 162669.0895 | 55.44 | 100%
[5 empty] | 55.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10078.1329 | 162705.6804 | 55.45 | 100%
[5 empty] | 55.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10080.3993 | 162742.2714 | 55.46 | 100%
[5 empty] | 55.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10082.6658 | 162778.8623 | 55.47 | 100%
[5 empty] | 55.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10084.9323 | 162815.4532 | 55.48 | 100%
[5 empty] | 55.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10087.1988 | 162852.0442 | 55.49 | 100%
[5 empty] | 55.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10089.4652 | 162888.6351 | 55.5 | 100%
[5 empty] | 55.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10091.7317 | 162925.2261 | 55.51 | 100%
[5 empty] | 55.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10093.9982 | 162961.817 | 55.52 | 100%
[5 empty] | 55.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10096.2647 | 162998.408 | 55.53 | 100%
[5 empty] | 55.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10098.5311 | 163034.9989 | 55.54 | 100%
[5 empty] | 55.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10100.7976 | 163071.5899 | 55.55 | 100%
[5 empty] | 55.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10103.0641 | 163108.1808 | 55.56 | 100%
[5 empty] | 55.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10105.3306 | 163144.7717 | 55.57 | 100%
[5 empty] | 55.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10107.597 | 163181.3627 | 55.58 | 100%
[5 empty] | 55.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10109.8635 | 163217.9536 | 55.59 | 100%
[5 empty] | 55.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10112.13 | 163254.5446 | 55.6 | 100%
[5 empty] | 55.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10114.3965 | 163291.1355 | 55.61 | 100%
[5 empty] | 55.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10116.6629 | 163327.7265 | 55.62 | 100%
[5 empty] | 55.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10118.9294 | 163364.3174 | 55.63 | 100%
[5 empty] | 55.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10121.1959 | 163400.9083 | 55.64 | 100%
[5 empty] | 55.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10123.4624 | 163437.4993 | 55.65 | 100%
[5 empty] | 55.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10125.7288 | 163474.0902 | 55.66 | 100%
[5 empty] | 55.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10127.9953 | 163510.6812 | 55.67 | 100%
[5 empty] | 55.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10130.2618 | 163547.2721 | 55.68 | 100%
[5 empty] | 55.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10132.5283 | 163583.8631 | 55.69 | 100%
[5 empty] | 55.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10134.7947 | 163620.454 | 55.7 | 100%
[5 empty] | 55.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10137.0612 | 163657.0449 | 55.71 | 100%
[5 empty] | 55.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10139.3277 | 163693.6359 | 55.72 | 100%
[5 empty] | 55.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10141.5942 | 163730.2268 | 55.73 | 100%
[5 empty] | 55.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10143.8606 | 163766.8178 | 55.74 | 100%
[5 empty] | 55.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10146.1271 | 163803.4087 | 55.75 | 100%
[5 empty] | 55.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10148.3936 | 163839.9997 | 55.76 | 100%
[5 empty] | 55.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10150.6601 | 163876.5906 | 55.77 | 100%
[5 empty] | 55.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10152.9265 | 163913.1816 | 55.78 | 100%
[5 empty] | 55.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10155.193 | 163949.7725 | 55.79 | 100%
[5 empty] | 55.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10157.4595 | 163986.3634 | 55.8 | 100%
[5 empty] | 55.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10159.726 | 164022.9544 | 55.81 | 100%
[5 empty] | 55.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10161.9924 | 164059.5453 | 55.82 | 100%
[5 empty] | 55.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10164.2589 | 164096.1363 | 55.83 | 100%
[5 empty] | 55.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10166.5254 | 164132.7272 | 55.84 | 100%
[5 empty] | 55.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10168.7919 | 164169.3182 | 55.85 | 100%
[5 empty] | 55.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10171.0583 | 164205.9091 | 55.86 | 100%
[5 empty] | 55.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10173.3248 | 164242.5 | 55.87 | 100%
[5 empty] | 55.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10175.5913 | 164279.091 | 55.88 | 100%
[5 empty] | 55.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10177.8578 | 164315.6819 | 55.89 | 100%
[5 empty] | 55.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10180.1242 | 164352.2729 | 55.9 | 100%
[5 empty] | 55.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10182.3907 | 164388.8638 | 55.91 | 100%
[5 empty] | 55.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10184.6572 | 164425.4548 | 55.92 | 100%
[5 empty] | 55.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10186.9237 | 164462.0457 | 55.93 | 100%
[5 empty] | 55.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10189.1901 | 164498.6367 | 55.94 | 100%
[5 empty] | 55.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10191.4566 | 164535.2276 | 55.95 | 100%
[5 empty] | 55.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10193.7231 | 164571.8185 | 55.96 | 100%
[5 empty] | 55.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10195.9896 | 164608.4095 | 55.97 | 100%
[5 empty] | 55.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10198.256 | 164645.0004 | 55.98 | 100%
[5 empty] | 55.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10200.5225 | 164681.5914 | 55.99 | 100%
[5 empty] | 56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10202.789 | 164718.1823 | 56 | 100%
[5 empty] | 56.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10205.0555 | 164754.7733 | 56.01 | 100%
[5 empty] | 56.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10207.3219 | 164791.3642 | 56.02 | 100%
[5 empty] | 56.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10209.5884 | 164827.9551 | 56.03 | 100%
[5 empty] | 56.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10211.8549 | 164864.5461 | 56.04 | 100%
[5 empty] | 56.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10214.1214 | 164901.137 | 56.05 | 100%
[5 empty] | 56.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10216.3878 | 164937.728 | 56.06 | 100%
[5 empty] | 56.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10218.6543 | 164974.3189 | 56.07 | 100%
[5 empty] | 56.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10220.9208 | 165010.9099 | 56.08 | 100%
[5 empty] | 56.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10223.1873 | 165047.5008 | 56.09 | 100%
[5 empty] | 56.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10225.4537 | 165084.0918 | 56.1 | 100%
[5 empty] | 56.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10227.7202 | 165120.6827 | 56.11 | 100%
[5 empty] | 56.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10229.9867 | 165157.2736 | 56.12 | 100%
[5 empty] | 56.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10232.2532 | 165193.8646 | 56.13 | 100%
[5 empty] | 56.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10234.5196 | 165230.4555 | 56.14 | 100%
[5 empty] | 56.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10236.7861 | 165267.0465 | 56.15 | 100%
[5 empty] | 56.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10239.0526 | 165303.6374 | 56.16 | 100%
[5 empty] | 56.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10241.3191 | 165340.2284 | 56.17 | 100%
[5 empty] | 56.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10243.5855 | 165376.8193 | 56.18 | 100%
[5 empty] | 56.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10245.852 | 165413.4102 | 56.19 | 100%
[5 empty] | 56.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10248.1185 | 165450.0012 | 56.2 | 100%
[5 empty] | 56.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10250.385 | 165486.5921 | 56.21 | 100%
[5 empty] | 56.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10252.6514 | 165523.1831 | 56.22 | 100%
[5 empty] | 56.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10254.9179 | 165559.774 | 56.23 | 100%
[5 empty] | 56.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10257.1844 | 165596.365 | 56.24 | 100%
[5 empty] | 56.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10259.4509 | 165632.9559 | 56.25 | 100%
[5 empty] | 56.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10261.7173 | 165669.5468 | 56.26 | 100%
[5 empty] | 56.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10263.9838 | 165706.1378 | 56.27 | 100%
[5 empty] | 56.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10266.2503 | 165742.7287 | 56.28 | 100%
[5 empty] | 56.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10268.5168 | 165779.3197 | 56.29 | 100%
[5 empty] | 56.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10270.7832 | 165815.9106 | 56.3 | 100%
[5 empty] | 56.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10273.0497 | 165852.5016 | 56.31 | 100%
[5 empty] | 56.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10275.3162 | 165889.0925 | 56.32 | 100%
[5 empty] | 56.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10277.5827 | 165925.6835 | 56.33 | 100%
[5 empty] | 56.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10279.8491 | 165962.2744 | 56.34 | 100%
[5 empty] | 56.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10282.1156 | 165998.8653 | 56.35 | 100%
[5 empty] | 56.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10284.3821 | 166035.4563 | 56.36 | 100%
[5 empty] | 56.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10286.6486 | 166072.0472 | 56.37 | 100%
[5 empty] | 56.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10288.915 | 166108.6382 | 56.38 | 100%
[5 empty] | 56.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10291.1815 | 166145.2291 | 56.39 | 100%
[5 empty] | 56.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10293.448 | 166181.8201 | 56.4 | 100%
[5 empty] | 56.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10295.7145 | 166218.411 | 56.41 | 100%
[5 empty] | 56.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10297.9809 | 166255.0019 | 56.42 | 100%
[5 empty] | 56.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10300.2474 | 166291.5929 | 56.43 | 100%
[5 empty] | 56.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10302.5139 | 166328.1838 | 56.44 | 100%
[5 empty] | 56.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10304.7804 | 166364.7748 | 56.45 | 100%
[5 empty] | 56.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10307.0469 | 166401.3657 | 56.46 | 100%
[5 empty] | 56.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10309.3133 | 166437.9567 | 56.47 | 100%
[5 empty] | 56.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10311.5798 | 166474.5476 | 56.48 | 100%
[5 empty] | 56.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10313.8463 | 166511.1386 | 56.49 | 100%
[5 empty] | 56.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10316.1128 | 166547.7295 | 56.5 | 100%
[5 empty] | 56.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10318.3792 | 166584.3204 | 56.51 | 100%
[5 empty] | 56.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10320.6457 | 166620.9114 | 56.52 | 100%
[5 empty] | 56.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10322.9122 | 166657.5023 | 56.53 | 100%
[5 empty] | 56.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10325.1787 | 166694.0933 | 56.54 | 100%
[5 empty] | 56.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10327.4451 | 166730.6842 | 56.55 | 100%
[5 empty] | 56.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10329.7116 | 166767.2752 | 56.56 | 100%
[5 empty] | 56.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10331.9781 | 166803.8661 | 56.57 | 100%
[5 empty] | 56.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10334.2446 | 166840.457 | 56.58 | 100%
[5 empty] | 56.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10336.511 | 166877.048 | 56.59 | 100%
[5 empty] | 56.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10338.7775 | 166913.6389 | 56.6 | 100%
[5 empty] | 56.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10341.044 | 166950.2299 | 56.61 | 100%
[5 empty] | 56.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10343.3105 | 166986.8208 | 56.62 | 100%
[5 empty] | 56.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10345.5769 | 167023.4118 | 56.63 | 100%
[5 empty] | 56.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10347.8434 | 167060.0027 | 56.64 | 100%
[5 empty] | 56.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10350.1099 | 167096.5937 | 56.65 | 100%
[5 empty] | 56.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10352.3764 | 167133.1846 | 56.66 | 100%
[5 empty] | 56.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10354.6428 | 167169.7755 | 56.67 | 100%
[5 empty] | 56.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10356.9093 | 167206.3665 | 56.68 | 100%
[5 empty] | 56.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10359.1758 | 167242.9574 | 56.69 | 100%
[5 empty] | 56.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10361.4423 | 167279.5484 | 56.7 | 100%
[5 empty] | 56.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10363.7087 | 167316.1393 | 56.71 | 100%
[5 empty] | 56.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10365.9752 | 167352.7303 | 56.72 | 100%
[5 empty] | 56.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10368.2417 | 167389.3212 | 56.73 | 100%
[5 empty] | 56.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10370.5082 | 167425.9121 | 56.74 | 100%
[5 empty] | 56.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10372.7746 | 167462.5031 | 56.75 | 100%
[5 empty] | 56.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10375.0411 | 167499.094 | 56.76 | 100%
[5 empty] | 56.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10377.3076 | 167535.685 | 56.77 | 100%
[5 empty] | 56.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10379.5741 | 167572.2759 | 56.78 | 100%
[5 empty] | 56.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10381.8405 | 167608.8669 | 56.79 | 100%
[5 empty] | 56.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10384.107 | 167645.4578 | 56.8 | 100%
[5 empty] | 56.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10386.3735 | 167682.0487 | 56.81 | 100%
[5 empty] | 56.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10388.64 | 167718.6397 | 56.82 | 100%
[5 empty] | 56.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10390.9064 | 167755.2306 | 56.83 | 100%
[5 empty] | 56.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10393.1729 | 167791.8216 | 56.84 | 100%
[5 empty] | 56.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10395.4394 | 167828.4125 | 56.85 | 100%
[5 empty] | 56.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10397.7059 | 167865.0035 | 56.86 | 100%
[5 empty] | 56.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10399.9723 | 167901.5944 | 56.87 | 100%
[5 empty] | 56.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10402.2388 | 167938.1854 | 56.88 | 100%
[5 empty] | 56.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10404.5053 | 167974.7763 | 56.89 | 100%
[5 empty] | 56.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10406.7718 | 168011.3672 | 56.9 | 100%
[5 empty] | 56.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10409.0382 | 168047.9582 | 56.91 | 100%
[5 empty] | 56.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10411.3047 | 168084.5491 | 56.92 | 100%
[5 empty] | 56.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10413.5712 | 168121.1401 | 56.93 | 100%
[5 empty] | 56.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10415.8377 | 168157.731 | 56.94 | 100%
[5 empty] | 56.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10418.1041 | 168194.322 | 56.95 | 100%
[5 empty] | 56.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10420.3706 | 168230.9129 | 56.96 | 100%
[5 empty] | 56.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10422.6371 | 168267.5038 | 56.97 | 100%
[5 empty] | 56.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10424.9036 | 168304.0948 | 56.98 | 100%
[5 empty] | 56.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10427.17 | 168340.6857 | 56.99 | 100%
[5 empty] | 57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10429.4365 | 168377.2767 | 57 | 100%
[5 empty] | 57.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10431.703 | 168413.8676 | 57.01 | 100%
[5 empty] | 57.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10433.9695 | 168450.4586 | 57.02 | 100%
[5 empty] | 57.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10436.2359 | 168487.0495 | 57.03 | 100%
[5 empty] | 57.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10438.5024 | 168523.6405 | 57.04 | 100%
[5 empty] | 57.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10440.7689 | 168560.2314 | 57.05 | 100%
[5 empty] | 57.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10443.0354 | 168596.8223 | 57.06 | 100%
[5 empty] | 57.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10445.3018 | 168633.4133 | 57.07 | 100%
[5 empty] | 57.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10447.5683 | 168670.0042 | 57.08 | 100%
[5 empty] | 57.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10449.8348 | 168706.5952 | 57.09 | 100%
[5 empty] | 57.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10452.1013 | 168743.1861 | 57.1 | 100%
[5 empty] | 57.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10454.3677 | 168779.7771 | 57.11 | 100%
[5 empty] | 57.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10456.6342 | 168816.368 | 57.12 | 100%
[5 empty] | 57.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10458.9007 | 168852.9589 | 57.13 | 100%
[5 empty] | 57.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10461.1672 | 168889.5499 | 57.14 | 100%
[5 empty] | 57.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10463.4336 | 168926.1408 | 57.15 | 100%
[5 empty] | 57.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10465.7001 | 168962.7318 | 57.16 | 100%
[5 empty] | 57.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10467.9666 | 168999.3227 | 57.17 | 100%
[5 empty] | 57.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10470.2331 | 169035.9137 | 57.18 | 100%
[5 empty] | 57.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10472.4995 | 169072.5046 | 57.19 | 100%
[5 empty] | 57.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10474.766 | 169109.0955 | 57.2 | 100%
[5 empty] | 57.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10477.0325 | 169145.6865 | 57.21 | 100%
[5 empty] | 57.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10479.299 | 169182.2774 | 57.22 | 100%
[5 empty] | 57.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10481.5654 | 169218.8684 | 57.23 | 100%
[5 empty] | 57.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10483.8319 | 169255.4593 | 57.24 | 100%
[5 empty] | 57.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10486.0984 | 169292.0503 | 57.25 | 100%
[5 empty] | 57.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10488.3649 | 169328.6412 | 57.26 | 100%
[5 empty] | 57.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10490.6313 | 169365.2322 | 57.27 | 100%
[5 empty] | 57.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10492.8978 | 169401.8231 | 57.28 | 100%
[5 empty] | 57.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10495.1643 | 169438.414 | 57.29 | 100%
[5 empty] | 57.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10497.4308 | 169475.005 | 57.3 | 100%
[5 empty] | 57.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10499.6972 | 169511.5959 | 57.31 | 100%
[5 empty] | 57.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10501.9637 | 169548.1869 | 57.32 | 100%
[5 empty] | 57.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10504.2302 | 169584.7778 | 57.33 | 100%
[5 empty] | 57.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10506.4967 | 169621.3688 | 57.34 | 100%
[5 empty] | 57.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10508.7631 | 169657.9597 | 57.35 | 100%
[5 empty] | 57.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10511.0296 | 169694.5506 | 57.36 | 100%
[5 empty] | 57.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10513.2961 | 169731.1416 | 57.37 | 100%
[5 empty] | 57.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10515.5626 | 169767.7325 | 57.38 | 100%
[5 empty] | 57.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10517.829 | 169804.3235 | 57.39 | 100%
[5 empty] | 57.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10520.0955 | 169840.9144 | 57.4 | 100%
[5 empty] | 57.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10522.362 | 169877.5054 | 57.41 | 100%
[5 empty] | 57.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10524.6285 | 169914.0963 | 57.42 | 100%
[5 empty] | 57.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10526.8949 | 169950.6873 | 57.43 | 100%
[5 empty] | 57.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10529.1614 | 169987.2782 | 57.44 | 100%
[5 empty] | 57.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10531.4279 | 170023.8691 | 57.45 | 100%
[5 empty] | 57.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10533.6944 | 170060.4601 | 57.46 | 100%
[5 empty] | 57.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10535.9608 | 170097.051 | 57.47 | 100%
[5 empty] | 57.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10538.2273 | 170133.642 | 57.48 | 100%
[5 empty] | 57.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10540.4938 | 170170.2329 | 57.49 | 100%
[5 empty] | 57.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10542.7603 | 170206.8239 | 57.5 | 100%
[5 empty] | 57.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10545.0267 | 170243.4148 | 57.51 | 100%
[5 empty] | 57.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10547.2932 | 170280.0057 | 57.52 | 100%
[5 empty] | 57.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10549.5597 | 170316.5967 | 57.53 | 100%
[5 empty] | 57.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10551.8262 | 170353.1876 | 57.54 | 100%
[5 empty] | 57.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10554.0926 | 170389.7786 | 57.55 | 100%
[5 empty] | 57.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10556.3591 | 170426.3695 | 57.56 | 100%
[5 empty] | 57.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10558.6256 | 170462.9605 | 57.57 | 100%
[5 empty] | 57.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10560.8921 | 170499.5514 | 57.58 | 100%
[5 empty] | 57.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10563.1585 | 170536.1424 | 57.59 | 100%
[5 empty] | 57.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10565.425 | 170572.7333 | 57.6 | 100%
[5 empty] | 57.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10567.6915 | 170609.3242 | 57.61 | 100%
[5 empty] | 57.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10569.958 | 170645.9152 | 57.62 | 100%
[5 empty] | 57.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10572.2244 | 170682.5061 | 57.63 | 100%
[5 empty] | 57.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10574.4909 | 170719.0971 | 57.64 | 100%
[5 empty] | 57.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10576.7574 | 170755.688 | 57.65 | 100%
[5 empty] | 57.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10579.0239 | 170792.279 | 57.66 | 100%
[5 empty] | 57.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10581.2904 | 170828.8699 | 57.67 | 100%
[5 empty] | 57.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10583.5568 | 170865.4608 | 57.68 | 100%
[5 empty] | 57.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10585.8233 | 170902.0518 | 57.69 | 100%
[5 empty] | 57.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10588.0898 | 170938.6427 | 57.7 | 100%
[5 empty] | 57.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10590.3563 | 170975.2337 | 57.71 | 100%
[5 empty] | 57.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10592.6227 | 171011.8246 | 57.72 | 100%
[5 empty] | 57.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10594.8892 | 171048.4156 | 57.73 | 100%
[5 empty] | 57.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10597.1557 | 171085.0065 | 57.74 | 100%
[5 empty] | 57.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10599.4222 | 171121.5974 | 57.75 | 100%
[5 empty] | 57.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10601.6886 | 171158.1884 | 57.76 | 100%
[5 empty] | 57.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10603.9551 | 171194.7793 | 57.77 | 100%
[5 empty] | 57.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10606.2216 | 171231.3703 | 57.78 | 100%
[5 empty] | 57.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10608.4881 | 171267.9612 | 57.79 | 100%
[5 empty] | 57.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10610.7545 | 171304.5522 | 57.8 | 100%
[5 empty] | 57.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10613.021 | 171341.1431 | 57.81 | 100%
[5 empty] | 57.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10615.2875 | 171377.7341 | 57.82 | 100%
[5 empty] | 57.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10617.554 | 171414.325 | 57.83 | 100%
[5 empty] | 57.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10619.8204 | 171450.9159 | 57.84 | 100%
[5 empty] | 57.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10622.0869 | 171487.5069 | 57.85 | 100%
[5 empty] | 57.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10624.3534 | 171524.0978 | 57.86 | 100%
[5 empty] | 57.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10626.6199 | 171560.6888 | 57.87 | 100%
[5 empty] | 57.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10628.8863 | 171597.2797 | 57.88 | 100%
[5 empty] | 57.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10631.1528 | 171633.8707 | 57.89 | 100%
[5 empty] | 57.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10633.4193 | 171670.4616 | 57.9 | 100%
[5 empty] | 57.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10635.6858 | 171707.0525 | 57.91 | 100%
[5 empty] | 57.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10637.9522 | 171743.6435 | 57.92 | 100%
[5 empty] | 57.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10640.2187 | 171780.2344 | 57.93 | 100%
[5 empty] | 57.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10642.4852 | 171816.8254 | 57.94 | 100%
[5 empty] | 57.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10644.7517 | 171853.4163 | 57.95 | 100%
[5 empty] | 57.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10647.0181 | 171890.0073 | 57.96 | 100%
[5 empty] | 57.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10649.2846 | 171926.5982 | 57.97 | 100%
[5 empty] | 57.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10651.5511 | 171963.1892 | 57.98 | 100%
[5 empty] | 57.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10653.8176 | 171999.7801 | 57.99 | 100%
[5 empty] | 58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10656.084 | 172036.371 | 58 | 100%
[5 empty] | 58.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10658.3505 | 172072.962 | 58.01 | 100%
[5 empty] | 58.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10660.617 | 172109.5529 | 58.02 | 100%
[5 empty] | 58.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10662.8835 | 172146.1439 | 58.03 | 100%
[5 empty] | 58.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10665.1499 | 172182.7348 | 58.04 | 100%
[5 empty] | 58.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10667.4164 | 172219.3258 | 58.05 | 100%
[5 empty] | 58.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10669.6829 | 172255.9167 | 58.06 | 100%
[5 empty] | 58.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10671.9494 | 172292.5076 | 58.07 | 100%
[5 empty] | 58.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10674.2158 | 172329.0986 | 58.08 | 100%
[5 empty] | 58.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10676.4823 | 172365.6895 | 58.09 | 100%
[5 empty] | 58.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10678.7488 | 172402.2805 | 58.1 | 100%
[5 empty] | 58.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10681.0153 | 172438.8714 | 58.11 | 100%
[5 empty] | 58.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10683.2817 | 172475.4624 | 58.12 | 100%
[5 empty] | 58.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10685.5482 | 172512.0533 | 58.13 | 100%
[5 empty] | 58.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10687.8147 | 172548.6443 | 58.14 | 100%
[5 empty] | 58.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10690.0812 | 172585.2352 | 58.15 | 100%
[5 empty] | 58.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10692.3476 | 172621.8261 | 58.16 | 100%
[5 empty] | 58.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10694.6141 | 172658.4171 | 58.17 | 100%
[5 empty] | 58.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10696.8806 | 172695.008 | 58.18 | 100%
[5 empty] | 58.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10699.1471 | 172731.599 | 58.19 | 100%
[5 empty] | 58.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10701.4135 | 172768.1899 | 58.2 | 100%
[5 empty] | 58.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10703.68 | 172804.7809 | 58.21 | 100%
[5 empty] | 58.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10705.9465 | 172841.3718 | 58.22 | 100%
[5 empty] | 58.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10708.213 | 172877.9627 | 58.23 | 100%
[5 empty] | 58.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10710.4794 | 172914.5537 | 58.24 | 100%
[5 empty] | 58.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10712.7459 | 172951.1446 | 58.25 | 100%
[5 empty] | 58.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10715.0124 | 172987.7356 | 58.26 | 100%
[5 empty] | 58.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10717.2789 | 173024.3265 | 58.27 | 100%
[5 empty] | 58.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10719.5453 | 173060.9175 | 58.28 | 100%
[5 empty] | 58.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10721.8118 | 173097.5084 | 58.29 | 100%
[5 empty] | 58.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10724.0783 | 173134.0993 | 58.3 | 100%
[5 empty] | 58.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10726.3448 | 173170.6903 | 58.31 | 100%
[5 empty] | 58.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10728.6112 | 173207.2812 | 58.32 | 100%
[5 empty] | 58.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10730.8777 | 173243.8722 | 58.33 | 100%
[5 empty] | 58.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10733.1442 | 173280.4631 | 58.34 | 100%
[5 empty] | 58.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10735.4107 | 173317.0541 | 58.35 | 100%
[5 empty] | 58.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10737.6771 | 173353.645 | 58.36 | 100%
[5 empty] | 58.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10739.9436 | 173390.236 | 58.37 | 100%
[5 empty] | 58.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10742.2101 | 173426.8269 | 58.38 | 100%
[5 empty] | 58.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10744.4766 | 173463.4178 | 58.39 | 100%
[5 empty] | 58.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10746.743 | 173500.0088 | 58.4 | 100%
[5 empty] | 58.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10749.0095 | 173536.5997 | 58.41 | 100%
[5 empty] | 58.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10751.276 | 173573.1907 | 58.42 | 100%
[5 empty] | 58.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10753.5425 | 173609.7816 | 58.43 | 100%
[5 empty] | 58.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10755.8089 | 173646.3726 | 58.44 | 100%
[5 empty] | 58.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10758.0754 | 173682.9635 | 58.45 | 100%
[5 empty] | 58.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10760.3419 | 173719.5544 | 58.46 | 100%
[5 empty] | 58.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10762.6084 | 173756.1454 | 58.47 | 100%
[5 empty] | 58.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10764.8748 | 173792.7363 | 58.48 | 100%
[5 empty] | 58.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10767.1413 | 173829.3273 | 58.49 | 100%
[5 empty] | 58.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10769.4078 | 173865.9182 | 58.5 | 100%
[5 empty] | 58.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10771.6743 | 173902.5092 | 58.51 | 100%
[5 empty] | 58.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10773.9407 | 173939.1001 | 58.52 | 100%
[5 empty] | 58.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10776.2072 | 173975.6911 | 58.53 | 100%
[5 empty] | 58.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10778.4737 | 174012.282 | 58.54 | 100%
[5 empty] | 58.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10780.7402 | 174048.8729 | 58.55 | 100%
[5 empty] | 58.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10783.0066 | 174085.4639 | 58.56 | 100%
[5 empty] | 58.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10785.2731 | 174122.0548 | 58.57 | 100%
[5 empty] | 58.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10787.5396 | 174158.6458 | 58.58 | 100%
[5 empty] | 58.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10789.8061 | 174195.2367 | 58.59 | 100%
[5 empty] | 58.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10792.0725 | 174231.8277 | 58.6 | 100%
[5 empty] | 58.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10794.339 | 174268.4186 | 58.61 | 100%
[5 empty] | 58.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10796.6055 | 174305.0095 | 58.62 | 100%
[5 empty] | 58.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10798.872 | 174341.6005 | 58.63 | 100%
[5 empty] | 58.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10801.1384 | 174378.1914 | 58.64 | 100%
[5 empty] | 58.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10803.4049 | 174414.7824 | 58.65 | 100%
[5 empty] | 58.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10805.6714 | 174451.3733 | 58.66 | 100%
[5 empty] | 58.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10807.9379 | 174487.9643 | 58.67 | 100%
[5 empty] | 58.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10810.2043 | 174524.5552 | 58.68 | 100%
[5 empty] | 58.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10812.4708 | 174561.1461 | 58.69 | 100%
[5 empty] | 58.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10814.7373 | 174597.7371 | 58.7 | 100%
[5 empty] | 58.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10817.0038 | 174634.328 | 58.71 | 100%
[5 empty] | 58.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10819.2702 | 174670.919 | 58.72 | 100%
[5 empty] | 58.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10821.5367 | 174707.5099 | 58.73 | 100%
[5 empty] | 58.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10823.8032 | 174744.1009 | 58.74 | 100%
[5 empty] | 58.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10826.0697 | 174780.6918 | 58.75 | 100%
[5 empty] | 58.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10828.3361 | 174817.2828 | 58.76 | 100%
[5 empty] | 58.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10830.6026 | 174853.8737 | 58.77 | 100%
[5 empty] | 58.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10832.8691 | 174890.4646 | 58.78 | 100%
[5 empty] | 58.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10835.1356 | 174927.0556 | 58.79 | 100%
[5 empty] | 58.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10837.402 | 174963.6465 | 58.8 | 100%
[5 empty] | 58.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10839.6685 | 175000.2375 | 58.81 | 100%
[5 empty] | 58.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10841.935 | 175036.8284 | 58.82 | 100%
[5 empty] | 58.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10844.2015 | 175073.4194 | 58.83 | 100%
[5 empty] | 58.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10846.468 | 175110.0103 | 58.84 | 100%
[5 empty] | 58.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10848.7344 | 175146.6012 | 58.85 | 100%
[5 empty] | 58.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10851.0009 | 175183.1922 | 58.86 | 100%
[5 empty] | 58.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10853.2674 | 175219.7831 | 58.87 | 100%
[5 empty] | 58.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10855.5339 | 175256.3741 | 58.88 | 100%
[5 empty] | 58.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10857.8003 | 175292.965 | 58.89 | 100%
[5 empty] | 58.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10860.0668 | 175329.556 | 58.9 | 100%
[5 empty] | 58.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10862.3333 | 175366.1469 | 58.91 | 100%
[5 empty] | 58.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10864.5998 | 175402.7379 | 58.92 | 100%
[5 empty] | 58.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10866.8662 | 175439.3288 | 58.93 | 100%
[5 empty] | 58.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10869.1327 | 175475.9197 | 58.94 | 100%
[5 empty] | 58.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10871.3992 | 175512.5107 | 58.95 | 100%
[5 empty] | 58.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10873.6657 | 175549.1016 | 58.96 | 100%
[5 empty] | 58.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10875.9321 | 175585.6926 | 58.97 | 100%
[5 empty] | 58.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10878.1986 | 175622.2835 | 58.98 | 100%
[5 empty] | 58.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10880.4651 | 175658.8745 | 58.99 | 100%
[5 empty] | 59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10882.7316 | 175695.4654 | 59 | 100%
[5 empty] | 59.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10884.998 | 175732.0563 | 59.01 | 100%
[5 empty] | 59.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10887.2645 | 175768.6473 | 59.02 | 100%
[5 empty] | 59.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10889.531 | 175805.2382 | 59.03 | 100%
[5 empty] | 59.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10891.7975 | 175841.8292 | 59.04 | 100%
[5 empty] | 59.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10894.0639 | 175878.4201 | 59.05 | 100%
[5 empty] | 59.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10896.3304 | 175915.0111 | 59.06 | 100%
[5 empty] | 59.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10898.5969 | 175951.602 | 59.07 | 100%
[5 empty] | 59.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10900.8634 | 175988.193 | 59.08 | 100%
[5 empty] | 59.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10903.1298 | 176024.7839 | 59.09 | 100%
[5 empty] | 59.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10905.3963 | 176061.3748 | 59.1 | 100%
[5 empty] | 59.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10907.6628 | 176097.9658 | 59.11 | 100%
[5 empty] | 59.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10909.9293 | 176134.5567 | 59.12 | 100%
[5 empty] | 59.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10912.1957 | 176171.1477 | 59.13 | 100%
[5 empty] | 59.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10914.4622 | 176207.7386 | 59.14 | 100%
[5 empty] | 59.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10916.7287 | 176244.3296 | 59.15 | 100%
[5 empty] | 59.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10918.9952 | 176280.9205 | 59.16 | 100%
[5 empty] | 59.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10921.2616 | 176317.5114 | 59.17 | 100%
[5 empty] | 59.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10923.5281 | 176354.1024 | 59.18 | 100%
[5 empty] | 59.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10925.7946 | 176390.6933 | 59.19 | 100%
[5 empty] | 59.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10928.0611 | 176427.2843 | 59.2 | 100%
[5 empty] | 59.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10930.3275 | 176463.8752 | 59.21 | 100%
[5 empty] | 59.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10932.594 | 176500.4662 | 59.22 | 100%
[5 empty] | 59.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10934.8605 | 176537.0571 | 59.23 | 100%
[5 empty] | 59.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10937.127 | 176573.648 | 59.24 | 100%
[5 empty] | 59.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10939.3934 | 176610.239 | 59.25 | 100%
[5 empty] | 59.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10941.6599 | 176646.8299 | 59.26 | 100%
[5 empty] | 59.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10943.9264 | 176683.4209 | 59.27 | 100%
[5 empty] | 59.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10946.1929 | 176720.0118 | 59.28 | 100%
[5 empty] | 59.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10948.4593 | 176756.6028 | 59.29 | 100%
[5 empty] | 59.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10950.7258 | 176793.1937 | 59.3 | 100%
[5 empty] | 59.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10952.9923 | 176829.7847 | 59.31 | 100%
[5 empty] | 59.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10955.2588 | 176866.3756 | 59.32 | 100%
[5 empty] | 59.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10957.5252 | 176902.9665 | 59.33 | 100%
[5 empty] | 59.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10959.7917 | 176939.5575 | 59.34 | 100%
[5 empty] | 59.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10962.0582 | 176976.1484 | 59.35 | 100%
[5 empty] | 59.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10964.3247 | 177012.7394 | 59.36 | 100%
[5 empty] | 59.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10966.5911 | 177049.3303 | 59.37 | 100%
[5 empty] | 59.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10968.8576 | 177085.9213 | 59.38 | 100%
[5 empty] | 59.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10971.1241 | 177122.5122 | 59.39 | 100%
[5 empty] | 59.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10973.3906 | 177159.1031 | 59.4 | 100%
[5 empty] | 59.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10975.657 | 177195.6941 | 59.41 | 100%
[5 empty] | 59.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10977.9235 | 177232.285 | 59.42 | 100%
[5 empty] | 59.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10980.19 | 177268.876 | 59.43 | 100%
[5 empty] | 59.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10982.4565 | 177305.4669 | 59.44 | 100%
[5 empty] | 59.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10984.7229 | 177342.0579 | 59.45 | 100%
[5 empty] | 59.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10986.9894 | 177378.6488 | 59.46 | 100%
[5 empty] | 59.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10989.2559 | 177415.2398 | 59.47 | 100%
[5 empty] | 59.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10991.5224 | 177451.8307 | 59.48 | 100%
[5 empty] | 59.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10993.7888 | 177488.4216 | 59.49 | 100%
[5 empty] | 59.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10996.0553 | 177525.0126 | 59.5 | 100%
[5 empty] | 59.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 10998.3218 | 177561.6035 | 59.51 | 100%
[5 empty] | 59.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11000.5883 | 177598.1945 | 59.52 | 100%
[5 empty] | 59.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11002.8547 | 177634.7854 | 59.53 | 100%
[5 empty] | 59.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11005.1212 | 177671.3764 | 59.54 | 100%
[5 empty] | 59.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11007.3877 | 177707.9673 | 59.55 | 100%
[5 empty] | 59.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11009.6542 | 177744.5582 | 59.56 | 100%
[5 empty] | 59.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11011.9206 | 177781.1492 | 59.57 | 100%
[5 empty] | 59.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11014.1871 | 177817.7401 | 59.58 | 100%
[5 empty] | 59.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11016.4536 | 177854.3311 | 59.59 | 100%
[5 empty] | 59.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11018.7201 | 177890.922 | 59.6 | 100%
[5 empty] | 59.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11020.9865 | 177927.513 | 59.61 | 100%
[5 empty] | 59.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11023.253 | 177964.1039 | 59.62 | 100%
[5 empty] | 59.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11025.5195 | 178000.6949 | 59.63 | 100%
[5 empty] | 59.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11027.786 | 178037.2858 | 59.64 | 100%
[5 empty] | 59.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11030.0524 | 178073.8767 | 59.65 | 100%
[5 empty] | 59.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11032.3189 | 178110.4677 | 59.66 | 100%
[5 empty] | 59.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11034.5854 | 178147.0586 | 59.67 | 100%
[5 empty] | 59.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11036.8519 | 178183.6496 | 59.68 | 100%
[5 empty] | 59.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11039.1183 | 178220.2405 | 59.69 | 100%
[5 empty] | 59.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11041.3848 | 178256.8315 | 59.7 | 100%
[5 empty] | 59.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11043.6513 | 178293.4224 | 59.71 | 100%
[5 empty] | 59.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11045.9178 | 178330.0133 | 59.72 | 100%
[5 empty] | 59.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11048.1842 | 178366.6043 | 59.73 | 100%
[5 empty] | 59.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11050.4507 | 178403.1952 | 59.74 | 100%
[5 empty] | 59.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11052.7172 | 178439.7862 | 59.75 | 100%
[5 empty] | 59.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11054.9837 | 178476.3771 | 59.76 | 100%
[5 empty] | 59.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11057.2501 | 178512.9681 | 59.77 | 100%
[5 empty] | 59.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11059.5166 | 178549.559 | 59.78 | 100%
[5 empty] | 59.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11061.7831 | 178586.1499 | 59.79 | 100%
[5 empty] | 59.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11064.0496 | 178622.7409 | 59.8 | 100%
[5 empty] | 59.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11066.316 | 178659.3318 | 59.81 | 100%
[5 empty] | 59.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11068.5825 | 178695.9228 | 59.82 | 100%
[5 empty] | 59.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11070.849 | 178732.5137 | 59.83 | 100%
[5 empty] | 59.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11073.1155 | 178769.1047 | 59.84 | 100%
[5 empty] | 59.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11075.3819 | 178805.6956 | 59.85 | 100%
[5 empty] | 59.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11077.6484 | 178842.2866 | 59.86 | 100%
[5 empty] | 59.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11079.9149 | 178878.8775 | 59.87 | 100%
[5 empty] | 59.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11082.1814 | 178915.4684 | 59.88 | 100%
[5 empty] | 59.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11084.4478 | 178952.0594 | 59.89 | 100%
[5 empty] | 59.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11086.7143 | 178988.6503 | 59.9 | 100%
[5 empty] | 59.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11088.9808 | 179025.2413 | 59.91 | 100%
[5 empty] | 59.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11091.2473 | 179061.8322 | 59.92 | 100%
[5 empty] | 59.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11093.5137 | 179098.4232 | 59.93 | 100%
[5 empty] | 59.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11095.7802 | 179135.0141 | 59.94 | 100%
[5 empty] | 59.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11098.0467 | 179171.605 | 59.95 | 100%
[5 empty] | 59.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11100.3132 | 179208.196 | 59.96 | 100%
[5 empty] | 59.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11102.5796 | 179244.7869 | 59.97 | 100%
[5 empty] | 59.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11104.8461 | 179281.3779 | 59.98 | 100%
[5 empty] | 59.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11107.1126 | 179317.9688 | 59.99 | 100%
[5 empty] | 60 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11109.3791 | 179354.5598 | 60 | 100%
[5 empty] | 60.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11111.6455 | 179391.1507 | 60.01 | 100%
[5 empty] | 60.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11113.912 | 179427.7417 | 60.02 | 100%
[5 empty] | 60.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11116.1785 | 179464.3326 | 60.03 | 100%
[5 empty] | 60.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11118.445 | 179500.9235 | 60.04 | 100%
[5 empty] | 60.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11120.7115 | 179537.5145 | 60.05 | 100%
[5 empty] | 60.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11122.9779 | 179574.1054 | 60.06 | 100%
[5 empty] | 60.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11125.2444 | 179610.6964 | 60.07 | 100%
[5 empty] | 60.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11127.5109 | 179647.2873 | 60.08 | 100%
[5 empty] | 60.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11129.7774 | 179683.8783 | 60.09 | 100%
[5 empty] | 60.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11132.0438 | 179720.4692 | 60.1 | 100%
[5 empty] | 60.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11134.3103 | 179757.0601 | 60.11 | 100%
[5 empty] | 60.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11136.5768 | 179793.6511 | 60.12 | 100%
[5 empty] | 60.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11138.8433 | 179830.242 | 60.13 | 100%
[5 empty] | 60.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11141.1097 | 179866.833 | 60.14 | 100%
[5 empty] | 60.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11143.3762 | 179903.4239 | 60.15 | 100%
[5 empty] | 60.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11145.6427 | 179940.0149 | 60.16 | 100%
[5 empty] | 60.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11147.9092 | 179976.6058 | 60.17 | 100%
[5 empty] | 60.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11150.1756 | 180013.1968 | 60.18 | 100%
[5 empty] | 60.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11152.4421 | 180049.7877 | 60.19 | 100%
[5 empty] | 60.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11154.7086 | 180086.3786 | 60.2 | 100%
[5 empty] | 60.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11156.9751 | 180122.9696 | 60.21 | 100%
[5 empty] | 60.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11159.2415 | 180159.5605 | 60.22 | 100%
[5 empty] | 60.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11161.508 | 180196.1515 | 60.23 | 100%
[5 empty] | 60.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11163.7745 | 180232.7424 | 60.24 | 100%
[5 empty] | 60.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11166.041 | 180269.3334 | 60.25 | 100%
[5 empty] | 60.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11168.3074 | 180305.9243 | 60.26 | 100%
[5 empty] | 60.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11170.5739 | 180342.5152 | 60.27 | 100%
[5 empty] | 60.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11172.8404 | 180379.1062 | 60.28 | 100%
[5 empty] | 60.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11175.1069 | 180415.6971 | 60.29 | 100%
[5 empty] | 60.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11177.3733 | 180452.2881 | 60.3 | 100%
[5 empty] | 60.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11179.6398 | 180488.879 | 60.31 | 100%
[5 empty] | 60.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11181.9063 | 180525.47 | 60.32 | 100%
[5 empty] | 60.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11184.1728 | 180562.0609 | 60.33 | 100%
[5 empty] | 60.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11186.4392 | 180598.6518 | 60.34 | 100%
[5 empty] | 60.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11188.7057 | 180635.2428 | 60.35 | 100%
[5 empty] | 60.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11190.9722 | 180671.8337 | 60.36 | 100%
[5 empty] | 60.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11193.2387 | 180708.4247 | 60.37 | 100%
[5 empty] | 60.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11195.5051 | 180745.0156 | 60.38 | 100%
[5 empty] | 60.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11197.7716 | 180781.6066 | 60.39 | 100%
[5 empty] | 60.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11200.0381 | 180818.1975 | 60.4 | 100%
[5 empty] | 60.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11202.3046 | 180854.7885 | 60.41 | 100%
[5 empty] | 60.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11204.571 | 180891.3794 | 60.42 | 100%
[5 empty] | 60.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11206.8375 | 180927.9703 | 60.43 | 100%
[5 empty] | 60.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11209.104 | 180964.5613 | 60.44 | 100%
[5 empty] | 60.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11211.3705 | 181001.1522 | 60.45 | 100%
[5 empty] | 60.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11213.6369 | 181037.7432 | 60.46 | 100%
[5 empty] | 60.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11215.9034 | 181074.3341 | 60.47 | 100%
[5 empty] | 60.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11218.1699 | 181110.9251 | 60.48 | 100%
[5 empty] | 60.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11220.4364 | 181147.516 | 60.49 | 100%
[5 empty] | 60.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11222.7028 | 181184.1069 | 60.5 | 100%
[5 empty] | 60.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11224.9693 | 181220.6979 | 60.51 | 100%
[5 empty] | 60.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11227.2358 | 181257.2888 | 60.52 | 100%
[5 empty] | 60.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11229.5023 | 181293.8798 | 60.53 | 100%
[5 empty] | 60.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11231.7687 | 181330.4707 | 60.54 | 100%
[5 empty] | 60.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11234.0352 | 181367.0617 | 60.55 | 100%
[5 empty] | 60.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11236.3017 | 181403.6526 | 60.56 | 100%
[5 empty] | 60.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11238.5682 | 181440.2436 | 60.57 | 100%
[5 empty] | 60.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11240.8346 | 181476.8345 | 60.58 | 100%
[5 empty] | 60.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11243.1011 | 181513.4254 | 60.59 | 100%
[5 empty] | 60.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11245.3676 | 181550.0164 | 60.6 | 100%
[5 empty] | 60.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11247.6341 | 181586.6073 | 60.61 | 100%
[5 empty] | 60.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11249.9005 | 181623.1983 | 60.62 | 100%
[5 empty] | 60.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11252.167 | 181659.7892 | 60.63 | 100%
[5 empty] | 60.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11254.4335 | 181696.3802 | 60.64 | 100%
[5 empty] | 60.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11256.7 | 181732.9711 | 60.65 | 100%
[5 empty] | 60.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11258.9664 | 181769.562 | 60.66 | 100%
[5 empty] | 60.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11261.2329 | 181806.153 | 60.67 | 100%
[5 empty] | 60.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11263.4994 | 181842.7439 | 60.68 | 100%
[5 empty] | 60.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11265.7659 | 181879.3349 | 60.69 | 100%
[5 empty] | 60.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11268.0323 | 181915.9258 | 60.7 | 100%
[5 empty] | 60.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11270.2988 | 181952.5168 | 60.71 | 100%
[5 empty] | 60.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11272.5653 | 181989.1077 | 60.72 | 100%
[5 empty] | 60.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11274.8318 | 182025.6986 | 60.73 | 100%
[5 empty] | 60.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11277.0982 | 182062.2896 | 60.74 | 100%
[5 empty] | 60.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11279.3647 | 182098.8805 | 60.75 | 100%
[5 empty] | 60.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11281.6312 | 182135.4715 | 60.76 | 100%
[5 empty] | 60.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11283.8977 | 182172.0624 | 60.77 | 100%
[5 empty] | 60.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11286.1641 | 182208.6534 | 60.78 | 100%
[5 empty] | 60.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11288.4306 | 182245.2443 | 60.79 | 100%
[5 empty] | 60.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11290.6971 | 182281.8353 | 60.8 | 100%
[5 empty] | 60.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11292.9636 | 182318.4262 | 60.81 | 100%
[5 empty] | 60.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11295.23 | 182355.0171 | 60.82 | 100%
[5 empty] | 60.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11297.4965 | 182391.6081 | 60.83 | 100%
[5 empty] | 60.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11299.763 | 182428.199 | 60.84 | 100%
[5 empty] | 60.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11302.0295 | 182464.79 | 60.85 | 100%
[5 empty] | 60.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11304.2959 | 182501.3809 | 60.86 | 100%
[5 empty] | 60.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11306.5624 | 182537.9719 | 60.87 | 100%
[5 empty] | 60.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11308.8289 | 182574.5628 | 60.88 | 100%
[5 empty] | 60.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11311.0954 | 182611.1537 | 60.89 | 100%
[5 empty] | 60.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11313.3618 | 182647.7447 | 60.9 | 100%
[5 empty] | 60.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11315.6283 | 182684.3356 | 60.91 | 100%
[5 empty] | 60.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11317.8948 | 182720.9266 | 60.92 | 100%
[5 empty] | 60.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11320.1613 | 182757.5175 | 60.93 | 100%
[5 empty] | 60.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11322.4277 | 182794.1085 | 60.94 | 100%
[5 empty] | 60.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11324.6942 | 182830.6994 | 60.95 | 100%
[5 empty] | 60.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11326.9607 | 182867.2904 | 60.96 | 100%
[5 empty] | 60.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11329.2272 | 182903.8813 | 60.97 | 100%
[5 empty] | 60.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11331.4936 | 182940.4722 | 60.98 | 100%
[5 empty] | 60.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11333.7601 | 182977.0632 | 60.99 | 100%
[5 empty] | 61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11336.0266 | 183013.6541 | 61 | 100%
[5 empty] | 61.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11338.2931 | 183050.2451 | 61.01 | 100%
[5 empty] | 61.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11340.5595 | 183086.836 | 61.02 | 100%
[5 empty] | 61.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11342.826 | 183123.427 | 61.03 | 100%
[5 empty] | 61.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11345.0925 | 183160.0179 | 61.04 | 100%
[5 empty] | 61.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11347.359 | 183196.6088 | 61.05 | 100%
[5 empty] | 61.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11349.6254 | 183233.1998 | 61.06 | 100%
[5 empty] | 61.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11351.8919 | 183269.7907 | 61.07 | 100%
[5 empty] | 61.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11354.1584 | 183306.3817 | 61.08 | 100%
[5 empty] | 61.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11356.4249 | 183342.9726 | 61.09 | 100%
[5 empty] | 61.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11358.6913 | 183379.5636 | 61.1 | 100%
[5 empty] | 61.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11360.9578 | 183416.1545 | 61.11 | 100%
[5 empty] | 61.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11363.2243 | 183452.7455 | 61.12 | 100%
[5 empty] | 61.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11365.4908 | 183489.3364 | 61.13 | 100%
[5 empty] | 61.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11367.7572 | 183525.9273 | 61.14 | 100%
[5 empty] | 61.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11370.0237 | 183562.5183 | 61.15 | 100%
[5 empty] | 61.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11372.2902 | 183599.1092 | 61.16 | 100%
[5 empty] | 61.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11374.5567 | 183635.7002 | 61.17 | 100%
[5 empty] | 61.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11376.8231 | 183672.2911 | 61.18 | 100%
[5 empty] | 61.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11379.0896 | 183708.8821 | 61.19 | 100%
[5 empty] | 61.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11381.3561 | 183745.473 | 61.2 | 100%
[5 empty] | 61.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11383.6226 | 183782.0639 | 61.21 | 100%
[5 empty] | 61.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11385.8891 | 183818.6549 | 61.22 | 100%
[5 empty] | 61.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11388.1555 | 183855.2458 | 61.23 | 100%
[5 empty] | 61.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11390.422 | 183891.8368 | 61.24 | 100%
[5 empty] | 61.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11392.6885 | 183928.4277 | 61.25 | 100%
[5 empty] | 61.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11394.955 | 183965.0187 | 61.26 | 100%
[5 empty] | 61.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11397.2214 | 184001.6096 | 61.27 | 100%
[5 empty] | 61.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11399.4879 | 184038.2005 | 61.28 | 100%
[5 empty] | 61.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11401.7544 | 184074.7915 | 61.29 | 100%
[5 empty] | 61.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11404.0209 | 184111.3824 | 61.3 | 100%
[5 empty] | 61.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11406.2873 | 184147.9734 | 61.31 | 100%
[5 empty] | 61.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11408.5538 | 184184.5643 | 61.32 | 100%
[5 empty] | 61.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11410.8203 | 184221.1553 | 61.33 | 100%
[5 empty] | 61.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11413.0868 | 184257.7462 | 61.34 | 100%
[5 empty] | 61.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11415.3532 | 184294.3372 | 61.35 | 100%
[5 empty] | 61.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11417.6197 | 184330.9281 | 61.36 | 100%
[5 empty] | 61.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11419.8862 | 184367.519 | 61.37 | 100%
[5 empty] | 61.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11422.1527 | 184404.11 | 61.38 | 100%
[5 empty] | 61.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11424.4191 | 184440.7009 | 61.39 | 100%
[5 empty] | 61.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11426.6856 | 184477.2919 | 61.4 | 100%
[5 empty] | 61.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11428.9521 | 184513.8828 | 61.41 | 100%
[5 empty] | 61.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11431.2186 | 184550.4738 | 61.42 | 100%
[5 empty] | 61.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11433.485 | 184587.0647 | 61.43 | 100%
[5 empty] | 61.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11435.7515 | 184623.6556 | 61.44 | 100%
[5 empty] | 61.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11438.018 | 184660.2466 | 61.45 | 100%
[5 empty] | 61.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11440.2845 | 184696.8375 | 61.46 | 100%
[5 empty] | 61.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11442.5509 | 184733.4285 | 61.47 | 100%
[5 empty] | 61.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11444.8174 | 184770.0194 | 61.48 | 100%
[5 empty] | 61.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11447.0839 | 184806.6104 | 61.49 | 100%
[5 empty] | 61.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11449.3504 | 184843.2013 | 61.5 | 100%
[5 empty] | 61.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11451.6168 | 184879.7923 | 61.51 | 100%
[5 empty] | 61.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11453.8833 | 184916.3832 | 61.52 | 100%
[5 empty] | 61.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11456.1498 | 184952.9741 | 61.53 | 100%
[5 empty] | 61.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11458.4163 | 184989.5651 | 61.54 | 100%
[5 empty] | 61.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11460.6827 | 185026.156 | 61.55 | 100%
[5 empty] | 61.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11462.9492 | 185062.747 | 61.56 | 100%
[5 empty] | 61.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11465.2157 | 185099.3379 | 61.57 | 100%
[5 empty] | 61.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11467.4822 | 185135.9289 | 61.58 | 100%
[5 empty] | 61.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11469.7486 | 185172.5198 | 61.59 | 100%
[5 empty] | 61.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11472.0151 | 185209.1107 | 61.6 | 100%
[5 empty] | 61.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11474.2816 | 185245.7017 | 61.61 | 100%
[5 empty] | 61.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11476.5481 | 185282.2926 | 61.62 | 100%
[5 empty] | 61.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11478.8145 | 185318.8836 | 61.63 | 100%
[5 empty] | 61.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11481.081 | 185355.4745 | 61.64 | 100%
[5 empty] | 61.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11483.3475 | 185392.0655 | 61.65 | 100%
[5 empty] | 61.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11485.614 | 185428.6564 | 61.66 | 100%
[5 empty] | 61.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11487.8804 | 185465.2474 | 61.67 | 100%
[5 empty] | 61.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11490.1469 | 185501.8383 | 61.68 | 100%
[5 empty] | 61.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11492.4134 | 185538.4292 | 61.69 | 100%
[5 empty] | 61.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11494.6799 | 185575.0202 | 61.7 | 100%
[5 empty] | 61.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11496.9463 | 185611.6111 | 61.71 | 100%
[5 empty] | 61.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11499.2128 | 185648.2021 | 61.72 | 100%
[5 empty] | 61.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11501.4793 | 185684.793 | 61.73 | 100%
[5 empty] | 61.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11503.7458 | 185721.384 | 61.74 | 100%
[5 empty] | 61.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11506.0122 | 185757.9749 | 61.75 | 100%
[5 empty] | 61.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11508.2787 | 185794.5658 | 61.76 | 100%
[5 empty] | 61.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11510.5452 | 185831.1568 | 61.77 | 100%
[5 empty] | 61.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11512.8117 | 185867.7477 | 61.78 | 100%
[5 empty] | 61.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11515.0781 | 185904.3387 | 61.79 | 100%
[5 empty] | 61.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11517.3446 | 185940.9296 | 61.8 | 100%
[5 empty] | 61.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11519.6111 | 185977.5206 | 61.81 | 100%
[5 empty] | 61.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11521.8776 | 186014.1115 | 61.82 | 100%
[5 empty] | 61.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11524.144 | 186050.7024 | 61.83 | 100%
[5 empty] | 61.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11526.4105 | 186087.2934 | 61.84 | 100%
[5 empty] | 61.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11528.677 | 186123.8843 | 61.85 | 100%
[5 empty] | 61.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11530.9435 | 186160.4753 | 61.86 | 100%
[5 empty] | 61.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11533.2099 | 186197.0662 | 61.87 | 100%
[5 empty] | 61.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11535.4764 | 186233.6572 | 61.88 | 100%
[5 empty] | 61.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11537.7429 | 186270.2481 | 61.89 | 100%
[5 empty] | 61.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11540.0094 | 186306.8391 | 61.9 | 100%
[5 empty] | 61.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11542.2758 | 186343.43 | 61.91 | 100%
[5 empty] | 61.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11544.5423 | 186380.0209 | 61.92 | 100%
[5 empty] | 61.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11546.8088 | 186416.6119 | 61.93 | 100%
[5 empty] | 61.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11549.0753 | 186453.2028 | 61.94 | 100%
[5 empty] | 61.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11551.3417 | 186489.7938 | 61.95 | 100%
[5 empty] | 61.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11553.6082 | 186526.3847 | 61.96 | 100%
[5 empty] | 61.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11555.8747 | 186562.9757 | 61.97 | 100%
[5 empty] | 61.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11558.1412 | 186599.5666 | 61.98 | 100%
[5 empty] | 61.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11560.4076 | 186636.1575 | 61.99 | 100%
[5 empty] | 62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11562.6741 | 186672.7485 | 62 | 100%
[5 empty] | 62.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11564.9406 | 186709.3394 | 62.01 | 100%
[5 empty] | 62.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11567.2071 | 186745.9304 | 62.02 | 100%
[5 empty] | 62.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11569.4735 | 186782.5213 | 62.03 | 100%
[5 empty] | 62.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11571.74 | 186819.1123 | 62.04 | 100%
[5 empty] | 62.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11574.0065 | 186855.7032 | 62.05 | 100%
[5 empty] | 62.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11576.273 | 186892.2942 | 62.06 | 100%
[5 empty] | 62.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11578.5394 | 186928.8851 | 62.07 | 100%
[5 empty] | 62.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11580.8059 | 186965.476 | 62.08 | 100%
[5 empty] | 62.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11583.0724 | 187002.067 | 62.09 | 100%
[5 empty] | 62.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11585.3389 | 187038.6579 | 62.1 | 100%
[5 empty] | 62.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11587.6053 | 187075.2489 | 62.11 | 100%
[5 empty] | 62.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11589.8718 | 187111.8398 | 62.12 | 100%
[5 empty] | 62.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11592.1383 | 187148.4308 | 62.13 | 100%
[5 empty] | 62.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11594.4048 | 187185.0217 | 62.14 | 100%
[5 empty] | 62.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11596.6712 | 187221.6126 | 62.15 | 100%
[5 empty] | 62.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11598.9377 | 187258.2036 | 62.16 | 100%
[5 empty] | 62.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11601.2042 | 187294.7945 | 62.17 | 100%
[5 empty] | 62.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11603.4707 | 187331.3855 | 62.18 | 100%
[5 empty] | 62.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11605.7371 | 187367.9764 | 62.19 | 100%
[5 empty] | 62.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11608.0036 | 187404.5674 | 62.2 | 100%
[5 empty] | 62.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11610.2701 | 187441.1583 | 62.21 | 100%
[5 empty] | 62.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11612.5366 | 187477.7492 | 62.22 | 100%
[5 empty] | 62.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11614.803 | 187514.3402 | 62.23 | 100%
[5 empty] | 62.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11617.0695 | 187550.9311 | 62.24 | 100%
[5 empty] | 62.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11619.336 | 187587.5221 | 62.25 | 100%
[5 empty] | 62.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11621.6025 | 187624.113 | 62.26 | 100%
[5 empty] | 62.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11623.8689 | 187660.704 | 62.27 | 100%
[5 empty] | 62.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11626.1354 | 187697.2949 | 62.28 | 100%
[5 empty] | 62.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11628.4019 | 187733.8859 | 62.29 | 100%
[5 empty] | 62.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11630.6684 | 187770.4768 | 62.3 | 100%
[5 empty] | 62.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11632.9348 | 187807.0677 | 62.31 | 100%
[5 empty] | 62.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11635.2013 | 187843.6587 | 62.32 | 100%
[5 empty] | 62.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11637.4678 | 187880.2496 | 62.33 | 100%
[5 empty] | 62.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11639.7343 | 187916.8406 | 62.34 | 100%
[5 empty] | 62.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11642.0007 | 187953.4315 | 62.35 | 100%
[5 empty] | 62.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11644.2672 | 187990.0225 | 62.36 | 100%
[5 empty] | 62.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11646.5337 | 188026.6134 | 62.37 | 100%
[5 empty] | 62.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11648.8002 | 188063.2043 | 62.38 | 100%
[5 empty] | 62.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11651.0666 | 188099.7953 | 62.39 | 100%
[5 empty] | 62.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11653.3331 | 188136.3862 | 62.4 | 100%
[5 empty] | 62.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11655.5996 | 188172.9772 | 62.41 | 100%
[5 empty] | 62.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11657.8661 | 188209.5681 | 62.42 | 100%
[5 empty] | 62.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11660.1326 | 188246.1591 | 62.43 | 100%
[5 empty] | 62.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11662.399 | 188282.75 | 62.44 | 100%
[5 empty] | 62.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11664.6655 | 188319.341 | 62.45 | 100%
[5 empty] | 62.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11666.932 | 188355.9319 | 62.46 | 100%
[5 empty] | 62.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11669.1985 | 188392.5228 | 62.47 | 100%
[5 empty] | 62.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11671.4649 | 188429.1138 | 62.48 | 100%
[5 empty] | 62.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11673.7314 | 188465.7047 | 62.49 | 100%
[5 empty] | 62.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11675.9979 | 188502.2957 | 62.5 | 100%
[5 empty] | 62.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11678.2644 | 188538.8866 | 62.51 | 100%
[5 empty] | 62.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11680.5308 | 188575.4776 | 62.52 | 100%
[5 empty] | 62.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11682.7973 | 188612.0685 | 62.53 | 100%
[5 empty] | 62.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11685.0638 | 188648.6594 | 62.54 | 100%
[5 empty] | 62.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11687.3303 | 188685.2504 | 62.55 | 100%
[5 empty] | 62.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11689.5967 | 188721.8413 | 62.56 | 100%
[5 empty] | 62.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11691.8632 | 188758.4323 | 62.57 | 100%
[5 empty] | 62.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11694.1297 | 188795.0232 | 62.58 | 100%
[5 empty] | 62.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11696.3962 | 188831.6142 | 62.59 | 100%
[5 empty] | 62.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11698.6626 | 188868.2051 | 62.6 | 100%
[5 empty] | 62.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11700.9291 | 188904.7961 | 62.61 | 100%
[5 empty] | 62.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11703.1956 | 188941.387 | 62.62 | 100%
[5 empty] | 62.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11705.4621 | 188977.9779 | 62.63 | 100%
[5 empty] | 62.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11707.7285 | 189014.5689 | 62.64 | 100%
[5 empty] | 62.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11709.995 | 189051.1598 | 62.65 | 100%
[5 empty] | 62.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11712.2615 | 189087.7508 | 62.66 | 100%
[5 empty] | 62.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11714.528 | 189124.3417 | 62.67 | 100%
[5 empty] | 62.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11716.7944 | 189160.9327 | 62.68 | 100%
[5 empty] | 62.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11719.0609 | 189197.5236 | 62.69 | 100%
[5 empty] | 62.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11721.3274 | 189234.1145 | 62.7 | 100%
[5 empty] | 62.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11723.5939 | 189270.7055 | 62.71 | 100%
[5 empty] | 62.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11725.8603 | 189307.2964 | 62.72 | 100%
[5 empty] | 62.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11728.1268 | 189343.8874 | 62.73 | 100%
[5 empty] | 62.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11730.3933 | 189380.4783 | 62.74 | 100%
[5 empty] | 62.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11732.6598 | 189417.0693 | 62.75 | 100%
[5 empty] | 62.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11734.9262 | 189453.6602 | 62.76 | 100%
[5 empty] | 62.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11737.1927 | 189490.2511 | 62.77 | 100%
[5 empty] | 62.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11739.4592 | 189526.8421 | 62.78 | 100%
[5 empty] | 62.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11741.7257 | 189563.433 | 62.79 | 100%
[5 empty] | 62.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11743.9921 | 189600.024 | 62.8 | 100%
[5 empty] | 62.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11746.2586 | 189636.6149 | 62.81 | 100%
[5 empty] | 62.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11748.5251 | 189673.2059 | 62.82 | 100%
[5 empty] | 62.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11750.7916 | 189709.7968 | 62.83 | 100%
[5 empty] | 62.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11753.058 | 189746.3878 | 62.84 | 100%
[5 empty] | 62.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11755.3245 | 189782.9787 | 62.85 | 100%
[5 empty] | 62.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11757.591 | 189819.5696 | 62.86 | 100%
[5 empty] | 62.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11759.8575 | 189856.1606 | 62.87 | 100%
[5 empty] | 62.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11762.1239 | 189892.7515 | 62.88 | 100%
[5 empty] | 62.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11764.3904 | 189929.3425 | 62.89 | 100%
[5 empty] | 62.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11766.6569 | 189965.9334 | 62.9 | 100%
[5 empty] | 62.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11768.9234 | 190002.5244 | 62.91 | 100%
[5 empty] | 62.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11771.1898 | 190039.1153 | 62.92 | 100%
[5 empty] | 62.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11773.4563 | 190075.7062 | 62.93 | 100%
[5 empty] | 62.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11775.7228 | 190112.2972 | 62.94 | 100%
[5 empty] | 62.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11777.9893 | 190148.8881 | 62.95 | 100%
[5 empty] | 62.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11780.2557 | 190185.4791 | 62.96 | 100%
[5 empty] | 62.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11782.5222 | 190222.07 | 62.97 | 100%
[5 empty] | 62.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11784.7887 | 190258.661 | 62.98 | 100%
[5 empty] | 62.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11787.0552 | 190295.2519 | 62.99 | 100%
[5 empty] | 63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11789.3216 | 190331.8429 | 63 | 100%
[5 empty] | 63.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11791.5881 | 190368.4338 | 63.01 | 100%
[5 empty] | 63.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11793.8546 | 190405.0247 | 63.02 | 100%
[5 empty] | 63.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11796.1211 | 190441.6157 | 63.03 | 100%
[5 empty] | 63.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11798.3875 | 190478.2066 | 63.04 | 100%
[5 empty] | 63.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11800.654 | 190514.7976 | 63.05 | 100%
[5 empty] | 63.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11802.9205 | 190551.3885 | 63.06 | 100%
[5 empty] | 63.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11805.187 | 190587.9795 | 63.07 | 100%
[5 empty] | 63.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11807.4534 | 190624.5704 | 63.08 | 100%
[5 empty] | 63.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11809.7199 | 190661.1613 | 63.09 | 100%
[5 empty] | 63.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11811.9864 | 190697.7523 | 63.1 | 100%
[5 empty] | 63.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11814.2529 | 190734.3432 | 63.11 | 100%
[5 empty] | 63.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11816.5193 | 190770.9342 | 63.12 | 100%
[5 empty] | 63.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11818.7858 | 190807.5251 | 63.13 | 100%
[5 empty] | 63.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11821.0523 | 190844.1161 | 63.14 | 100%
[5 empty] | 63.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11823.3188 | 190880.707 | 63.15 | 100%
[5 empty] | 63.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11825.5852 | 190917.298 | 63.16 | 100%
[5 empty] | 63.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11827.8517 | 190953.8889 | 63.17 | 100%
[5 empty] | 63.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11830.1182 | 190990.4798 | 63.18 | 100%
[5 empty] | 63.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11832.3847 | 191027.0708 | 63.19 | 100%
[5 empty] | 63.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11834.6511 | 191063.6617 | 63.2 | 100%
[5 empty] | 63.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11836.9176 | 191100.2527 | 63.21 | 100%
[5 empty] | 63.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11839.1841 | 191136.8436 | 63.22 | 100%
[5 empty] | 63.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11841.4506 | 191173.4346 | 63.23 | 100%
[5 empty] | 63.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11843.717 | 191210.0255 | 63.24 | 100%
[5 empty] | 63.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11845.9835 | 191246.6164 | 63.25 | 100%
[5 empty] | 63.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11848.25 | 191283.2074 | 63.26 | 100%
[5 empty] | 63.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11850.5165 | 191319.7983 | 63.27 | 100%
[5 empty] | 63.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11852.7829 | 191356.3893 | 63.28 | 100%
[5 empty] | 63.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11855.0494 | 191392.9802 | 63.29 | 100%
[5 empty] | 63.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11857.3159 | 191429.5712 | 63.3 | 100%
[5 empty] | 63.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11859.5824 | 191466.1621 | 63.31 | 100%
[5 empty] | 63.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11861.8488 | 191502.753 | 63.32 | 100%
[5 empty] | 63.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11864.1153 | 191539.344 | 63.33 | 100%
[5 empty] | 63.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11866.3818 | 191575.9349 | 63.34 | 100%
[5 empty] | 63.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11868.6483 | 191612.5259 | 63.35 | 100%
[5 empty] | 63.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11870.9147 | 191649.1168 | 63.36 | 100%
[5 empty] | 63.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11873.1812 | 191685.7078 | 63.37 | 100%
[5 empty] | 63.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11875.4477 | 191722.2987 | 63.38 | 100%
[5 empty] | 63.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11877.7142 | 191758.8897 | 63.39 | 100%
[5 empty] | 63.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11879.9806 | 191795.4806 | 63.4 | 100%
[5 empty] | 63.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11882.2471 | 191832.0715 | 63.41 | 100%
[5 empty] | 63.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11884.5136 | 191868.6625 | 63.42 | 100%
[5 empty] | 63.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11886.7801 | 191905.2534 | 63.43 | 100%
[5 empty] | 63.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11889.0465 | 191941.8444 | 63.44 | 100%
[5 empty] | 63.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11891.313 | 191978.4353 | 63.45 | 100%
[5 empty] | 63.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11893.5795 | 192015.0263 | 63.46 | 100%
[5 empty] | 63.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11895.846 | 192051.6172 | 63.47 | 100%
[5 empty] | 63.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11898.1124 | 192088.2081 | 63.48 | 100%
[5 empty] | 63.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11900.3789 | 192124.7991 | 63.49 | 100%
[5 empty] | 63.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11902.6454 | 192161.39 | 63.5 | 100%
[5 empty] | 63.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11904.9119 | 192197.981 | 63.51 | 100%
[5 empty] | 63.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11907.1783 | 192234.5719 | 63.52 | 100%
[5 empty] | 63.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11909.4448 | 192271.1629 | 63.53 | 100%
[5 empty] | 63.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11911.7113 | 192307.7538 | 63.54 | 100%
[5 empty] | 63.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11913.9778 | 192344.3448 | 63.55 | 100%
[5 empty] | 63.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11916.2442 | 192380.9357 | 63.56 | 100%
[5 empty] | 63.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11918.5107 | 192417.5266 | 63.57 | 100%
[5 empty] | 63.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11920.7772 | 192454.1176 | 63.58 | 100%
[5 empty] | 63.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11923.0437 | 192490.7085 | 63.59 | 100%
[5 empty] | 63.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11925.3102 | 192527.2995 | 63.6 | 100%
[5 empty] | 63.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11927.5766 | 192563.8904 | 63.61 | 100%
[5 empty] | 63.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11929.8431 | 192600.4814 | 63.62 | 100%
[5 empty] | 63.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11932.1096 | 192637.0723 | 63.63 | 100%
[5 empty] | 63.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11934.3761 | 192673.6632 | 63.64 | 100%
[5 empty] | 63.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11936.6425 | 192710.2542 | 63.65 | 100%
[5 empty] | 63.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11938.909 | 192746.8451 | 63.66 | 100%
[5 empty] | 63.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11941.1755 | 192783.4361 | 63.67 | 100%
[5 empty] | 63.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11943.442 | 192820.027 | 63.68 | 100%
[5 empty] | 63.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11945.7084 | 192856.618 | 63.69 | 100%
[5 empty] | 63.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11947.9749 | 192893.2089 | 63.7 | 100%
[5 empty] | 63.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11950.2414 | 192929.7999 | 63.71 | 100%
[5 empty] | 63.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11952.5079 | 192966.3908 | 63.72 | 100%
[5 empty] | 63.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11954.7743 | 193002.9817 | 63.73 | 100%
[5 empty] | 63.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11957.0408 | 193039.5727 | 63.74 | 100%
[5 empty] | 63.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11959.3073 | 193076.1636 | 63.75 | 100%
[5 empty] | 63.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11961.5738 | 193112.7546 | 63.76 | 100%
[5 empty] | 63.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11963.8402 | 193149.3455 | 63.77 | 100%
[5 empty] | 63.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11966.1067 | 193185.9365 | 63.78 | 100%
[5 empty] | 63.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11968.3732 | 193222.5274 | 63.79 | 100%
[5 empty] | 63.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11970.6397 | 193259.1183 | 63.8 | 100%
[5 empty] | 63.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11972.9061 | 193295.7093 | 63.81 | 100%
[5 empty] | 63.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11975.1726 | 193332.3002 | 63.82 | 100%
[5 empty] | 63.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11977.4391 | 193368.8912 | 63.83 | 100%
[5 empty] | 63.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11979.7056 | 193405.4821 | 63.84 | 100%
[5 empty] | 63.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11981.972 | 193442.0731 | 63.85 | 100%
[5 empty] | 63.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11984.2385 | 193478.664 | 63.86 | 100%
[5 empty] | 63.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11986.505 | 193515.2549 | 63.87 | 100%
[5 empty] | 63.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11988.7715 | 193551.8459 | 63.88 | 100%
[5 empty] | 63.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11991.0379 | 193588.4368 | 63.89 | 100%
[5 empty] | 63.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11993.3044 | 193625.0278 | 63.9 | 100%
[5 empty] | 63.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11995.5709 | 193661.6187 | 63.91 | 100%
[5 empty] | 63.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 11997.8374 | 193698.2097 | 63.92 | 100%
[5 empty] | 63.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12000.1038 | 193734.8006 | 63.93 | 100%
[5 empty] | 63.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12002.3703 | 193771.3916 | 63.94 | 100%
[5 empty] | 63.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12004.6368 | 193807.9825 | 63.95 | 100%
[5 empty] | 63.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12006.9033 | 193844.5734 | 63.96 | 100%
[5 empty] | 63.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12009.1697 | 193881.1644 | 63.97 | 100%
[5 empty] | 63.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12011.4362 | 193917.7553 | 63.98 | 100%
[5 empty] | 63.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12013.7027 | 193954.3463 | 63.99 | 100%
[5 empty] | 64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12015.9692 | 193990.9372 | 64 | 100%
[5 empty] | 64.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12018.2356 | 194027.5282 | 64.01 | 100%
[5 empty] | 64.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12020.5021 | 194064.1191 | 64.02 | 100%
[5 empty] | 64.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12022.7686 | 194100.71 | 64.03 | 100%
[5 empty] | 64.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12025.0351 | 194137.301 | 64.04 | 100%
[5 empty] | 64.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12027.3015 | 194173.8919 | 64.05 | 100%
[5 empty] | 64.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12029.568 | 194210.4829 | 64.06 | 100%
[5 empty] | 64.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12031.8345 | 194247.0738 | 64.07 | 100%
[5 empty] | 64.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12034.101 | 194283.6648 | 64.08 | 100%
[5 empty] | 64.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12036.3674 | 194320.2557 | 64.09 | 100%
[5 empty] | 64.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12038.6339 | 194356.8467 | 64.1 | 100%
[5 empty] | 64.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12040.9004 | 194393.4376 | 64.11 | 100%
[5 empty] | 64.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12043.1669 | 194430.0285 | 64.12 | 100%
[5 empty] | 64.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12045.4333 | 194466.6195 | 64.13 | 100%
[5 empty] | 64.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12047.6998 | 194503.2104 | 64.14 | 100%
[5 empty] | 64.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12049.9663 | 194539.8014 | 64.15 | 100%
[5 empty] | 64.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12052.2328 | 194576.3923 | 64.16 | 100%
[5 empty] | 64.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12054.4992 | 194612.9833 | 64.17 | 100%
[5 empty] | 64.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12056.7657 | 194649.5742 | 64.18 | 100%
[5 empty] | 64.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12059.0322 | 194686.1651 | 64.19 | 100%
[5 empty] | 64.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12061.2987 | 194722.7561 | 64.2 | 100%
[5 empty] | 64.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12063.5651 | 194759.347 | 64.21 | 100%
[5 empty] | 64.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12065.8316 | 194795.938 | 64.22 | 100%
[5 empty] | 64.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12068.0981 | 194832.5289 | 64.23 | 100%
[5 empty] | 64.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12070.3646 | 194869.1199 | 64.24 | 100%
[5 empty] | 64.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12072.631 | 194905.7108 | 64.25 | 100%
[5 empty] | 64.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12074.8975 | 194942.3017 | 64.26 | 100%
[5 empty] | 64.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12077.164 | 194978.8927 | 64.27 | 100%
[5 empty] | 64.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12079.4305 | 195015.4836 | 64.28 | 100%
[5 empty] | 64.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12081.6969 | 195052.0746 | 64.29 | 100%
[5 empty] | 64.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12083.9634 | 195088.6655 | 64.3 | 100%
[5 empty] | 64.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12086.2299 | 195125.2565 | 64.31 | 100%
[5 empty] | 64.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12088.4964 | 195161.8474 | 64.32 | 100%
[5 empty] | 64.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12090.7628 | 195198.4384 | 64.33 | 100%
[5 empty] | 64.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12093.0293 | 195235.0293 | 64.34 | 100%
[5 empty] | 64.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12095.2958 | 195271.6202 | 64.35 | 100%
[5 empty] | 64.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12097.5623 | 195308.2112 | 64.36 | 100%
[5 empty] | 64.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12099.8287 | 195344.8021 | 64.37 | 100%
[5 empty] | 64.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12102.0952 | 195381.3931 | 64.38 | 100%
[5 empty] | 64.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12104.3617 | 195417.984 | 64.39 | 100%
[5 empty] | 64.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12106.6282 | 195454.575 | 64.4 | 100%
[5 empty] | 64.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12108.8946 | 195491.1659 | 64.41 | 100%
[5 empty] | 64.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12111.1611 | 195527.7568 | 64.42 | 100%
[5 empty] | 64.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12113.4276 | 195564.3478 | 64.43 | 100%
[5 empty] | 64.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12115.6941 | 195600.9387 | 64.44 | 100%
[5 empty] | 64.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12117.9605 | 195637.5297 | 64.45 | 100%
[5 empty] | 64.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12120.227 | 195674.1206 | 64.46 | 100%
[5 empty] | 64.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12122.4935 | 195710.7116 | 64.47 | 100%
[5 empty] | 64.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12124.76 | 195747.3025 | 64.48 | 100%
[5 empty] | 64.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12127.0264 | 195783.8935 | 64.49 | 100%
[5 empty] | 64.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12129.2929 | 195820.4844 | 64.5 | 100%
[5 empty] | 64.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12131.5594 | 195857.0753 | 64.51 | 100%
[5 empty] | 64.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12133.8259 | 195893.6663 | 64.52 | 100%
[5 empty] | 64.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12136.0923 | 195930.2572 | 64.53 | 100%
[5 empty] | 64.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12138.3588 | 195966.8482 | 64.54 | 100%
[5 empty] | 64.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12140.6253 | 196003.4391 | 64.55 | 100%
[5 empty] | 64.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12142.8918 | 196040.0301 | 64.56 | 100%
[5 empty] | 64.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12145.1582 | 196076.621 | 64.57 | 100%
[5 empty] | 64.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12147.4247 | 196113.2119 | 64.58 | 100%
[5 empty] | 64.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12149.6912 | 196149.8029 | 64.59 | 100%
[5 empty] | 64.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12151.9577 | 196186.3938 | 64.6 | 100%
[5 empty] | 64.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12154.2241 | 196222.9848 | 64.61 | 100%
[5 empty] | 64.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12156.4906 | 196259.5757 | 64.62 | 100%
[5 empty] | 64.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12158.7571 | 196296.1667 | 64.63 | 100%
[5 empty] | 64.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12161.0236 | 196332.7576 | 64.64 | 100%
[5 empty] | 64.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12163.29 | 196369.3486 | 64.65 | 100%
[5 empty] | 64.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12165.5565 | 196405.9395 | 64.66 | 100%
[5 empty] | 64.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12167.823 | 196442.5304 | 64.67 | 100%
[5 empty] | 64.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12170.0895 | 196479.1214 | 64.68 | 100%
[5 empty] | 64.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12172.3559 | 196515.7123 | 64.69 | 100%
[5 empty] | 64.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12174.6224 | 196552.3033 | 64.7 | 100%
[5 empty] | 64.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12176.8889 | 196588.8942 | 64.71 | 100%
[5 empty] | 64.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12179.1554 | 196625.4852 | 64.72 | 100%
[5 empty] | 64.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12181.4218 | 196662.0761 | 64.73 | 100%
[5 empty] | 64.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12183.6883 | 196698.667 | 64.74 | 100%
[5 empty] | 64.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12185.9548 | 196735.258 | 64.75 | 100%
[5 empty] | 64.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12188.2213 | 196771.8489 | 64.76 | 100%
[5 empty] | 64.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12190.4877 | 196808.4399 | 64.77 | 100%
[5 empty] | 64.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12192.7542 | 196845.0308 | 64.78 | 100%
[5 empty] | 64.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12195.0207 | 196881.6218 | 64.79 | 100%
[5 empty] | 64.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12197.2872 | 196918.2127 | 64.8 | 100%
[5 empty] | 64.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12199.5537 | 196954.8036 | 64.81 | 100%
[5 empty] | 64.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12201.8201 | 196991.3946 | 64.82 | 100%
[5 empty] | 64.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12204.0866 | 197027.9855 | 64.83 | 100%
[5 empty] | 64.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12206.3531 | 197064.5765 | 64.84 | 100%
[5 empty] | 64.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12208.6196 | 197101.1674 | 64.85 | 100%
[5 empty] | 64.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12210.886 | 197137.7584 | 64.86 | 100%
[5 empty] | 64.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12213.1525 | 197174.3493 | 64.87 | 100%
[5 empty] | 64.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12215.419 | 197210.9403 | 64.88 | 100%
[5 empty] | 64.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12217.6855 | 197247.5312 | 64.89 | 100%
[5 empty] | 64.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12219.9519 | 197284.1221 | 64.9 | 100%
[5 empty] | 64.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12222.2184 | 197320.7131 | 64.91 | 100%
[5 empty] | 64.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12224.4849 | 197357.304 | 64.92 | 100%
[5 empty] | 64.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12226.7514 | 197393.895 | 64.93 | 100%
[5 empty] | 64.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12229.0178 | 197430.4859 | 64.94 | 100%
[5 empty] | 64.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12231.2843 | 197467.0769 | 64.95 | 100%
[5 empty] | 64.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12233.5508 | 197503.6678 | 64.96 | 100%
[5 empty] | 64.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12235.8173 | 197540.2587 | 64.97 | 100%
[5 empty] | 64.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12238.0837 | 197576.8497 | 64.98 | 100%
[5 empty] | 64.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12240.3502 | 197613.4406 | 64.99 | 100%
[5 empty] | 65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12242.6167 | 197650.0316 | 65 | 100%
[5 empty] | 65.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12244.8832 | 197686.6225 | 65.01 | 100%
[5 empty] | 65.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12247.1496 | 197723.2135 | 65.02 | 100%
[5 empty] | 65.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12249.4161 | 197759.8044 | 65.03 | 100%
[5 empty] | 65.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12251.6826 | 197796.3954 | 65.04 | 100%
[5 empty] | 65.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12253.9491 | 197832.9863 | 65.05 | 100%
[5 empty] | 65.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12256.2155 | 197869.5772 | 65.06 | 100%
[5 empty] | 65.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12258.482 | 197906.1682 | 65.07 | 100%
[5 empty] | 65.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12260.7485 | 197942.7591 | 65.08 | 100%
[5 empty] | 65.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12263.015 | 197979.3501 | 65.09 | 100%
[5 empty] | 65.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12265.2814 | 198015.941 | 65.1 | 100%
[5 empty] | 65.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12267.5479 | 198052.532 | 65.11 | 100%
[5 empty] | 65.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12269.8144 | 198089.1229 | 65.12 | 100%
[5 empty] | 65.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12272.0809 | 198125.7138 | 65.13 | 100%
[5 empty] | 65.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12274.3473 | 198162.3048 | 65.14 | 100%
[5 empty] | 65.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12276.6138 | 198198.8957 | 65.15 | 100%
[5 empty] | 65.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12278.8803 | 198235.4867 | 65.16 | 100%
[5 empty] | 65.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12281.1468 | 198272.0776 | 65.17 | 100%
[5 empty] | 65.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12283.4132 | 198308.6686 | 65.18 | 100%
[5 empty] | 65.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12285.6797 | 198345.2595 | 65.19 | 100%
[5 empty] | 65.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12287.9462 | 198381.8505 | 65.2 | 100%
[5 empty] | 65.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12290.2127 | 198418.4414 | 65.21 | 100%
[5 empty] | 65.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12292.4791 | 198455.0323 | 65.22 | 100%
[5 empty] | 65.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12294.7456 | 198491.6233 | 65.23 | 100%
[5 empty] | 65.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12297.0121 | 198528.2142 | 65.24 | 100%
[5 empty] | 65.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12299.2786 | 198564.8052 | 65.25 | 100%
[5 empty] | 65.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12301.545 | 198601.3961 | 65.26 | 100%
[5 empty] | 65.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12303.8115 | 198637.9871 | 65.27 | 100%
[5 empty] | 65.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12306.078 | 198674.578 | 65.28 | 100%
[5 empty] | 65.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12308.3445 | 198711.1689 | 65.29 | 100%
[5 empty] | 65.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12310.6109 | 198747.7599 | 65.3 | 100%
[5 empty] | 65.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12312.8774 | 198784.3508 | 65.31 | 100%
[5 empty] | 65.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12315.1439 | 198820.9418 | 65.32 | 100%
[5 empty] | 65.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12317.4104 | 198857.5327 | 65.33 | 100%
[5 empty] | 65.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12319.6768 | 198894.1237 | 65.34 | 100%
[5 empty] | 65.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12321.9433 | 198930.7146 | 65.35 | 100%
[5 empty] | 65.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12324.2098 | 198967.3055 | 65.36 | 100%
[5 empty] | 65.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12326.4763 | 199003.8965 | 65.37 | 100%
[5 empty] | 65.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12328.7427 | 199040.4874 | 65.38 | 100%
[5 empty] | 65.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12331.0092 | 199077.0784 | 65.39 | 100%
[5 empty] | 65.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12333.2757 | 199113.6693 | 65.4 | 100%
[5 empty] | 65.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12335.5422 | 199150.2603 | 65.41 | 100%
[5 empty] | 65.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12337.8086 | 199186.8512 | 65.42 | 100%
[5 empty] | 65.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12340.0751 | 199223.4422 | 65.43 | 100%
[5 empty] | 65.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12342.3416 | 199260.0331 | 65.44 | 100%
[5 empty] | 65.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12344.6081 | 199296.624 | 65.45 | 100%
[5 empty] | 65.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12346.8745 | 199333.215 | 65.46 | 100%
[5 empty] | 65.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12349.141 | 199369.8059 | 65.47 | 100%
[5 empty] | 65.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12351.4075 | 199406.3969 | 65.48 | 100%
[5 empty] | 65.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12353.674 | 199442.9878 | 65.49 | 100%
[5 empty] | 65.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12355.9404 | 199479.5788 | 65.5 | 100%
[5 empty] | 65.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12358.2069 | 199516.1697 | 65.51 | 100%
[5 empty] | 65.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12360.4734 | 199552.7606 | 65.52 | 100%
[5 empty] | 65.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12362.7399 | 199589.3516 | 65.53 | 100%
[5 empty] | 65.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12365.0063 | 199625.9425 | 65.54 | 100%
[5 empty] | 65.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12367.2728 | 199662.5335 | 65.55 | 100%
[5 empty] | 65.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12369.5393 | 199699.1244 | 65.56 | 100%
[5 empty] | 65.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12371.8058 | 199735.7154 | 65.57 | 100%
[5 empty] | 65.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12374.0722 | 199772.3063 | 65.58 | 100%
[5 empty] | 65.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12376.3387 | 199808.8973 | 65.59 | 100%
[5 empty] | 65.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12378.6052 | 199845.4882 | 65.6 | 100%
[5 empty] | 65.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12380.8717 | 199882.0791 | 65.61 | 100%
[5 empty] | 65.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12383.1381 | 199918.6701 | 65.62 | 100%
[5 empty] | 65.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12385.4046 | 199955.261 | 65.63 | 100%
[5 empty] | 65.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12387.6711 | 199991.852 | 65.64 | 100%
[5 empty] | 65.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12389.9376 | 200028.4429 | 65.65 | 100%
[5 empty] | 65.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12392.204 | 200065.0339 | 65.66 | 100%
[5 empty] | 65.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12394.4705 | 200101.6248 | 65.67 | 100%
[5 empty] | 65.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12396.737 | 200138.2157 | 65.68 | 100%
[5 empty] | 65.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12399.0035 | 200174.8067 | 65.69 | 100%
[5 empty] | 65.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12401.2699 | 200211.3976 | 65.7 | 100%
[5 empty] | 65.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12403.5364 | 200247.9886 | 65.71 | 100%
[5 empty] | 65.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12405.8029 | 200284.5795 | 65.72 | 100%
[5 empty] | 65.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12408.0694 | 200321.1705 | 65.73 | 100%
[5 empty] | 65.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12410.3358 | 200357.7614 | 65.74 | 100%
[5 empty] | 65.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12412.6023 | 200394.3523 | 65.75 | 100%
[5 empty] | 65.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12414.8688 | 200430.9433 | 65.76 | 100%
[5 empty] | 65.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12417.1353 | 200467.5342 | 65.77 | 100%
[5 empty] | 65.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12419.4017 | 200504.1252 | 65.78 | 100%
[5 empty] | 65.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12421.6682 | 200540.7161 | 65.79 | 100%
[5 empty] | 65.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12423.9347 | 200577.3071 | 65.8 | 100%
[5 empty] | 65.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12426.2012 | 200613.898 | 65.81 | 100%
[5 empty] | 65.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12428.4676 | 200650.489 | 65.82 | 100%
[5 empty] | 65.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12430.7341 | 200687.0799 | 65.83 | 100%
[5 empty] | 65.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12433.0006 | 200723.6708 | 65.84 | 100%
[5 empty] | 65.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12435.2671 | 200760.2618 | 65.85 | 100%
[5 empty] | 65.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12437.5335 | 200796.8527 | 65.86 | 100%
[5 empty] | 65.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12439.8 | 200833.4437 | 65.87 | 100%
[5 empty] | 65.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12442.0665 | 200870.0346 | 65.88 | 100%
[5 empty] | 65.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12444.333 | 200906.6256 | 65.89 | 100%
[5 empty] | 65.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12446.5994 | 200943.2165 | 65.9 | 100%
[5 empty] | 65.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12448.8659 | 200979.8074 | 65.91 | 100%
[5 empty] | 65.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12451.1324 | 201016.3984 | 65.92 | 100%
[5 empty] | 65.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12453.3989 | 201052.9893 | 65.93 | 100%
[5 empty] | 65.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12455.6653 | 201089.5803 | 65.94 | 100%
[5 empty] | 65.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12457.9318 | 201126.1712 | 65.95 | 100%
[5 empty] | 65.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12460.1983 | 201162.7622 | 65.96 | 100%
[5 empty] | 65.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12462.4648 | 201199.3531 | 65.97 | 100%
[5 empty] | 65.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12464.7313 | 201235.9441 | 65.98 | 100%
[5 empty] | 65.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12466.9977 | 201272.535 | 65.99 | 100%
[5 empty] | 66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12469.2642 | 201309.1259 | 66 | 100%
[5 empty] | 66.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12471.5307 | 201345.7169 | 66.01 | 100%
[5 empty] | 66.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12473.7972 | 201382.3078 | 66.02 | 100%
[5 empty] | 66.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12476.0636 | 201418.8988 | 66.03 | 100%
[5 empty] | 66.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12478.3301 | 201455.4897 | 66.04 | 100%
[5 empty] | 66.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12480.5966 | 201492.0807 | 66.05 | 100%
[5 empty] | 66.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12482.8631 | 201528.6716 | 66.06 | 100%
[5 empty] | 66.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12485.1295 | 201565.2625 | 66.07 | 100%
[5 empty] | 66.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12487.396 | 201601.8535 | 66.08 | 100%
[5 empty] | 66.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12489.6625 | 201638.4444 | 66.09 | 100%
[5 empty] | 66.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12491.929 | 201675.0354 | 66.1 | 100%
[5 empty] | 66.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12494.1954 | 201711.6263 | 66.11 | 100%
[5 empty] | 66.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12496.4619 | 201748.2173 | 66.12 | 100%
[5 empty] | 66.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12498.7284 | 201784.8082 | 66.13 | 100%
[5 empty] | 66.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12500.9949 | 201821.3992 | 66.14 | 100%
[5 empty] | 66.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12503.2613 | 201857.9901 | 66.15 | 100%
[5 empty] | 66.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12505.5278 | 201894.581 | 66.16 | 100%
[5 empty] | 66.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12507.7943 | 201931.172 | 66.17 | 100%
[5 empty] | 66.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12510.0608 | 201967.7629 | 66.18 | 100%
[5 empty] | 66.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12512.3272 | 202004.3539 | 66.19 | 100%
[5 empty] | 66.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12514.5937 | 202040.9448 | 66.2 | 100%
[5 empty] | 66.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12516.8602 | 202077.5358 | 66.21 | 100%
[5 empty] | 66.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12519.1267 | 202114.1267 | 66.22 | 100%
[5 empty] | 66.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12521.3931 | 202150.7176 | 66.23 | 100%
[5 empty] | 66.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12523.6596 | 202187.3086 | 66.24 | 100%
[5 empty] | 66.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12525.9261 | 202223.8995 | 66.25 | 100%
[5 empty] | 66.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12528.1926 | 202260.4905 | 66.26 | 100%
[5 empty] | 66.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12530.459 | 202297.0814 | 66.27 | 100%
[5 empty] | 66.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12532.7255 | 202333.6724 | 66.28 | 100%
[5 empty] | 66.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12534.992 | 202370.2633 | 66.29 | 100%
[5 empty] | 66.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12537.2585 | 202406.8542 | 66.3 | 100%
[5 empty] | 66.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12539.5249 | 202443.4452 | 66.31 | 100%
[5 empty] | 66.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12541.7914 | 202480.0361 | 66.32 | 100%
[5 empty] | 66.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12544.0579 | 202516.6271 | 66.33 | 100%
[5 empty] | 66.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12546.3244 | 202553.218 | 66.34 | 100%
[5 empty] | 66.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12548.5908 | 202589.809 | 66.35 | 100%
[5 empty] | 66.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12550.8573 | 202626.3999 | 66.36 | 100%
[5 empty] | 66.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12553.1238 | 202662.9909 | 66.37 | 100%
[5 empty] | 66.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12555.3903 | 202699.5818 | 66.38 | 100%
[5 empty] | 66.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12557.6567 | 202736.1727 | 66.39 | 100%
[5 empty] | 66.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12559.9232 | 202772.7637 | 66.4 | 100%
[5 empty] | 66.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12562.1897 | 202809.3546 | 66.41 | 100%
[5 empty] | 66.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12564.4562 | 202845.9456 | 66.42 | 100%
[5 empty] | 66.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12566.7226 | 202882.5365 | 66.43 | 100%
[5 empty] | 66.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12568.9891 | 202919.1275 | 66.44 | 100%
[5 empty] | 66.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12571.2556 | 202955.7184 | 66.45 | 100%
[5 empty] | 66.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12573.5221 | 202992.3093 | 66.46 | 100%
[5 empty] | 66.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12575.7885 | 203028.9003 | 66.47 | 100%
[5 empty] | 66.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12578.055 | 203065.4912 | 66.48 | 100%
[5 empty] | 66.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12580.3215 | 203102.0822 | 66.49 | 100%
[5 empty] | 66.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12582.588 | 203138.6731 | 66.5 | 100%
[5 empty] | 66.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12584.8544 | 203175.2641 | 66.51 | 100%
[5 empty] | 66.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12587.1209 | 203211.855 | 66.52 | 100%
[5 empty] | 66.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12589.3874 | 203248.446 | 66.53 | 100%
[5 empty] | 66.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12591.6539 | 203285.0369 | 66.54 | 100%
[5 empty] | 66.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12593.9203 | 203321.6278 | 66.55 | 100%
[5 empty] | 66.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12596.1868 | 203358.2188 | 66.56 | 100%
[5 empty] | 66.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12598.4533 | 203394.8097 | 66.57 | 100%
[5 empty] | 66.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12600.7198 | 203431.4007 | 66.58 | 100%
[5 empty] | 66.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12602.9862 | 203467.9916 | 66.59 | 100%
[5 empty] | 66.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12605.2527 | 203504.5826 | 66.6 | 100%
[5 empty] | 66.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12607.5192 | 203541.1735 | 66.61 | 100%
[5 empty] | 66.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12609.7857 | 203577.7644 | 66.62 | 100%
[5 empty] | 66.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12612.0521 | 203614.3554 | 66.63 | 100%
[5 empty] | 66.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12614.3186 | 203650.9463 | 66.64 | 100%
[5 empty] | 66.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12616.5851 | 203687.5373 | 66.65 | 100%
[5 empty] | 66.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12618.8516 | 203724.1282 | 66.66 | 100%
[5 empty] | 66.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12621.118 | 203760.7192 | 66.67 | 100%
[5 empty] | 66.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12623.3845 | 203797.3101 | 66.68 | 100%
[5 empty] | 66.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12625.651 | 203833.9011 | 66.69 | 100%
[5 empty] | 66.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12627.9175 | 203870.492 | 66.7 | 100%
[5 empty] | 66.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12630.1839 | 203907.0829 | 66.71 | 100%
[5 empty] | 66.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12632.4504 | 203943.6739 | 66.72 | 100%
[5 empty] | 66.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12634.7169 | 203980.2648 | 66.73 | 100%
[5 empty] | 66.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12636.9834 | 204016.8558 | 66.74 | 100%
[5 empty] | 66.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12639.2498 | 204053.4467 | 66.75 | 100%
[5 empty] | 66.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12641.5163 | 204090.0377 | 66.76 | 100%
[5 empty] | 66.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12643.7828 | 204126.6286 | 66.77 | 100%
[5 empty] | 66.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12646.0493 | 204163.2195 | 66.78 | 100%
[5 empty] | 66.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12648.3157 | 204199.8105 | 66.79 | 100%
[5 empty] | 66.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12650.5822 | 204236.4014 | 66.8 | 100%
[5 empty] | 66.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12652.8487 | 204272.9924 | 66.81 | 100%
[5 empty] | 66.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12655.1152 | 204309.5833 | 66.82 | 100%
[5 empty] | 66.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12657.3816 | 204346.1743 | 66.83 | 100%
[5 empty] | 66.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12659.6481 | 204382.7652 | 66.84 | 100%
[5 empty] | 66.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12661.9146 | 204419.3561 | 66.85 | 100%
[5 empty] | 66.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12664.1811 | 204455.9471 | 66.86 | 100%
[5 empty] | 66.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12666.4475 | 204492.538 | 66.87 | 100%
[5 empty] | 66.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12668.714 | 204529.129 | 66.88 | 100%
[5 empty] | 66.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12670.9805 | 204565.7199 | 66.89 | 100%
[5 empty] | 66.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12673.247 | 204602.3109 | 66.9 | 100%
[5 empty] | 66.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12675.5134 | 204638.9018 | 66.91 | 100%
[5 empty] | 66.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12677.7799 | 204675.4928 | 66.92 | 100%
[5 empty] | 66.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12680.0464 | 204712.0837 | 66.93 | 100%
[5 empty] | 66.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12682.3129 | 204748.6746 | 66.94 | 100%
[5 empty] | 66.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12684.5793 | 204785.2656 | 66.95 | 100%
[5 empty] | 66.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12686.8458 | 204821.8565 | 66.96 | 100%
[5 empty] | 66.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12689.1123 | 204858.4475 | 66.97 | 100%
[5 empty] | 66.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12691.3788 | 204895.0384 | 66.98 | 100%
[5 empty] | 66.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12693.6452 | 204931.6294 | 66.99 | 100%
[5 empty] | 67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12695.9117 | 204968.2203 | 67 | 100%
[5 empty] | 67.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12698.1782 | 205004.8112 | 67.01 | 100%
[5 empty] | 67.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12700.4447 | 205041.4022 | 67.02 | 100%
[5 empty] | 67.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12702.7111 | 205077.9931 | 67.03 | 100%
[5 empty] | 67.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12704.9776 | 205114.5841 | 67.04 | 100%
[5 empty] | 67.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12707.2441 | 205151.175 | 67.05 | 100%
[5 empty] | 67.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12709.5106 | 205187.766 | 67.06 | 100%
[5 empty] | 67.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12711.777 | 205224.3569 | 67.07 | 100%
[5 empty] | 67.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12714.0435 | 205260.9479 | 67.08 | 100%
[5 empty] | 67.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12716.31 | 205297.5388 | 67.09 | 100%
[5 empty] | 67.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12718.5765 | 205334.1297 | 67.1 | 100%
[5 empty] | 67.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12720.8429 | 205370.7207 | 67.11 | 100%
[5 empty] | 67.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12723.1094 | 205407.3116 | 67.12 | 100%
[5 empty] | 67.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12725.3759 | 205443.9026 | 67.13 | 100%
[5 empty] | 67.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12727.6424 | 205480.4935 | 67.14 | 100%
[5 empty] | 67.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12729.9088 | 205517.0845 | 67.15 | 100%
[5 empty] | 67.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12732.1753 | 205553.6754 | 67.16 | 100%
[5 empty] | 67.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12734.4418 | 205590.2663 | 67.17 | 100%
[5 empty] | 67.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12736.7083 | 205626.8573 | 67.18 | 100%
[5 empty] | 67.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12738.9748 | 205663.4482 | 67.19 | 100%
[5 empty] | 67.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12741.2412 | 205700.0392 | 67.2 | 100%
[5 empty] | 67.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12743.5077 | 205736.6301 | 67.21 | 100%
[5 empty] | 67.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12745.7742 | 205773.2211 | 67.22 | 100%
[5 empty] | 67.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12748.0407 | 205809.812 | 67.23 | 100%
[5 empty] | 67.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12750.3071 | 205846.403 | 67.24 | 100%
[5 empty] | 67.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12752.5736 | 205882.9939 | 67.25 | 100%
[5 empty] | 67.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12754.8401 | 205919.5848 | 67.26 | 100%
[5 empty] | 67.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12757.1066 | 205956.1758 | 67.27 | 100%
[5 empty] | 67.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12759.373 | 205992.7667 | 67.28 | 100%
[5 empty] | 67.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12761.6395 | 206029.3577 | 67.29 | 100%
[5 empty] | 67.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12763.906 | 206065.9486 | 67.3 | 100%
[5 empty] | 67.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12766.1725 | 206102.5396 | 67.31 | 100%
[5 empty] | 67.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12768.4389 | 206139.1305 | 67.32 | 100%
[5 empty] | 67.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12770.7054 | 206175.7214 | 67.33 | 100%
[5 empty] | 67.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12772.9719 | 206212.3124 | 67.34 | 100%
[5 empty] | 67.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12775.2384 | 206248.9033 | 67.35 | 100%
[5 empty] | 67.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12777.5048 | 206285.4943 | 67.36 | 100%
[5 empty] | 67.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12779.7713 | 206322.0852 | 67.37 | 100%
[5 empty] | 67.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12782.0378 | 206358.6762 | 67.38 | 100%
[5 empty] | 67.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12784.3043 | 206395.2671 | 67.39 | 100%
[5 empty] | 67.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12786.5707 | 206431.858 | 67.4 | 100%
[5 empty] | 67.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12788.8372 | 206468.449 | 67.41 | 100%
[5 empty] | 67.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12791.1037 | 206505.0399 | 67.42 | 100%
[5 empty] | 67.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12793.3702 | 206541.6309 | 67.43 | 100%
[5 empty] | 67.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12795.6366 | 206578.2218 | 67.44 | 100%
[5 empty] | 67.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12797.9031 | 206614.8128 | 67.45 | 100%
[5 empty] | 67.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12800.1696 | 206651.4037 | 67.46 | 100%
[5 empty] | 67.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12802.4361 | 206687.9947 | 67.47 | 100%
[5 empty] | 67.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12804.7025 | 206724.5856 | 67.48 | 100%
[5 empty] | 67.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12806.969 | 206761.1765 | 67.49 | 100%
[5 empty] | 67.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12809.2355 | 206797.7675 | 67.5 | 100%
[5 empty] | 67.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12811.502 | 206834.3584 | 67.51 | 100%
[5 empty] | 67.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12813.7684 | 206870.9494 | 67.52 | 100%
[5 empty] | 67.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12816.0349 | 206907.5403 | 67.53 | 100%
[5 empty] | 67.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12818.3014 | 206944.1313 | 67.54 | 100%
[5 empty] | 67.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12820.5679 | 206980.7222 | 67.55 | 100%
[5 empty] | 67.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12822.8343 | 207017.3131 | 67.56 | 100%
[5 empty] | 67.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12825.1008 | 207053.9041 | 67.57 | 100%
[5 empty] | 67.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12827.3673 | 207090.495 | 67.58 | 100%
[5 empty] | 67.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12829.6338 | 207127.086 | 67.59 | 100%
[5 empty] | 67.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12831.9002 | 207163.6769 | 67.6 | 100%
[5 empty] | 67.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12834.1667 | 207200.2679 | 67.61 | 100%
[5 empty] | 67.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12836.4332 | 207236.8588 | 67.62 | 100%
[5 empty] | 67.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12838.6997 | 207273.4498 | 67.63 | 100%
[5 empty] | 67.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12840.9661 | 207310.0407 | 67.64 | 100%
[5 empty] | 67.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12843.2326 | 207346.6316 | 67.65 | 100%
[5 empty] | 67.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12845.4991 | 207383.2226 | 67.66 | 100%
[5 empty] | 67.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12847.7656 | 207419.8135 | 67.67 | 100%
[5 empty] | 67.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12850.032 | 207456.4045 | 67.68 | 100%
[5 empty] | 67.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12852.2985 | 207492.9954 | 67.69 | 100%
[5 empty] | 67.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12854.565 | 207529.5864 | 67.7 | 100%
[5 empty] | 67.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12856.8315 | 207566.1773 | 67.71 | 100%
[5 empty] | 67.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12859.0979 | 207602.7682 | 67.72 | 100%
[5 empty] | 67.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12861.3644 | 207639.3592 | 67.73 | 100%
[5 empty] | 67.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12863.6309 | 207675.9501 | 67.74 | 100%
[5 empty] | 67.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12865.8974 | 207712.5411 | 67.75 | 100%
[5 empty] | 67.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12868.1638 | 207749.132 | 67.76 | 100%
[5 empty] | 67.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12870.4303 | 207785.723 | 67.77 | 100%
[5 empty] | 67.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12872.6968 | 207822.3139 | 67.78 | 100%
[5 empty] | 67.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12874.9633 | 207858.9048 | 67.79 | 100%
[5 empty] | 67.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12877.2297 | 207895.4958 | 67.8 | 100%
[5 empty] | 67.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12879.4962 | 207932.0867 | 67.81 | 100%
[5 empty] | 67.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12881.7627 | 207968.6777 | 67.82 | 100%
[5 empty] | 67.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12884.0292 | 208005.2686 | 67.83 | 100%
[5 empty] | 67.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12886.2956 | 208041.8596 | 67.84 | 100%
[5 empty] | 67.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12888.5621 | 208078.4505 | 67.85 | 100%
[5 empty] | 67.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12890.8286 | 208115.0415 | 67.86 | 100%
[5 empty] | 67.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12893.0951 | 208151.6324 | 67.87 | 100%
[5 empty] | 67.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12895.3615 | 208188.2233 | 67.88 | 100%
[5 empty] | 67.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12897.628 | 208224.8143 | 67.89 | 100%
[5 empty] | 67.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12899.8945 | 208261.4052 | 67.9 | 100%
[5 empty] | 67.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12902.161 | 208297.9962 | 67.91 | 100%
[5 empty] | 67.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12904.4274 | 208334.5871 | 67.92 | 100%
[5 empty] | 67.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12906.6939 | 208371.1781 | 67.93 | 100%
[5 empty] | 67.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12908.9604 | 208407.769 | 67.94 | 100%
[5 empty] | 67.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12911.2269 | 208444.3599 | 67.95 | 100%
[5 empty] | 67.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12913.4933 | 208480.9509 | 67.96 | 100%
[5 empty] | 67.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12915.7598 | 208517.5418 | 67.97 | 100%
[5 empty] | 67.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12918.0263 | 208554.1328 | 67.98 | 100%
[5 empty] | 67.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12920.2928 | 208590.7237 | 67.99 | 100%
[5 empty] | 68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12922.5592 | 208627.3147 | 68 | 100%
[5 empty] | 68.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12924.8257 | 208663.9056 | 68.01 | 100%
[5 empty] | 68.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12927.0922 | 208700.4966 | 68.02 | 100%
[5 empty] | 68.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12929.3587 | 208737.0875 | 68.03 | 100%
[5 empty] | 68.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12931.6251 | 208773.6784 | 68.04 | 100%
[5 empty] | 68.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12933.8916 | 208810.2694 | 68.05 | 100%
[5 empty] | 68.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12936.1581 | 208846.8603 | 68.06 | 100%
[5 empty] | 68.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12938.4246 | 208883.4513 | 68.07 | 100%
[5 empty] | 68.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12940.691 | 208920.0422 | 68.08 | 100%
[5 empty] | 68.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12942.9575 | 208956.6332 | 68.09 | 100%
[5 empty] | 68.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12945.224 | 208993.2241 | 68.1 | 100%
[5 empty] | 68.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12947.4905 | 209029.815 | 68.11 | 100%
[5 empty] | 68.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12949.7569 | 209066.406 | 68.12 | 100%
[5 empty] | 68.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12952.0234 | 209102.9969 | 68.13 | 100%
[5 empty] | 68.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12954.2899 | 209139.5879 | 68.14 | 100%
[5 empty] | 68.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12956.5564 | 209176.1788 | 68.15 | 100%
[5 empty] | 68.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12958.8228 | 209212.7698 | 68.16 | 100%
[5 empty] | 68.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12961.0893 | 209249.3607 | 68.17 | 100%
[5 empty] | 68.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12963.3558 | 209285.9517 | 68.18 | 100%
[5 empty] | 68.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12965.6223 | 209322.5426 | 68.19 | 100%
[5 empty] | 68.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12967.8887 | 209359.1335 | 68.2 | 100%
[5 empty] | 68.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12970.1552 | 209395.7245 | 68.21 | 100%
[5 empty] | 68.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12972.4217 | 209432.3154 | 68.22 | 100%
[5 empty] | 68.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12974.6882 | 209468.9064 | 68.23 | 100%
[5 empty] | 68.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12976.9546 | 209505.4973 | 68.24 | 100%
[5 empty] | 68.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12979.2211 | 209542.0883 | 68.25 | 100%
[5 empty] | 68.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12981.4876 | 209578.6792 | 68.26 | 100%
[5 empty] | 68.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12983.7541 | 209615.2701 | 68.27 | 100%
[5 empty] | 68.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12986.0205 | 209651.8611 | 68.28 | 100%
[5 empty] | 68.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12988.287 | 209688.452 | 68.29 | 100%
[5 empty] | 68.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12990.5535 | 209725.043 | 68.3 | 100%
[5 empty] | 68.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12992.82 | 209761.6339 | 68.31 | 100%
[5 empty] | 68.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12995.0864 | 209798.2249 | 68.32 | 100%
[5 empty] | 68.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12997.3529 | 209834.8158 | 68.33 | 100%
[5 empty] | 68.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 12999.6194 | 209871.4067 | 68.34 | 100%
[5 empty] | 68.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13001.8859 | 209907.9977 | 68.35 | 100%
[5 empty] | 68.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13004.1523 | 209944.5886 | 68.36 | 100%
[5 empty] | 68.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13006.4188 | 209981.1796 | 68.37 | 100%
[5 empty] | 68.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13008.6853 | 210017.7705 | 68.38 | 100%
[5 empty] | 68.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13010.9518 | 210054.3615 | 68.39 | 100%
[5 empty] | 68.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13013.2183 | 210090.9524 | 68.4 | 100%
[5 empty] | 68.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13015.4847 | 210127.5434 | 68.41 | 100%
[5 empty] | 68.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13017.7512 | 210164.1343 | 68.42 | 100%
[5 empty] | 68.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13020.0177 | 210200.7252 | 68.43 | 100%
[5 empty] | 68.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13022.2842 | 210237.3162 | 68.44 | 100%
[5 empty] | 68.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13024.5506 | 210273.9071 | 68.45 | 100%
[5 empty] | 68.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13026.8171 | 210310.4981 | 68.46 | 100%
[5 empty] | 68.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13029.0836 | 210347.089 | 68.47 | 100%
[5 empty] | 68.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13031.3501 | 210383.68 | 68.48 | 100%
[5 empty] | 68.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13033.6165 | 210420.2709 | 68.49 | 100%
[5 empty] | 68.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13035.883 | 210456.8618 | 68.5 | 100%
[5 empty] | 68.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13038.1495 | 210493.4528 | 68.51 | 100%
[5 empty] | 68.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13040.416 | 210530.0437 | 68.52 | 100%
[5 empty] | 68.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13042.6824 | 210566.6347 | 68.53 | 100%
[5 empty] | 68.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13044.9489 | 210603.2256 | 68.54 | 100%
[5 empty] | 68.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13047.2154 | 210639.8166 | 68.55 | 100%
[5 empty] | 68.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13049.4819 | 210676.4075 | 68.56 | 100%
[5 empty] | 68.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13051.7483 | 210712.9985 | 68.57 | 100%
[5 empty] | 68.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13054.0148 | 210749.5894 | 68.58 | 100%
[5 empty] | 68.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13056.2813 | 210786.1803 | 68.59 | 100%
[5 empty] | 68.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13058.5478 | 210822.7713 | 68.6 | 100%
[5 empty] | 68.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13060.8142 | 210859.3622 | 68.61 | 100%
[5 empty] | 68.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13063.0807 | 210895.9532 | 68.62 | 100%
[5 empty] | 68.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13065.3472 | 210932.5441 | 68.63 | 100%
[5 empty] | 68.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13067.6137 | 210969.1351 | 68.64 | 100%
[5 empty] | 68.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13069.8801 | 211005.726 | 68.65 | 100%
[5 empty] | 68.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13072.1466 | 211042.3169 | 68.66 | 100%
[5 empty] | 68.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13074.4131 | 211078.9079 | 68.67 | 100%
[5 empty] | 68.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13076.6796 | 211115.4988 | 68.68 | 100%
[5 empty] | 68.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13078.946 | 211152.0898 | 68.69 | 100%
[5 empty] | 68.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13081.2125 | 211188.6807 | 68.7 | 100%
[5 empty] | 68.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13083.479 | 211225.2717 | 68.71 | 100%
[5 empty] | 68.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13085.7455 | 211261.8626 | 68.72 | 100%
[5 empty] | 68.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13088.0119 | 211298.4536 | 68.73 | 100%
[5 empty] | 68.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13090.2784 | 211335.0445 | 68.74 | 100%
[5 empty] | 68.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13092.5449 | 211371.6354 | 68.75 | 100%
[5 empty] | 68.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13094.8114 | 211408.2264 | 68.76 | 100%
[5 empty] | 68.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13097.0778 | 211444.8173 | 68.77 | 100%
[5 empty] | 68.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13099.3443 | 211481.4083 | 68.78 | 100%
[5 empty] | 68.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13101.6108 | 211517.9992 | 68.79 | 100%
[5 empty] | 68.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13103.8773 | 211554.5902 | 68.8 | 100%
[5 empty] | 68.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13106.1437 | 211591.1811 | 68.81 | 100%
[5 empty] | 68.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13108.4102 | 211627.772 | 68.82 | 100%
[5 empty] | 68.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13110.6767 | 211664.363 | 68.83 | 100%
[5 empty] | 68.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13112.9432 | 211700.9539 | 68.84 | 100%
[5 empty] | 68.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13115.2096 | 211737.5449 | 68.85 | 100%
[5 empty] | 68.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13117.4761 | 211774.1358 | 68.86 | 100%
[5 empty] | 68.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13119.7426 | 211810.7268 | 68.87 | 100%
[5 empty] | 68.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13122.0091 | 211847.3177 | 68.88 | 100%
[5 empty] | 68.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13124.2755 | 211883.9086 | 68.89 | 100%
[5 empty] | 68.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13126.542 | 211920.4996 | 68.9 | 100%
[5 empty] | 68.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13128.8085 | 211957.0905 | 68.91 | 100%
[5 empty] | 68.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13131.075 | 211993.6815 | 68.92 | 100%
[5 empty] | 68.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13133.3414 | 212030.2724 | 68.93 | 100%
[5 empty] | 68.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13135.6079 | 212066.8634 | 68.94 | 100%
[5 empty] | 68.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13137.8744 | 212103.4543 | 68.95 | 100%
[5 empty] | 68.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13140.1409 | 212140.0453 | 68.96 | 100%
[5 empty] | 68.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13142.4073 | 212176.6362 | 68.97 | 100%
[5 empty] | 68.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13144.6738 | 212213.2271 | 68.98 | 100%
[5 empty] | 68.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13146.9403 | 212249.8181 | 68.99 | 100%
[5 empty] | 69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13149.2068 | 212286.409 | 69 | 100%
[5 empty] | 69.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13151.4732 | 212323 | 69.01 | 100%
[5 empty] | 69.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13153.7397 | 212359.5909 | 69.02 | 100%
[5 empty] | 69.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13156.0062 | 212396.1819 | 69.03 | 100%
[5 empty] | 69.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13158.2727 | 212432.7728 | 69.04 | 100%
[5 empty] | 69.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13160.5391 | 212469.3637 | 69.05 | 100%
[5 empty] | 69.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13162.8056 | 212505.9547 | 69.06 | 100%
[5 empty] | 69.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13165.0721 | 212542.5456 | 69.07 | 100%
[5 empty] | 69.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13167.3386 | 212579.1366 | 69.08 | 100%
[5 empty] | 69.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13169.605 | 212615.7275 | 69.09 | 100%
[5 empty] | 69.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13171.8715 | 212652.3185 | 69.1 | 100%
[5 empty] | 69.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13174.138 | 212688.9094 | 69.11 | 100%
[5 empty] | 69.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13176.4045 | 212725.5004 | 69.12 | 100%
[5 empty] | 69.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13178.6709 | 212762.0913 | 69.13 | 100%
[5 empty] | 69.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13180.9374 | 212798.6822 | 69.14 | 100%
[5 empty] | 69.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13183.2039 | 212835.2732 | 69.15 | 100%
[5 empty] | 69.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13185.4704 | 212871.8641 | 69.16 | 100%
[5 empty] | 69.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13187.7368 | 212908.4551 | 69.17 | 100%
[5 empty] | 69.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13190.0033 | 212945.046 | 69.18 | 100%
[5 empty] | 69.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13192.2698 | 212981.637 | 69.19 | 100%
[5 empty] | 69.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13194.5363 | 213018.2279 | 69.2 | 100%
[5 empty] | 69.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13196.8027 | 213054.8188 | 69.21 | 100%
[5 empty] | 69.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13199.0692 | 213091.4098 | 69.22 | 100%
[5 empty] | 69.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13201.3357 | 213128.0007 | 69.23 | 100%
[5 empty] | 69.24 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13203.6022 | 213164.5917 | 69.24 | 100%
[5 empty] | 69.25 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13205.8686 | 213201.1826 | 69.25 | 100%
[5 empty] | 69.26 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13208.1351 | 213237.7736 | 69.26 | 100%
[5 empty] | 69.27 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13210.4016 | 213274.3645 | 69.27 | 100%
[5 empty] | 69.28 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13212.6681 | 213310.9554 | 69.28 | 100%
[5 empty] | 69.29 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13214.9345 | 213347.5464 | 69.29 | 100%
[5 empty] | 69.3 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13217.201 | 213384.1373 | 69.3 | 100%
[5 empty] | 69.31 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13219.4675 | 213420.7283 | 69.31 | 100%
[5 empty] | 69.32 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13221.734 | 213457.3192 | 69.32 | 100%
[5 empty] | 69.33 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13224.0004 | 213493.9102 | 69.33 | 100%
[5 empty] | 69.34 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13226.2669 | 213530.5011 | 69.34 | 100%
[5 empty] | 69.35 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13228.5334 | 213567.0921 | 69.35 | 100%
[5 empty] | 69.36 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13230.7999 | 213603.683 | 69.36 | 100%
[5 empty] | 69.37 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13233.0663 | 213640.2739 | 69.37 | 100%
[5 empty] | 69.38 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13235.3328 | 213676.8649 | 69.38 | 100%
[5 empty] | 69.39 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13237.5993 | 213713.4558 | 69.39 | 100%
[5 empty] | 69.4 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13239.8658 | 213750.0468 | 69.4 | 100%
[5 empty] | 69.41 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13242.1322 | 213786.6377 | 69.41 | 100%
[5 empty] | 69.42 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13244.3987 | 213823.2287 | 69.42 | 100%
[5 empty] | 69.43 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13246.6652 | 213859.8196 | 69.43 | 100%
[5 empty] | 69.44 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13248.9317 | 213896.4105 | 69.44 | 100%
[5 empty] | 69.45 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13251.1981 | 213933.0015 | 69.45 | 100%
[5 empty] | 69.46 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13253.4646 | 213969.5924 | 69.46 | 100%
[5 empty] | 69.47 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13255.7311 | 214006.1834 | 69.47 | 100%
[5 empty] | 69.48 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13257.9976 | 214042.7743 | 69.48 | 100%
[5 empty] | 69.49 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13260.264 | 214079.3653 | 69.49 | 100%
[5 empty] | 69.5 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13262.5305 | 214115.9562 | 69.5 | 100%
[5 empty] | 69.51 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13264.797 | 214152.5472 | 69.51 | 100%
[5 empty] | 69.52 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13267.0635 | 214189.1381 | 69.52 | 100%
[5 empty] | 69.53 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13269.3299 | 214225.729 | 69.53 | 100%
[5 empty] | 69.54 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13271.5964 | 214262.32 | 69.54 | 100%
[5 empty] | 69.55 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13273.8629 | 214298.9109 | 69.55 | 100%
[5 empty] | 69.56 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13276.1294 | 214335.5019 | 69.56 | 100%
[5 empty] | 69.57 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13278.3959 | 214372.0928 | 69.57 | 100%
[5 empty] | 69.58 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13280.6623 | 214408.6838 | 69.58 | 100%
[5 empty] | 69.59 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13282.9288 | 214445.2747 | 69.59 | 100%
[5 empty] | 69.6 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13285.1953 | 214481.8656 | 69.6 | 100%
[5 empty] | 69.61 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13287.4618 | 214518.4566 | 69.61 | 100%
[5 empty] | 69.62 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13289.7282 | 214555.0475 | 69.62 | 100%
[5 empty] | 69.63 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13291.9947 | 214591.6385 | 69.63 | 100%
[5 empty] | 69.64 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13294.2612 | 214628.2294 | 69.64 | 100%
[5 empty] | 69.65 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13296.5277 | 214664.8204 | 69.65 | 100%
[5 empty] | 69.66 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13298.7941 | 214701.4113 | 69.66 | 100%
[5 empty] | 69.67 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13301.0606 | 214738.0023 | 69.67 | 100%
[5 empty] | 69.68 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13303.3271 | 214774.5932 | 69.68 | 100%
[5 empty] | 69.69 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13305.5936 | 214811.1841 | 69.69 | 100%
[5 empty] | 69.7 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13307.86 | 214847.7751 | 69.7 | 100%
[5 empty] | 69.71 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13310.1265 | 214884.366 | 69.71 | 100%
[5 empty] | 69.72 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13312.393 | 214920.957 | 69.72 | 100%
[5 empty] | 69.73 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13314.6595 | 214957.5479 | 69.73 | 100%
[5 empty] | 69.74 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13316.9259 | 214994.1389 | 69.74 | 100%
[5 empty] | 69.75 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13319.1924 | 215030.7298 | 69.75 | 100%
[5 empty] | 69.76 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13321.4589 | 215067.3207 | 69.76 | 100%
[5 empty] | 69.77 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13323.7254 | 215103.9117 | 69.77 | 100%
[5 empty] | 69.78 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13325.9918 | 215140.5026 | 69.78 | 100%
[5 empty] | 69.79 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13328.2583 | 215177.0936 | 69.79 | 100%
[5 empty] | 69.8 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13330.5248 | 215213.6845 | 69.8 | 100%
[5 empty] | 69.81 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13332.7913 | 215250.2755 | 69.81 | 100%
[5 empty] | 69.82 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13335.0577 | 215286.8664 | 69.82 | 100%
[5 empty] | 69.83 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13337.3242 | 215323.4573 | 69.83 | 100%
[5 empty] | 69.84 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13339.5907 | 215360.0483 | 69.84 | 100%
[5 empty] | 69.85 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13341.8572 | 215396.6392 | 69.85 | 100%
[5 empty] | 69.86 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13344.1236 | 215433.2302 | 69.86 | 100%
[5 empty] | 69.87 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13346.3901 | 215469.8211 | 69.87 | 100%
[5 empty] | 69.88 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13348.6566 | 215506.4121 | 69.88 | 100%
[5 empty] | 69.89 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13350.9231 | 215543.003 | 69.89 | 100%
[5 empty] | 69.9 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13353.1895 | 215579.594 | 69.9 | 100%
[5 empty] | 69.91 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13355.456 | 215616.1849 | 69.91 | 100%
[5 empty] | 69.92 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13357.7225 | 215652.7758 | 69.92 | 100%
[5 empty] | 69.93 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13359.989 | 215689.3668 | 69.93 | 100%
[5 empty] | 69.94 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13362.2554 | 215725.9577 | 69.94 | 100%
[5 empty] | 69.95 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13364.5219 | 215762.5487 | 69.95 | 100%
[5 empty] | 69.96 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13366.7884 | 215799.1396 | 69.96 | 100%
[5 empty] | 69.97 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13369.0549 | 215835.7306 | 69.97 | 100%
[5 empty] | 69.98 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13371.3213 | 215872.3215 | 69.98 | 100%
[5 empty] | 69.99 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13373.5878 | 215908.9124 | 69.99 | 100%
[5 empty] | 70 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13375.8543 | 215945.5034 | 70 | 100%
[5 empty] | 70.01 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13378.1208 | 215982.0943 | 70.01 | 100%
[5 empty] | 70.02 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13380.3872 | 216018.6853 | 70.02 | 100%
[5 empty] | 70.03 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13382.6537 | 216055.2762 | 70.03 | 100%
[5 empty] | 70.04 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13384.9202 | 216091.8672 | 70.04 | 100%
[5 empty] | 70.05 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13387.1867 | 216128.4581 | 70.05 | 100%
[5 empty] | 70.06 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13389.4531 | 216165.0491 | 70.06 | 100%
[5 empty] | 70.07 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13391.7196 | 216201.64 | 70.07 | 100%
[5 empty] | 70.08 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13393.9861 | 216238.2309 | 70.08 | 100%
[5 empty] | 70.09 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13396.2526 | 216274.8219 | 70.09 | 100%
[5 empty] | 70.1 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13398.519 | 216311.4128 | 70.1 | 100%
[5 empty] | 70.11 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13400.7855 | 216348.0038 | 70.11 | 100%
[5 empty] | 70.12 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13403.052 | 216384.5947 | 70.12 | 100%
[5 empty] | 70.13 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13405.3185 | 216421.1857 | 70.13 | 100%
[5 empty] | 70.14 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13407.5849 | 216457.7766 | 70.14 | 100%
[5 empty] | 70.15 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13409.8514 | 216494.3675 | 70.15 | 100%
[5 empty] | 70.16 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13412.1179 | 216530.9585 | 70.16 | 100%
[5 empty] | 70.17 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13414.3844 | 216567.5494 | 70.17 | 100%
[5 empty] | 70.18 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13416.6508 | 216604.1404 | 70.18 | 100%
[5 empty] | 70.19 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13418.9173 | 216640.7313 | 70.19 | 100%
[5 empty] | 70.2 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13421.1838 | 216677.3223 | 70.2 | 100%
[5 empty] | 70.21 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13423.4503 | 216713.9132 | 70.21 | 100%
[5 empty] | 70.22 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13425.7167 | 216750.5042 | 70.22 | 100%
[5 empty] | 70.23 | 246000 | 396 | 100% | 100% | 100% | 1 | 1910.8108 | 5474.8509 | 212160 | 219545.6618 | 13427.9832 | 216787.0951 | 70.23 | 100%

## RadCompList (hidden)
Column Radiators
| Sq Ft Radiation Per Section | Columns |  |  |  |  | FALSE |  |  |  | Rad Types | ft3/edr
Rad Type | Column | 1 | 2 | 3 | 4 | 5 | 1 |  |  |  | Column | 0.025
Column | 13 | - | - | - | - | 3 | 2 |  |  |  | Tube | 0.013
Column | 16 | - | - | - | - | 3.75 | 3 |  |  |  | Cast Rad/Conv | 0.0003
Column | 18 | - | - | 2.25 | 3 | 4.25 | 4 |  |  |  | Copper Cabinet | 0.0003
Column | 20 | 1.5 | 2 | - | - | 5 | 5
Column | 22 | - | - | 3 | 4 | - | 6
Column | 23 | 1.66 | 2.33 | - | - | - | 7
Column | 26 | 2 | 2.66 | 3.75 | 5 | - | 8 |  |  |  |  | Sections list
Column | 32 | 2.5 | 3.33 | 4.5 | 6.5 | - | 9 |  |  |  |  | 1
Column | 38 | 3 | 4 | 5 | 8 | - | 10 |  |  |  |  | 2
Column | 45 | - | 5 | 6 | 10 | - | 11 |  |  |  |  | 3
|  | Columns 1: Tubes |  |  |  |  | 4
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 |  |  | 5
Tube | 13 | , | - | - | - | - | - | 2.625 | 2 |  |  | 6
Tube | 16.5 | - | - | - | - | - | - | 3.5 | 3 |  |  | 7
Tube | 20 | - | - | 1.75 | 2.25 | 2.66 | 3 | 4.25 | 4 |  |  | 8
Tube | 23 | - | - | 2 | 2.5 | 3 | 3.5 | - | 5 |  |  | 9
Tube | 26 | - | - | 2.11 | 2.75 | 3.5 | 4 | - | 6 |  |  | 10
Tube | 32 | - | - | 3 | 3.5 | 4.33 | 5 | - | 7 |  |  | 11
Tube | 37 | - | - | 3.5 | 4.125 | 5 | 6 | - | 8 |  |  | 12
13
14
15
|  | Tubes 1: Width |  |  | 16
|  | Tubes 1: 5; Tubes 2: 7.5 |  |  | 17
Cast Rad/Conv | 20 | Tubes 1: 2.25; Tubes 2: 3.4 |  |  | 18
19
20
10-1/2 X 20-1/2
|  | 10-1/2 X 20-1/2 |  | 1
|  | 18 | #N/A | 31
Height
| Cabinet Depth | Cabinet Length | Dimensions | 18 | 20 | 24 | 26 | 32 | 38
Copper Cabinet | 4-1/2" | 20-1/2" | 4-1/2 X 20-1/2 | 10.4 | 11.3 | 13.1 | 13.4 | 14 | 14.6
Copper Cabinet | 4-1/2" | 24-1/2" | 4-1/2 X 24-1/2 | 12.8 | 13.9 | 16.1 | 16.4 | 17.2 | 18
Copper Cabinet | 4-1/2" | 28-1/2" | 4-1/2 X 28-1/2 | 15.2 | 16.5 | 19.2 | 19.5 | 20.4 | 21.3
Copper Cabinet | 4-1/2" | 32-1/2" | 4-1/2 X 32-1/2 | 17.6 | 19.1 | 22.2 | 22.5 | 23.6 | 24.6
Copper Cabinet | 4-1/2" | 36-1/2" | 4-1/2 X 36-1/2 | 19.7 | 21.7 | 25.2 | 25.6 | 26.8 | 28
Copper Cabinet | 4-1/2" | 40-1/2" | 4-1/2 X 40-1/2 | 22.3 | 24.3 | 28.2 | 28.6 | 30 | 31.3
Copper Cabinet | 4-1/2" | 44-1/2" | 4-1/2 X 44-1/2 | 24.7 | 26.9 | 31.2 | 31.7 | 33.2 | 34.7
Copper Cabinet | 4-1/2" | 48-1/2" | 4-1/2 X 48-1/2 | 27.1 | 29.5 | 34.2 | 34.7 | 36.4 | 38
Copper Cabinet | 4-1/2" | 56-1/2" | 4-1/2 X 56-1/2 | 31.9 | 34.7 | 40.2 | 40.8 | 42.8 | 44.7
Copper Cabinet | 4-1/2" | 64-1/2" | 4-1/2 X 64-1/2 | 36.6 | 39.9 | 46.2 | 46.9 | 49.2 | 51.7
Copper Cabinet | 6-1/2" | 20-1/2" | 6-1/2 X 20-1/2 | 15.3 | 16.3 | 18.4 | 18.8 | 19.6 | 20.6
Copper Cabinet | 6-1/2" | 24-1/2" | 6-1/2 X 24-1/2 | 18.8 | 20.1 | 22.6 | 23.1 | 24.1 | 25.3
Copper Cabinet | 6-1/2" | 28-1/2" | 6-1/2 X 28-1/2 | 22.3 | 23.8 | 26.9 | 27.4 | 28.6 | 30.1
Copper Cabinet | 6-1/2" | 32-1/2" | 6-1/2 X 32-1/2 | 25.8 | 27.6 | 31.1 | 31.7 | 33.2 | 34.8
Copper Cabinet | 6-1/2" | 36-1/2" | 6-1/2 X 36-1/2 | 29.3 | 31.3 | 35.4 | 36 | 37.7 | 39.6
Copper Cabinet | 6-1/2" | 40-1/2" | 6-1/2 X 40-1/2 | 32.8 | 35.1 | 39.6 | 40.3 | 42.2 | 44.3
Copper Cabinet | 6-1/2" | 44-1/2" | 6-1/2 X 44-1/2 | 36.3 | 38.9 | 43.8 | 44.6 | 48.7 | 49.9 | Cabinet Depth
Copper Cabinet | 6-1/2" | 48-1/2" | 6-1/2 X 48-1/2 | 39.8 | 42.6 | 48.1 | 48.9 | 51.2 | 53.8 | 4-1/2"
Copper Cabinet | 6-1/2" | 56-1/2" | 6-1/2 X 56-1/2 | 46.8 | 50.1 | 56.6 | 57.5 | 60.6 | 63.3 | 6-1/2"
Copper Cabinet | 6-1/2" | 64-1/2" | 6-1/2 X 64-1/2 | 53.9 | 57.7 | 65 | 66.2 | 69.3 | 72.7 | 8-1/2"
Copper Cabinet | 8-1/2" | 20-1/2" | 8-1/2 X 20-1/2 | 18.7 | 20 | 22.5 | 23 | 24.4 | 25.8 | 10-1/2"
Copper Cabinet | 8-1/2" | 24-1/2" | 8-1/2 X 24-1/2 | 22.9 | 24.5 | 27.7 | 28.8 | 30 | 3.7
Copper Cabinet | 8-1/2" | 28-1/2" | 8-1/2 X 28-1/2 | 27.2 | 20.1 | 32.8 | 33.5 | 35.6 | 37.7
Copper Cabinet | 8-1/2" | 32-1/2" | 8-1/2 X 32-1/2 | 31.5 | 33.7 | 38 | 38.8 | 41.2 | 43.6
Copper Cabinet | 8-1/2" | 36-1/2" | 8-1/2 X 36-1/2 | 35.8 | 38.3 | 43.2 | 44.1 | 46.8 | 49.5
Copper Cabinet | 8-1/2" | 40-1/2" | 8-1/2 X 40-1/2 | 40.1 | 42.9 | 48.3 | 49.4 | 52.4 | 55.5
Copper Cabinet | 8-1/2" | 44-1/2" | 8-1/2 X 44-1/2 | 44.3 | 47.4 | 53.3 | 54.6 | 58 | 61.4
Copper Cabinet | 8-1/2" | 48-1/2" | 8-1/2 X 48-1/2 | 48.6 | 52 | 58.7 | 59.9 | 63.6 | 67.3
Copper Cabinet | 8-1/2" | 56-1/2" | 8-1/2 X 56-1/2 | 57.2 | 61.2 | 69 | 70.5 | 74.8 | 79.2
Copper Cabinet | 8-1/2" | 64-1/2" | 8-1/2 X 64-1/2 | 65.7 | 70.3 | 79.4 | 81 | 86 | 91
Copper Cabinet | 10-1/2" | 20-1/2" | 10-1/2 X 20-1/2 | 20.4 | 22 | 25 | 25.7 | 27.4 | 29.3
Copper Cabinet | 10-1/2" | 24-1/2" | 10-1/2 X 24-1/2 | 25.2 | 27.1 | 30.9 | 31.7 | 33.8 | 36.2
Copper Cabinet | 10-1/2" | 28-1/2" | 10-1/2 X 28-1/2 | 30 | 32.3 | 36.8 | 37.7 | 40.2 | 43.1
Copper Cabinet | 10-1/2" | 32-1/2" | 10-1/2 X 32-1/2 | 34.8 | 37.4 | 42.6 | 43.7 | 46.6 | 50
Copper Cabinet | 10-1/2" | 36-1/2" | 10-1/2 X 36-1/2 | 39.6 | 42.6 | 48.5 | 49.8 | 53.1 | 56.9
Copper Cabinet | 10-1/2" | 40-1/2" | 10-1/2 X 40-1/2 | 44.4 | 47.7 | 54.4 | 55.8 | 59.5 | 63.7
Copper Cabinet | 10-1/2" | 44-1/2" | 10-1/2 X 44-1/2 | 49.2 | 52.9 | 60.3 | 61.8 | 65.9 | 70.6
Copper Cabinet | 10-1/2" | 48-1/2" | 10-1/2 X 48-1/2 | 53.9 | 58 | 66.1 | 67.8 | 72.3 | 77.5
Copper Cabinet | 10-1/2" | 56-1/2" | 10-1/2 X 56-1/2 | 63.5 | 68.3 | 77.9 | 79.9 | 85.2 | 91.2
Copper Cabinet | 10-1/2" | 64-1/2" | 10-1/2 X 64-1/2 | 73.1 | 78.6 | 89.6 | 91.9 | 98 | 105

## VentList (hidden)
MAIN VENTS | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM |  |  |  |  | Vent Lines
- | 0 | 0 | 0 | Equivalent Orifice ID (in) | Equivalent Orifice ID (in) | Equivalent Orifice ID (in) | Equivalent Orifice (in)
Open 1/8" Steel Pipe | 1.2 | 2 | 2.5 | 0.032313 | 0.038081 | 0.038867 | 0.03642
Open 1/2" Steel Pipe | 2.6 | 3.4 | 4.8 | 0.070012 | 0.064738 | 0.074624 | 0.069791 | A
Open 3/4" Steel Pipe | Note 1 | Note 1 | 9.5 | #VALUE! | #VALUE! | 0.14769 | #VALUE! | B
Open 1" Steel Pipe | Note 1 | Note 1 | 11 | #VALUE! | #VALUE! | 0.17101 | #VALUE! | C
American Radiator Co. Ideal Vac-Vent #822 - (obsolete) | 0.1 | 0.158 | 0.2 | 0.0026928 | 0.0030084 | 0.0031093 | 0.0029368 | D
Barnes & Jones QV 1 (obsolete) | 0.583 | 1.58 | 2 | 0.015699 | 0.030084 | 0.031093 | 0.025625 | E
Barnes & Jones Ventrite #75-- (obsolete) | 0.116 | 0.175 | 0.225 | 0.0031236 | 0.0033321 | 0.003498 | 0.0033179 | F
Detroit Controls #841 Quick Vent (obsolete) | 0.333 | 0.55 | 0.7 | 0.0089669 | 0.010472 | 0.010883 | 0.010107 | G
Dole #5 Quick Vent | 0.066 | 0.116 | 0.15 | 0.0017772 | 0.0022087 | 0.002332 | 0.002106 | H
Gorton #1 | 0.33 | 0.54 | 0.7 | 0.0088861 | 0.010282 | 0.010883 | 0.010017 | I
Gorton #2 | 1.1 | 1.75 | 2.2 | 0.02962 | 0.033321 | 0.034203 | 0.032381 | J
Hoffman #4 | 0.06 | 0.11 | 0.13 | 0.0016157 | 0.0020945 | 0.0020211 | 0.0019104 | K
Hoffman #4A | 0.133 | 0.216 | 0.266 | 0.0035814 | 0.0041128 | 0.0041354 | 0.0039432 | L
Hoffman #6 Vacuum Valve (obsolete) | 0.033 | 0.083 | 0.108 | 0.00088861 | 0.0015804 | 0.001679 | 0.0013827 | M
Hoffman #10 Vapor Vent - (obsolete) | 2.033 | 2.5 | 3.7 | 0.054744 | 0.047602 | 0.057523 | 0.053289 | N
Hoffman #11 Vapor Vacuum Vent (obsolete) | 1 | 2.41 | 3.33 | 0.026928 | 0.045888 | 0.05177 | 0.041529 | O
Hoffman #15 Vacuum Vent (obsolete) Differential Loop | 1.283 | 2.75 | 3.416 | 0.034548 | 0.052362 | 0.053107 | 0.046672 | Single Pipe
Hoffman #16 Vacuum Valve (obsolete) | 0.066 | 0.116 | 0.15 | 0.0017772 | 0.0022087 | 0.002332 | 0.002106
Hoffman #16A Vacuum Valve (obsolete) | 0.1 | 0.183 | 0.241 | 0.0026928 | 0.0034844 | 0.0037467 | 0.003308
Hoffman #75 | 0.5 | 0.75 | 0.96 | 0.013464 | 0.014281 | 0.014925 | 0.014223
Hoffman #76 Vacuum Valve | 0.383 | 0.666 | 0.833 | 0.010313 | 0.012681 | 0.01295 | 0.011982
Ideal Htg. Co. "Wafer Style" - - (obsolete) | 0.09 | 0.13 | 0.166 | 0.0024235 | 0.0024753 | 0.0025807 | 0.0024932
Maid-O-Mist #1 Straight Pattern | 0.333 | 0.59 | 0.766 | 0.0089669 | 0.011234 | 0.011909 | 0.010703
Marsh #55 | 0.01 | 0.021 | 0.033 | 0.00026928 | 0.00039985 | 0.00051304 | 0.00039406
Mouat Cast Iron 'Bullet' Style (obsolete) | 0.53 | 0.91 | 1.11 | 0.014272 | 0.017327 | 0.017257 | 0.016285
Mouat Tri Tube (obsolete) | 1.16 | 1.8 | 2 | 0.031236 | 0.034273 | 0.031093 | 0.032201
Squires Co. Mouat Series Cast Iron Bullet Style (obsolete) | 0.53 | 0.91 | 1.11 | 0.014272 | 0.017327 | 0.017257 | 0.016285
Trane Cast Iron Bullet Style (obsolete) | 0.78 | 1.33 | 1.7 | 0.021004 | 0.025324 | 0.026429 | 0.024252
Vent Rite #35 | 0.11 | 0.2 | 0.25 | 0.002962 | 0.0038081 | 0.0038867 | 0.0035523
Vent Rite #75 (Barnes & Jones Issue) (obsolete) | 0.116 | 0.175 | 0.225 | 0.0031236 | 0.0033321 | 0.003498 | 0.0033179
Vent Rite #77 | 0.19 | 0.31 | 0.4 | 0.0051162 | 0.0059026 | 0.0062187 | 0.0057458
Watts SVS-3 | 0.07 | 0.116 | 0.15 | 0.0018849 | 0.0022087 | 0.002332 | 0.0021419
Warco #3(obsolete) | 0.05 | 0.108 | 0.15 | 0.0013464 | 0.0020564 | 0.002332 | 0.0019116
Warco #87 (obsolete) | 0.108 | 0.175 | 0.233 | 0.0029082 | 0.0033321 | 0.0036224 | 0.0032876
Warren Webster #40-15 Vent Trap (obsolete) | 1.166 | 1.866 | 2.366 | 0.031398 | 0.03553 | 0.036783 | 0.03457
Radiator Vents | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM | #VALUE! | #VALUE! | #VALUE! | #VALUE!
- | 0 | 0 | 0 | 0 | 0 | 0 | 0
#1 (obsolete) Airmatic | 0.045 | 0.222 | 0.1 | 0.0012117 | 0.004227 | 0.0015547 | 0.0023311
American Radiator Co. Detroit Controls #500 Airid (obsolete) | 0.036 | 0.061 | 0.08 | 0.00096939 | 0.0011615 | 0.0012437 | 0.0011249
ARCO Detroit Controls Multiport Setting 1-- (obsolete) | Note 3 | Note 3 | Note 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ARCO Detroit Controls Multiport Setting 2 (obsolete) | Note 3 | Note 3 | Note 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
ARCO Detroit Controls Multiport Setting 3- (obsolete) | Note 3 | Note 3 | 0.011 | #VALUE! | #VALUE! | 0.00017101 | #VALUE!
Detroit Controls Multiport Setting 4 (obsolete) ARCO | 0.021 | 0.028 | 0.038 | 0.00056548 | 0.00053314 | 0.00059077 | 0.00056313
ARCO Detroit Controls Multiport Setting 5 (obsolete) | 0.045 | 0.075 | 0.1 | 0.0012117 | 0.0014281 | 0.0015547 | 0.0013982
ARCO Detroit Controls Multiport Setting 6 (obsolete) | 0.05 | 0.108 | 0.141 | 0.0013464 | 0.0020564 | 0.0021921 | 0.0018649
ARCO Detroit Controls Multiport Setting 7-- (obsolete) | 0.066 | 0.116 | 0.158 | 0.0017772 | 0.0022087 | 0.0024564 | 0.0021474
Detroit Controls Multiport Setting 8 (obsolete) ARCO | 0.083 | 0.141 | 0.191 | 0.002235 | 0.0026847 | 0.0029694 | 0.0026297
ARCO Detroit Controls Multiport Setting 9 (obsolete) | 0.1 | 0.158 | 0.208 | 0.0026928 | 0.0030084 | 0.0032337 | 0.0029783
ARCO Detroit Controls Multiport Setting 10- (obsolete) | 0.116 | 0.183 | 0.241 | 0.0031236 | 0.0034844 | 0.0037467 | 0.0034516
Detroit Controls #5000 Airid Variport (obsolete) Low setting | NONE | 0.011 | 0.016 | #VALUE! | 0.00020945 | 0.00024875 | #VALUE!
Detroit Controls #5000 Airid Variport (obsolete) Med setting | 0.036 | 0.051 | 0.061 | 0.00096939 | 0.00097107 | 0.00094835 | 0.00096294
Detroit Controls #5000 Airid Variport (obsolete) High setting | 0.066 | 0.125 | 0.166 | 0.0017772 | 0.0023801 | 0.0025807 | 0.002246
Dole 1933 | 0.033 | 0.055 | 0.07 | 0.00088861 | 0.0010472 | 0.0010883 | 0.001008
Dole 1A Setting 1 | 0.045 | 0.071 | 0.125 | 0.0012117 | 0.0013519 | 0.0019433 | 0.0015023
Dole 1A Setting 2 | 0.068 | 0.116 | 0.15 | 0.0018311 | 0.0022087 | 0.002332 | 0.0021239
Dole 1A Setting 3 | 0.083 | 0.125 | 0.166 | 0.002235 | 0.0023801 | 0.0025807 | 0.0023986
Dole 1A Setting 4 | 0.091 | 0.15 | 0.191 | 0.0024504 | 0.0028561 | 0.0029694 | 0.0027586
Dole 1A Setting 5 | 0.125 | 0.208 | 0.266 | 0.0033659 | 0.0039605 | 0.0041354 | 0.0038206
Dole 1A Setting 6 | 0.133 | 0.216 | 0.283 | 0.0035814 | 0.0041128 | 0.0043997 | 0.0040313
Dole 1A Setting 1 Modern Version W/Plastic Tongue *Note 4 | 0.061 | 0.111 | 0.148 | 0.0016426 | 0.0021135 | 0.0023009 | 0.002019
Dole 1A Setting 2 Modern Version W/Plastic Tongue *Note 4 | 0.084 | 0.141 | 0.186 | 0.0022619 | 0.0026847 | 0.0028917 | 0.0026128
Dole 1A Setting 3 Modern Version W/Plastic Tongue *Note 4 | 0.108 | 0.183 | 0.228 | 0.0029082 | 0.0034844 | 0.0035446 | 0.0033124
Dole 1A Setting 4 Modern Version W/Plastic Tongue *Note 4 | 0.116 | 0.201 | 0.254 | 0.0031236 | 0.0038272 | 0.0039488 | 0.0036332
Dole 1A Setting 5 Modern Version W/Plastic Tongue *Note 4 | 0.129 | 0.21 | 0.266 | 0.0034737 | 0.0039985 | 0.0041354 | 0.0038692
Dole 1A Setting 6 Modern Version W/Plastic Tongue *Note 4 | 0.133 | 0.22 | 0.274 | 0.0035814 | 0.0041889 | 0.0042598 | 0.00401
Dole 1A Setting 7 Modern Version W/Plastic Tongue *Note 4 | 0.143 | 0.233 | 0.295 | 0.0038506 | 0.0044365 | 0.0045863 | 0.0042911
Dole 1A Setting 8 Modern Version W/Plastic Tongue *Note 4 | 0.147 | 0.245 | 0.283 | 0.0039584 | 0.004665 | 0.0043997 | 0.004341
Dole 1A Setting 9 Modern Version W/Plastic Tongue *Note 4 | 0.152 | 0.268 | 0.289 | 0.004093 | 0.0051029 | 0.004493 | 0.004563
Dole 1A Setting 10 Modern Version W/Plastic Tongue *Note 4 | 0.152 | 0.269 | 0.289 | 0.004093 | 0.0051219 | 0.004493 | 0.0045693
Dole 1A Cap Removed Modern Version W/Plastic Tongue | 0.212 | 0.339 | 0.431 | 0.0057086 | 0.0064548 | 0.0067006 | 0.006288
Flair #51 - - (obsolete) | 0.116 | 0.191 | 0.25 | 0.0031236 | 0.0036368 | 0.0038867 | 0.003549
Gorton 4 | 0.025 | 0.04 | 0.055 | 0.00067319 | 0.00076163 | 0.00085507 | 0.00076329
Gorton 5 | 0.08 | 0.13 | 0.16 | 0.0021542 | 0.0024753 | 0.0024875 | 0.0023723
Gorton 6 | 0.15 | 0.235 | 0.3 | 0.0040391 | 0.0044746 | 0.004664 | 0.0043926
Gorton C | 0.27 | 0.45 | 0.57 | 0.0072704 | 0.0085683 | 0.0088616 | 0.0082334
Gorton D | 0.33 | 0.54 | 0.7 | 0.0088861 | 0.010282 | 0.010883 | 0.010017
Heat Timer Varivalve Min Setting Angle Pattern | 0.065 | 0.158 | 0.2 | 0.0017503 | 0.0030084 | 0.0031093 | 0.0026227
Heat Timer Varivalve 50% Setting Angle Pattern | 0.34 | 0.58 | 0.766 | 0.0091554 | 0.011044 | 0.011909 | 0.010703
Heat Timer Varivalve Max Setting Angle Pattern | 0.516 | 0.85 | 1.13 | 0.013895 | 0.016185 | 0.017568 | 0.015882
Heat Timer Varivalve Min Setting Straight Pattern | 0.06 | 0.083 | 0.33 | 0.0016157 | 0.0015804 | 0.0051304 | 0.0027755
Heat Timer Varivalve 50% Setting Straight Pattern | 0.53 | 0.8 | 1.03 | 0.014272 | 0.015233 | 0.016013 | 0.015172
Heat Timer Varivalve Max Setting Straight Pattern | 0.66 | 1.08 | 1.36 | 0.017772 | 0.020564 | 0.021143 | 0.019827
Hoffman #1 - - (obsolete) | 0.016 | 0.075 | 0.1 | 0.00043084 | 0.0014281 | 0.0015547 | 0.0011379
Hoffman 1A Setting 1 | 0.02 | 0.026 | 0.033 | 0.00053855 | 0.00049506 | 0.00051304 | 0.00051555
Hoffman 1A Setting 2 | 0.026 | 0.043 | 0.056 | 0.00070012 | 0.00081875 | 0.00087061 | 0.00079649
Hoffman 1A Setting 3 | 0.1 | 0.158 | 0.2 | 0.0026928 | 0.0030084 | 0.0031093 | 0.0029368
Hoffman 1A Setting 4 | 0.108 | 0.16 | 0.21 | 0.0029082 | 0.0030465 | 0.0032648 | 0.0030732
Hoffman 1A Setting 5 | 0.14 | 0.22 | 0.29 | 0.0037699 | 0.0041889 | 0.0045085 | 0.0041558
Hoffman 1A Setting 6 | 0.145 | 0.225 | 0.3 | 0.0039045 | 0.0042842 | 0.004664 | 0.0042842
Hoffman #2 Vacuum Vent Non Adjustable - - (obsolete) | 0.016 | 0.066 | 0.1 | 0.00043084 | 0.0012567 | 0.0015547 | 0.0010807
Hoffman #2 Vacuum Vent Setting 1 - - (obsolete) | 0.001 | 0.021 | 0.025 | 2.6928e-05 | 0.00039985 | 0.00038867 | 0.00027182
Hoffman #2 Vacuum Vent Setting 2 - - (obsolete) | 0.006 | 0.024 | 0.028 | 0.00016157 | 0.00045698 | 0.00043531 | 0.00035128
Hoffman #2 Vacuum Vent Setting 3 - - (obsolete) | 0.008 | 0.025 | 0.033 | 0.00021542 | 0.00047602 | 0.00051304 | 0.00040149
Hoffman #2 Vacuum Vent Setting 4 - - (obsolete) | 0.01 | 0.026 | 0.036 | 0.00026928 | 0.00049506 | 0.00055968 | 0.00044134
Hoffman #2 Vacuum Vent Setting 5 - - (obsolete) | 0.013 | 0.029 | 0.04 | 0.00035006 | 0.00055218 | 0.00062187 | 0.00050803
Hoffman #2 Vacuum Vent Setting 6 - - (obsolete) | 0.016 | 0.031 | 0.045 | 0.00043084 | 0.00059026 | 0.0006996 | 0.00057357
Hoffman #2A Vacuum Vent Setting 1 - - (obsolete) | 0.001 | 0.023 | 0.025 | 2.6928e-05 | 0.00043794 | 0.00038867 | 0.00028451
Hoffman #2A Vacuum Vent Setting 2 - - (obsolete) | 0.018 | 0.03 | 0.043 | 0.0004847 | 0.00057122 | 0.00066851 | 0.00057481
Hoffman #2A Vacuum Vent Setting 3 - - (obsolete) | 0.021 | 0.038 | 0.053 | 0.00056548 | 0.00072355 | 0.00082397 | 0.00070433
Hoffman #2A Vacuum Vent Setting 4 - - (obsolete) | 0.028 | 0.058 | 0.068 | 0.00075397 | 0.0011044 | 0.0010572 | 0.00097183
Hoffman #2A Vacuum Vent Setting 5 - - (obsolete) | 0.036 | 0.063 | 0.088 | 0.00096939 | 0.0011996 | 0.0013681 | 0.001179
Hoffman #2A Vacuum Vent Setting 6 - - (obsolete) | 0.041 | 0.083 | 0.116 | 0.001104 | 0.0015804 | 0.0018034 | 0.0014959
Hoffman #3 (Paul Vent) | 0.175 | 0.283 | 0.416 | 0.0047123 | 0.0053885 | 0.0064674 | 0.0055227
Hoffman 40 | 0.042 | 0.067 | 0.087 | 0.001131 | 0.0012757 | 0.0013526 | 0.0012531
Hoffman 41 | 0.058 | 0.1 | 0.125 | 0.0015618 | 0.0019041 | 0.0019433 | 0.0018031
Hoffman #70 Airport Non Adjustable - - (obsolete) | 0.05 | 0.108 | 0.141 | 0.0013464 | 0.0020564 | 0.0021921 | 0.0018649
Hoffman #70 Airport Setting #1 - - (obsolete) | 0.045 | 0.078 | 0.125 | 0.0012117 | 0.0014852 | 0.0019433 | 0.0015467
Hoffman #70 Airport Setting #2 - - (obsolete) | 0.05 | 0.087 | 0.15 | 0.0013464 | 0.0016565 | 0.002332 | 0.0017783
Hoffman #70 Airport Setting #3 - - (obsolete) | 0.053 | 0.116 | 0.166 | 0.0014272 | 0.0022087 | 0.0025807 | 0.0020722
Hoffman #70 Airport Setting #4 - - (obsolete) | 0.056 | 0.141 | 0.183 | 0.0015079 | 0.0026847 | 0.002845 | 0.0023459
Hoffman #70 Airport Setting #5 - - (obsolete) | 0.06 | 0.15 | 0.191 | 0.0016157 | 0.0028561 | 0.0029694 | 0.0024804
Hoffman #70 Airport Setting #6 - - (obsolete) | 0.066 | 0.15 | 0.191 | 0.0017772 | 0.0028561 | 0.0029694 | 0.0025342
Hoffman #74 Unit Heater Vent | 0.033 | 0.083 | 0.108 | 0.00088861 | 0.0015804 | 0.001679 | 0.0013827
Hoffman #500 | 0.066 | 0.112 | 0.142 | 0.0017772 | 0.0021326 | 0.0022076 | 0.0020391
Homart #775.8812 | 0.083 | 0.133 | 0.175 | 0.002235 | 0.0025324 | 0.0027207 | 0.002496
Marsh Paul Vent (circa 1901) - - (obsolete) | 0.35 | 0.583 | 0.75 | 0.0094246 | 0.011101 | 0.01166 | 0.010728
Marsh #3 (Paul Vent) - - (obsolete) | 0.183 | 0.295 | 0.375 | 0.0049277 | 0.005617 | 0.00583 | 0.0054582
Maid-O-Mist 4 | 0.028 | 0.045 | 0.06 | 0.00075397 | 0.00085683 | 0.0009328 | 0.00084787
Maid-O-Mist 5 | 0.1 | 0.158 | 0.2 | 0.0026928 | 0.0030084 | 0.0031093 | 0.0029368
Maid-O-Mist 6 | 0.15 | 0.241 | 0.3 | 0.0040391 | 0.0045888 | 0.004664 | 0.0044306
Maid-O-Mist C | 0.283 | 0.45 | 0.583 | 0.0076205 | 0.0085683 | 0.0090637 | 0.0084175
Maid-O-Mist D | 0.341 | 0.6 | 0.783 | 0.0091823 | 0.011424 | 0.012173 | 0.010927
M.S. Little Co. #L-15 - - (obsolete) | 0.026 | 0.045 | 0.055 | 0.00070012 | 0.00085683 | 0.00085507 | 0.000804
National Steam Specialty Co. Paul Vent - - (obsolete) | 0.15 | 0.266 | 0.333 | 0.0040391 | 0.0050648 | 0.005177 | 0.0047603
U.S. Radiator #3 Triton - - (obsolete) | 0.023 | 0.033 | 0.041 | 0.00061933 | 0.00062834 | 0.00063741 | 0.00062836
Ventrite #1 Setting 1 | Off | Off | Off | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Ventrite #1 Setting 2 | 0.033 | 0.02 | 0.021 | 0.00088861 | 0.00038081 | 0.00032648 | 0.00053197
Ventrite #1 Setting 3 | 0.025 | 0.036 | 0.046 | 0.00067319 | 0.00068546 | 0.00071515 | 0.00069127
Ventrite #1 Setting 4 | 0.03 | 0.053 | 0.066 | 0.00080783 | 0.0010092 | 0.0010261 | 0.00094769
Ventrite #1 Setting 5 | 0.045 | 0.071 | 0.091 | 0.0012117 | 0.0013519 | 0.0014147 | 0.0013261
Ventrite #1 Setting 6 | 0.056 | 0.091 | 0.116 | 0.0015079 | 0.0017327 | 0.0018034 | 0.0016814
Ventrite #1 Setting 7 | 0.07 | 0.108 | 0.133 | 0.0018849 | 0.0020564 | 0.0020677 | 0.002003
Ventrite #1 Setting 8 | 0.083 | 0.125 | 0.158 | 0.002235 | 0.0023801 | 0.0024564 | 0.0023571
Ventrite #2 IVS (obsolete Anderson Manufacturing) | 0.028 | 0.053 | 0.078 | 0.00075397 | 0.0010092 | 0.0012126 | 0.00099192
Ventrite #11 | 0.06 | 0.1 | 0.116 | 0.0016157 | 0.0019041 | 0.0018034 | 0.0017744
Watts SV | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 1/8 | 0.03 | 0.063 | 0.075 | 0.00080783 | 0.0011996 | 0.001166 | 0.0010578
Watts SVA setting 1/4 | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 1/2 ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 3/4 ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting 7/8 ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
Watts SVA setting Full ** | 0.066 | 0.108 | 0.133 | 0.0017772 | 0.0020564 | 0.0020677 | 0.0019671
STEAM TRAPS | 1 OZ. CFM | 2 OZ. CFM | 3 OZ. CFM | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Barnes & Jones 1/2" #122 | 1.5 | 1.8 | 2.7 | 0.040391 | 0.034273 | 0.041976 | 0.03888
Dunham #1 1/2" - - (obsolete) | 1.45 | 2.41 | 3 | 0.039045 | 0.045888 | 0.04664 | 0.043858
Dunham #1 W/B&J Cage Unit | 0.73 | 1.16 | 1.5 | 0.019657 | 0.022087 | 0.02332 | 0.021688
Dunham - Bush #1E - - (obsolete) | 1.08 | 1.8 | 2.25 | 0.029082 | 0.034273 | 0.03498 | 0.032778
Dunham - Bush #1E W/B&J Cage Unit | 0.71 | 1.13 | 1.41 | 0.019119 | 0.021516 | 0.021921 | 0.020852
Hoffman 17C 1/2" W/Dura-Stat Capsule | 0.53 | 0.85 | 1.1 | 0.014272 | 0.016185 | 0.017101 | 0.015852
Hoffman 17C W/B&J Cage Unit | 1.3 | 2.116 | 2.7 | 0.035006 | 0.04029 | 0.041976 | 0.039091
Hoffman 17D 1/2" Model 1939 - - (obsolete) | 1.45 | 2.38 | 3 | 0.039045 | 0.045317 | 0.04664 | 0.043667
Ideal Heating Co. Thermostatic 1/2" - - (obsolete) | 1.53 | 2.33 | 3.08 | 0.041199 | 0.044365 | 0.047884 | 0.044483
Ideal W/B&J Cage Unit Installed | 1.25 | 2 | 2.58 | 0.033659 | 0.038081 | 0.04011 | 0.037284
Illinois 1/2" #1G | 0.86 | 1.2 | 1.6 | 0.023158 | 0.022849 | 0.024875 | 0.023627
Marsh #1 Reflux - - (obsolete) | 1.13 | 1.83 | 2.36 | 0.030428 | 0.034844 | 0.03669 | 0.033988
Marsh #1 Reflux W/B&J Cage Unit | 0.73 | 1.16 | 1.5 | 0.019657 | 0.022087 | 0.02332 | 0.021688
Marsh 1N 1/2" | 0.53 | 0.91 | 1.16 | 0.014272 | 0.017327 | 0.018034 | 0.016544
Mepco 1/2" #1E | 1.08 | 1.4 | 1.9 | 0.029082 | 0.026657 | 0.029539 | 0.028426
Mepco 1/2" #1R | 1.08 | 1.4 | 1.9 | 0.029082 | 0.026657 | 0.029539 | 0.028426
Milvaco Model #0 - - (obsolete) | 1.08 | 1.71 | 2.13 | 0.029082 | 0.03256 | 0.033114 | 0.031585
Milvaco Model #0 W/B&J Cage Unit | 1 | 1.58 | 1.966 | 0.026928 | 0.030084 | 0.030565 | 0.029192
Monash #30 1/2" | 0.86 | 1.2 | 1.6 | 0.023158 | 0.022849 | 0.024875 | 0.023627
Monash #34 1/2" | 1.21 | 2 | 2.5 | 0.032582 | 0.038081 | 0.038867 | 0.03651
Monash #38 1/2" | 1.45 | 2.45 | 3.08 | 0.039045 | 0.04665 | 0.047884 | 0.044526
Mouat Model 1924 Thermostatic 1/2" - - (obsolete) | 1.53 | 2.33 | 3.08 | 0.041199 | 0.044365 | 0.047884 | 0.044483
Mouat 1924 W/B&J Cage Unit Installed | 1.25 | 2 | 2.58 | 0.033659 | 0.038081 | 0.04011 | 0.037284
Mouat #35 1/2" - - (Obsolete) | 1.33 | 1.66 | 2.08 | 0.035814 | 0.031608 | 0.032337 | 0.033253
Mouat #35 1/2" W/B&J Cage Unit Installed | 1.366 | 2.33 | 2.91 | 0.036783 | 0.044365 | 0.045241 | 0.04213
Mouat #36 1/2" - - (Obsolete) | 1.083 | 1.533 | 1.83 | 0.029163 | 0.029189 | 0.02845 | 0.028934
Mouat #36 1/2" W/B&J Cage Unit Installed | 1.266 | 2 | 2.5 | 0.03409 | 0.038081 | 0.038867 | 0.037013
Mouat Water Seal Trap 1/2" Oval - - (obsolete) | 2 | 2.4 | 3.4 | 0.053855 | 0.045698 | 0.052859 | 0.050804
Mouat Water Seal Trap 1/2" Round - - (obsolete) | 2 | 2.4 | 3.6 | 0.053855 | 0.045698 | 0.055968 | 0.05184
Nicholson #N125 | 1.53 | 2.53 | 3.08 | 0.041199 | 0.048173 | 0.047884 | 0.045752
Sarco A125 1/2" | 0.5 | 0.78 | 1 | 0.013464 | 0.014852 | 0.015547 | 0.014621
Sterling 7-50-A-1/2" | 1.08 | 1.75 | 2.16 | 0.029082 | 0.033321 | 0.033581 | 0.031995
Trane B1 W/Original Bellows - - (obsolete) | 0.5 | 0.75 | 1 | 0.013464 | 0.014281 | 0.015547 | 0.01443
Trane B1 W/Modern Trane Element | 0.78 | 1.25 | 1.58 | 0.021004 | 0.023801 | 0.024564 | 0.023123
Trane B1 W/B&J Cage Unit | 0.75 | 1.2 | 1.5 | 0.020196 | 0.022849 | 0.02332 | 0.022121
Trane 1/2" (no number) - - (obsolete) | 1.58 | 2.66 | 3.33 | 0.042546 | 0.050648 | 0.05177 | 0.048321
Warren Webster 02H 1/2" W/B&J Cage Unit | 0.783 | 1.333 | 1.75 | 0.021084 | 0.025381 | 0.027207 | 0.024557
Warren Webster 02H 1/2" W/Tunstall Capsule | 0.616 | 0.966 | 1.21 | 0.016587 | 0.018393 | 0.018811 | 0.017931
Warren Webster 512H 1/2" W/512A seat (5/16") - - (obsolete) | 1.08 | 1.75 | 2.25 | 0.029082 | 0.033321 | 0.03498 | 0.032461
Warren Webster 512H 1/2" W/512S seat (1/4") - - (obsolete) | 0.783 | 1.28 | 1.66 | 0.021084 | 0.024372 | 0.025807 | 0.023755
Warren Webster 512H 1/2" W/B&J Cage Unit | 1.36 | 2.25 | 2.83 | 0.036621 | 0.042842 | 0.043997 | 0.041153
Warren Webster 712HB 1/2" W/H57 Seat (.368") - - (obsolete) | 0.75 | 1.233 | 1.433 | 0.020196 | 0.023477 | 0.022278 | 0.021984
Warren Webster 712 HB 1/2" W/522S Seat (.332") - - (obsolete) | 0.5 | 0.8 | 1.25 | 0.013464 | 0.015233 | 0.019433 | 0.016043
Warren Webster 712 HB 1/2" W/B&J Cage Unit | 1.55 | 2.55 | 3.216 | 0.041738 | 0.048554 | 0.049998 | 0.046763
Barnes & Jones 3/4" #134A | 1.36 | 2.28 | 2.88 | 0.036621 | 0.043413 | 0.044774 | 0.041603
Hoffman 8C 3/4" | 1 | 1.58 | 2 | 0.026928 | 0.030084 | 0.031093 | 0.029368
Mepco 3/4" 2E | 1.53 | 2.55 | 3.16 | 0.041199 | 0.048554 | 0.049127 | 0.046293
Monash #48 3/4" | 2.16 | 3.5 | 5 | 0.058164 | 0.066642 | 0.077733 | 0.067513
Sterling 3/4" #753A | 1.25 | 2 | 2.58 | 0.033659 | 0.038081 | 0.04011 | 0.037284
Spirax Sarco F&T Traps (FT-15, FT-30, etc.) | 0.5 | 0.75 | 0.966 | 0.013464 | 0.014281 | 0.015018 | 0.014254
Hoffman F&T Traps (FT015H, FT015C, etc.) | 0.5 | 0.75 | 0.95 | 0.013464 | 0.014281 | 0.014769 | 0.014171
Sterling F&T Traps (vac. to 15 lb.) | 1.3 | 2.083 | 2.666 | 0.035006 | 0.039662 | 0.041447 | 0.038705
Barnes & Jones F&T Traps (vac. to 15 lb.) | 0.75 | 1.2 | 1.5 | 0.020196 | 0.022849 | 0.02332 | 0.022121

## REPORT
Address:
Boiler Information |  | Relevant Calculations
Boiler Manufacturer | Burnham | Time to Steam(minutes) | 10
Boiler Model | STMX299 | Time to Vent(minutes) | 23
Rated Power Input(BTU/HR) | 299000 | Time to Steady State(min) | 56.2951
Gross Power Output(BTU/HR) | 246000
Water @ Waterline(gal) | 15.6
Generation/Radiation | 112% | System Status
|  | Trap Operating % | 0%
|  | Radiator Efficiency % | 100%
Radiator Calculations |  | Steam Loss(BTU/Hr) | 0
TOTAL RADIATION (BTU/HR) | 219545.6618 | Failed Traps | 21
Total Radiation/Radiators | 1.0348
TOTAL RADIATION (EDR) | 914.7736
Radiator Output(EDR) | 884 | Combustion Air
Steam Main Output(EDR) | 7.9617 | One Opening Size(in2) | 159.5556
Steam Upfeed Output(EDR) | 22.8119 | Two Opening Size(in2) | 119.6667
Column Radiators | 0
Tube Radiators | 21
Convectors | 0
Copper Cabinets | 0
Notes

## Boiler List (hidden)
Manufacturer | Boiler Model | Input MBH (Note 2) | Gross Output MBH (Note 2) | Sq. Ft. Steam | Boiler Water Content Gallons (Steam to Waterline) | Approx. Shipping Weight (lbs.) | Steamable Volume(gal) |  | Manufactuer List
Weil-Mclain | LGB-4 | 400 | 312 | 975 | 23.2 | 1185 |  | Weil-Mclain
Weil-Mclain | LGB-5 | 520 | 409 | 1279 | 28.9 | 1455 |  | Weil-Mclain | Weil-Mclain
Weil-Mclain | LGB-6 | 650 | 514 | 1607 | 34.6 | 1725 |  | Weil-Mclain | Burnham
Weil-Mclain | LGB-7 | 780 | 619 | 1936 | 40.3 | 2005 |  | Weil-Mclain | Peerless
Weil-Mclain | LGB-8 | 910 | 724 | 2264 | 46 | 2290 |  | Weil-Mclain | Green Mountain
Weil-Mclain | LGB-9 | 1040 | 829 | 2591 | 51.9 | 2560 |  | Weil-Mclain
Weil-Mclain | LGB-10 | 1170 | 934 | 2918 | 57.6 | 2800 |  | Weil-Mclain
Weil-Mclain | LGB-11 | 1300 | 1039 | 3246 | 63.4 | 3105 |  | Weil-Mclain
Weil-Mclain | LGB-12 | 1430 | 1144 | 3576 | 69.1 | 3365 |  | Weil-Mclain
Weil-Mclain | LGB-13 | 1560 | 1239 | 3868 | 74.9 | 3785 |  | Weil-Mclain
Weil-Mclain | LGB-14 | 1690 | 1344 | 4228 | 80.7 | 4085 |  | Weil-Mclain
Weil-Mclain | LGB-15 | 1820 | 1449 | 4592 | 86.4 | 4355 |  | Weil-Mclain
Weil-Mclain | LGB-16 | 1950 | 1552 | 4950 | 92.2 | 4725 |  | Weil-Mclain
Weil-Mclain | LGB-17 | 2080 | 1658 | 5316 | 98 | 4975 |  | Weil-Mclain
Weil-Mclain | LGB-18 | 2210 | 1764 | 5682 | 103.6 | 5270 |  | Weil-Mclain
Weil-Mclain | LGB-19 | 2340 | 1867 | 6034 | 109.5 | 5540 |  | Weil-Mclain
Weil-Mclain | LGB-20 | 2470 | 1974 | 6384 | 115.3 | 5820 |  | Weil-Mclain
Weil-Mclain | LGB-21 | 2600 | 2077 | 6720 | 121 | 6080 |  | Weil-Mclain
Weil-Mclain | LGB-22 | 2730 | 2184 | 7065 | 126.8 | 6365 |  | Weil-Mclain
Weil-Mclain | LGB-23 | 2860 | 2288 | 7402 | 132.5 | 6625 |  | Weil-Mclain
Weil-Mclain | Series 80 - 380 | 346 | 278 | 867 | 27.5 | 1058 |  | Weil-Mclain
Weil-Mclain | Series 80 - 480 | 491 | 396 | 1238 | 36 | 1203 |  | Weil-Mclain
Weil-Mclain | Series 80 - 580 | 639 | 515 | 1608 | 44.5 | 1448 |  | Weil-Mclain
Weil-Mclain | Series 80 - 680 | 787 | 634 | 1983 | 53 | 1843 |  | Weil-Mclain
Weil-Mclain | Series 80 - 780 | 935 | 753 | 2354 | 61.5 | 2088 |  | Weil-Mclain
Weil-Mclain | Series 80 - 880 | 1082 | 872 | 2725 | 70 | 2317 |  | Weil-Mclain
Weil-Mclain | Series 80 - 980 | 1230 | 991 | 3096 | 78.5 | 2678 |  | Weil-Mclain
Weil-Mclain | Series 80 - 1080 | 1378 | 1110 | 3471 | 87 | 2923 |  | Weil-Mclain
Weil-Mclain | Series 80 - 1180 | 1526 | 1229 | 3842 | 95.5 | 3068 |  | Weil-Mclain
Weil-Mclain | Series 80 - 1280 | 1674 | 1348 | 4242 | 104 | 3313 |  | Weil-Mclain
Weil-Mclain | Series 88 - 488R | 996 | 827 | 2583 | 109 | 2860 |  | Weil-Mclain
Weil-Mclain | Series 88 - 488 | 1010 | 839 | 2621 | 109 | 2860 |  | Weil-Mclain
Weil-Mclain | Series 88 - 588 | 1356 | 1126 | 3521 | 132 | 3340 |  | Weil-Mclain
Weil-Mclain | Series 88 - 688 | 1701 | 1413 | 4469 | 155 | 3820 |  | Weil-Mclain
Weil-Mclain | Series 88 - 788 | 2046 | 1700 | 5463 | 178 | 4345 |  | Weil-Mclain
Weil-Mclain | Series 88 - 788R | 1999 | 1661 | 5463 | 178 | 4345 |  | Weil-Mclain
Weil-Mclain | Series 88 - 888 | 2382 | 1987 | 6427 | 201 | 4925 |  | Weil-Mclain
Weil-Mclain | Series 88 - 988R | 2482 | 2062 | 6671 | 224 | 5600 |  | Weil-Mclain
Weil-Mclain | Series 88 - 988 | 2737 | 2274 | 7358 | 224 | 5600 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1088R | 2887 | 2399 | 7763 | 247 | 6130 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1088 | 3082 | 2561 | 8283 | 247 | 6130 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1188 | 3428 | 2848 | 9213 | 270 | 6695 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1288 | 3773 | 3135 | 10147 | 293 | 7260 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1388 | 4119 | 3422 | 11071 | 316 | 7890 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1488 | 4464 | 3709 | 12000 | 339 | 8410 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1588 | 4809 | 3996 | 12925 | 362 | 9005 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1688R | 4979 | 4137 | 13383 | 385 | 9525 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1688 | 5155 | 4283 | 13854 | 385 | 9525 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1788 | 5494 | 4570 | 14783 | 408 | 9780 |  | Weil-Mclain
Weil-Mclain | Series 88 - 1888 | 5845 | 4857 | 15713 | 431 | 10775 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1094 | 3247 | 2607 | 8435 | 329.8 | 12320 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1194 | 3608 | 2897 | 9372 | 357.5 | 13162 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1294 | 3969 | 3187 | 10310 | 385.2 | 14004 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1394 | 4330 | 3481 | 11262 | 413 | 14846 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1494 | 4691 | 3772 | 12201 | 440.7 | 15688 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1594 | 5052 | 4062 | 13140 | 468.4 | 16530 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1694 | 5412 | 4351 | 14076 | 496.2 | 17372 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1794 | 5773 | 4641 | 15015 | 523.9 | 19014 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1894 | 6134 | 4938 | 15974 | 551.6 | 19856 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-1994 | 6495 | 5228 | 16914 | 579.4 | 20698 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-2094 | 6856 | 5519 | 17854 | 607.1 | 21540 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-2194 | 7216 | 5809 | 18792 | 634.8 | 22552 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-2294 | 7649 | 6157 | 19919 | 662.6 | 23419 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-2394 | 7938 | 6390 | 20672 | 690.3 | 24286 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-2494 | 8371 | 6739 | 21799 | 718 | 25153 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-2594 | 8660 | 6971 | 22552 | 745.8 | 26020 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-894 | 2540 | 2040 | 6598 | 274.3 | 10636 |  | Weil-Mclain
Weil-Mclain | Series 94 - H-994 | 2887 | 2318 | 7500 | 302 | 11478 |  | Weil-Mclain
Weil-Mclain | *EG-30- | 75 | 62 | 196 | 8.4 | 430 |  | Weil-Mclain
Weil-Mclain | *EG-35- | 100 | 82 | 258 | 8.4 | 430 |  | Weil-Mclain
Weil-Mclain | *EG-40- | 125 | 103 | 321 | 9.8 | 505 |  | Weil-Mclain
Weil-Mclain | *EG-45- | 150 | 124 | 388 | 9.8 | 505 |  | Weil-Mclain
Weil-Mclain | *EG-50- | 175 | 145 | 454 | 11.2 | 585 |  | Weil-Mclain
Weil-Mclain | *EG-55- | 200 | 166 | 521 | 11.2 | 585 |  | Weil-Mclain
Weil-Mclain | *EG-65- | 238 | 198 | 621 | 12.6 | 660 |  | Weil-Mclain
Weil-Mclain | EG-75- | 282 | 234 | 733 | 14 | 735 |  | Weil-Mclain
Weil-Mclain | EGH-85-S | 315 | 240.24 | 760 | 15.4 | 825 |  | Weil-Mclain
Weil-Mclain | EGH-95-S | 360 | 275.88 | 868 | 16.8 | 915 |  | Weil-Mclain
Weil-Mclain | EGH-105-S | 405 | 308.88 | 977 | 18.2 | 1005 |  | Weil-Mclain
Weil-Mclain | EGH-115-S | 450 | 343.2 | 1085 | 19.6 | 1095 |  | Weil-Mclain
Weil-Mclain | EGH-125-S | 495 | 378.84 | 1193 | 21 | 1185 |  | Weil-Mclain
Burnham | V1104H | 837 | 674 | 2106 | 59 | 2103.94 |  | Burnham
Burnham | V1105H | 1068 | 862 | 2694 | 68 | 2508.88 |  | Burnham
Burnham | V1106H | 1328 | 1074 | 3358 | 77 | 2918.82 |  | Burnham
Burnham | V1107H | 1588 | 1288 | 4036 | 87 | 3324.42 |  | Burnham
Burnham | V1108H | 1876 | 1525 | 4857 | 96 | 3732.36 |  | Burnham
Burnham | V1109H | 2136 | 1741 | 5604 | 105 | 4146.3 |  | Burnham
Burnham | V1110H | 2396 | 1958 | 6333 | 115 | 4555.9 |  | Burnham
Burnham | V1111H | 2656 | 2175 | 7037 | 124 | 4962.84 |  | Burnham
Burnham | V1112H | 2887 | 2370 | 7668 | 133 | 5372.78 |  | Burnham
Burnham | V1113H | 3103 | 2546 | 8236 | 143 | 5769.38 |  | Burnham
Burnham | V1114H | 3392 | 2781 | 8997 | 152 | 6182.32 |  | Burnham
Burnham | V1115H | 3680 | 3015 | 9754 | 161 | 6599.26 |  | Burnham
Burnham | V1116H | 3897 | 3191 | 10323 | 171 | 7005.86 |  | Burnham
Burnham | V1117H | 4186 | 3425 | 11081 | 180 | 7414.8 |  | Burnham
Burnham | V1118H | 4474 | 3659 | 11835 | 189 | 7820.74 |  | Burnham
Burnham | V1119H | 4691 | 3833 | 12401 | 199 | 8229.34 |  | Burnham
Burnham | V1120H | 4979 | 4066 | 13154 | 208 | 8636.28 |  | Burnham
Burnham | V1121H | 5268 | 4299 | 13908 | 217 | 9051.22 |  | Burnham
Burnham | V1122H | 5485 | 4473 | 14471 | 227 | 9453.82 |  | Burnham
Burnham | V1123H | 5773 | 4705 | 15221 | 236 | 9862.76 |  | Burnham
Burnham | V903A | 447 | 347 | 1083 | 44.5 | 1067.87 |  | Burnham
Burnham | V904A | 606 | 483 | 1508 | 53 | 1368.98 |  | Burnham
Burnham | V905A | 808 | 646 | 2021 | 61.5 | 1671.09 |  | Burnham
Burnham | V906A | 1010 | 808 | 2525 | 70 | 1973.2 |  | Burnham
Burnham | V907A | 1198 | 959 | 2996 | 78.5 | 2275.31 |  | Burnham
Burnham | V908A | 1386 | 1110 | 3471 | 87 | 2577.42 |  | Burnham
Burnham | V909A | 1674 | 1342 | 4225 | 95.5 | 2879.53 |  | Burnham
Burnham | V910A | 1905 | 1528 | 4867 | 104 | 3180.64 |  | Burnham
Burnham | V911A | 2136 | 1714 | 5513 | 112.5 | 3482.75 |  | Burnham
Burnham | V912A | 2367 | 1900 | 6142 | 121 | 3784.86 |  | Burnham
Burnham | STMX075 | 75 | 62 | 169 | 6.8 | 484 | 0.54 | Burnham
Burnham | STMX100 | 100 | 82 | 258 | 6.8 | 484 | 0.54 | Burnham
Burnham | STMX125 | 125 | 103 | 321 | 9 | 600 | 0.64 | Burnham
Burnham | STMX150 | 150 | 124 | 388 | 9 | 600 | 0.64 | Burnham
Burnham | STMX175 | 175 | 144 | 450 | 11.2 | 729 | 0.72 | Burnham
Burnham | STMX200 | 200 | 165 | 517 | 11.2 | 729 | 0.72 | Burnham
Burnham | STMX250 | 250 | 206 | 646 | 13.2 | 842 | 0.84 | Burnham
Burnham | STMX299 | 299 | 246 | 771 | 15.6 | 881 | 0.89 | Burnham
Burnham | STMX350 | 350 | 284 | 892 | 27.8 | 1008 | 0.97 | Burnham
Burnham | STMX399 | 399 | 323 | 1013 | 20.1 | 1123 | 1.04 | Burnham
Burnham | STMX450 | 450 | 365 | 1142 | 22.2 | 1239 | 1.14 | Burnham
Burnham | STMX500 | 500 | 405 | 1271 | 24.4 | 1354 | 1.22 | Burnham
Burnham | STMX550 | 550 | 446 | 1396 | 26.6 | 1469 | 1.31 | Burnham
Burnham | Independence3 | 62 | 51 | 158 | 5.1 | 350 | 1.2 | Burnham
Burnham | Independence4 | 105 | 87 | 271 | 6.5 | 420 | 1.5 | Burnham
Burnham | Independence5 | 140 | 115 | 358 | 7.9 | 485 | 1.8 | Burnham
Burnham | Independence6 | 175 | 144 | 450 | 9.3 | 555 | 2.1 | Burnham
Burnham | Independence7 | 210 | 173 | 542 | 10.7 | 620 | 2.4 | Burnham
Burnham | Independence8 | 245 | 202 | 633 | 12.1 | 690 | 2.7 | Burnham
Burnham | Independence9 | 280 | 231 | 721 | 13.5 | 760 | 3 | Burnham
Peerless | 63-03L | 88.5 | 74 | 233 | 9.3 | 465 |  | Peerless
Peerless | 63-03 | 118 | 98 | 308 | 9.3 | 465 |  | Peerless
Peerless | 63-04L | 147.5 | 123 | 383 | 10.8 | 576 |  | Peerless
Peerless | 63-04 | 177 | 147 | 458 | 10.8 | 576 |  | Peerless
Peerless | 63-05L | 206.5 | 171 | 533 | 12.4 | 700 |  | Peerless
Peerless | 63-05 | 236 | 196 | 613 | 12.4 | 700 |  | Peerless
Peerless | 63-06 | 287.5 | 238 | 746 | 13.9 | 812 |  | Peerless
Peerless | SC(T)-05 | 404 | 327 | 1022 | 20.4 | 815 |  | Peerless
Peerless | SC(T)-06 | 505 | 409 | 1278 | 23.52 | 910 |  | Peerless
Peerless | SC(T)-07 | 577 | 468 | 1463 | 26.64 | 1005 |  | Peerless
Peerless | SC(T)-08 | 649 | 527 | 1647 | 29.76 | 1100 |  | Peerless
Peerless | SC(T)-09 | 722 | 586 | 1832 | 32.88 | 1195 |  | Peerless
Peerless | SC(T)-10 | 794 | 645 | 2016 | 36 | 1280 |  | Peerless
Peerless | 64-07 | 345 | 274 | 858 | 15.5 | 945 |  | Peerless
Peerless | 64-08 | 399 | 318 | 996 | 17 | 1081 |  | Peerless
Peerless | 64-09 | 460 | 367 | 1146 | 18.6 | 1218 |  | Peerless
Peerless | 64-10 | 517.5 | 413 | 1292 | 20.1 | 1354 |  | Peerless
Peerless | 64-11 | 575 | 459 | 1433 | 21.7 | 1490 |  | Peerless
Peerless | 64-12 | 632.5 | 506 | 1583 | 23.2 | 1527 |  | Peerless
Peerless | TCII-04 | 1143 | 931 | 2908 | 104 | 3185.844 |  | Peerless
Peerless | TCII-05 | 1458 | 1194 | 3733 | 126 | 3784.498 |  | Peerless
Peerless | TCII-06 | 1773 | 1458 | 4625 | 148 | 4383.152 |  | Peerless
Peerless | TCII-07 | 2088 | 1722 | 5542 | 169 | 4981.806 |  | Peerless
Peerless | TCII-08 | 2403 | 1985 | 6421 | 192 | 5580.46 |  | Peerless
Peerless | TCII-09 | 2718 | 2249 | 7275 | 214 | 6180.114 |  | Peerless
Peerless | TCII-10 | 3033 | 2513 | 8129 | 236 | 6793.768 |  | Peerless
Peerless | TCII-11 | 3348 | 2776 | 8979 | 258 | 7392.422 |  | Peerless
Peerless | TCII-12 | 3663 | 3040 | 9833 | 280 | 7991.076 |  | Peerless
Peerless | TCII-13 | 3978 | 3304 | 10688 | 302 | 8600.73 |  | Peerless
Peerless | TCII-14 | 4293 | 3567 | 11538 | 324 | 9194.384 |  | Peerless
Peerless | TCII-15 | 4608 | 3851 | 12392 | 346 | 10014.038 |  | Peerless
Peerless | TCII-16 | 4923 | 4095 | 13246 | 368 | 10653.692 |  | Peerless
Peerless | TCII-17 | 5238 | 4358 | 14100 | 390 | 11293.346 |  | Peerless
Peerless | TCII-18 | 5553 | 4622 | 14954 | 412 | 11933 |  | Peerless
Peerless | LC-04 | 686 | 1708 | 410 | 40.57 | 890 |  | Peerless
Peerless | LC-05R | 808 | 2029 | 487 | 47.29 | 1080 |  | Peerless
Peerless | LC-05 | 881 | 2208 | 530 | 47.29 | 1080 |  | Peerless
Peerless | LC-06 | 1077 | 2713 | 651 | 54.01 | 1270 |  | Peerless
Peerless | LC-07 | 1273 | 3217 | 772 | 60.73 | 1460 |  | Peerless
Peerless | LC-08 | 1469 | 3717 | 892 | 67.45 | 1650 |  | Peerless
Peerless | LC-09 | 1664 | 4250 | 1020 | 74.17 | 1840 |  | Peerless
Peerless | LC-10 | 1860 | 4804 | 1153 | 80.89 | 2030 |  | Peerless
Peerless | LC-11 | 2056 | 5367 | 1288 | 87.61 | 2220 |  | Peerless
Peerless | LC-12 | 2252 | 5917 | 1420 | 94.33 | 2410 |  | Peerless
Peerless | LCE-13 | 2464 | 6358 | 1526 | 101.05 | 2600 |  | Peerless
Peerless | LCE-14 | 2657 | 6875 | 1650 | 107.77 | 2790 |  | Peerless
Peerless | LCE-15 | 2850 | 7388 | 1773 | 114.49 | 2980 |  | Peerless
Peerless | LCE-16 | 3043 | 7908 | 1898 | 121.21 | 3170 |  | Peerless
Peerless | LCE-17 | 3236 | 8421 | 2021 | 127.93 | 3360 |  | Peerless
Peerless | LCE-18 | 3429 | 8938 | 2145 | 134.65 | 3550 |  | Peerless
Peerless | LCE-19 | 3622 | 9454 | 2269 | 141.37 | 3740 |  | Peerless
Peerless | LCE-20 | 3815 | 9971 | 2393 | 148.09 | 3930 |  | Peerless
Peerless | LCE-21 | 4027 | 10533 | 2528 | 154.81 | 4120 |  | Peerless
Peerless | LCE-22 | 4239 | 11096 | 2663 | 161.53 | 4310 |  | Peerless
Peerless | LCE-23 | 4451 | 11658 | 2798 | 168.25 | 4500 |  | Peerless
Peerless | LCE-24 | 4663 | 12217 | 2932 | 174.97 | 4690 |  | Peerless
Peerless | CC-03 | 375 | 308 | 963 | 33 | 1440.78 |  | Peerless
Peerless | CC-04 | 520 | 421 | 1316 | 41 | 1780.06 |  | Peerless
Peerless | CC-05 | 722 | 587 | 1725 | 49 | 2119.34 |  | Peerless
Peerless | CC-06 | 938 | 762 | 2382 | 56 | 2465.96 |  | Peerless
Peerless | CC-07 | 1140 | 924 | 2888 | 64 | 2805.24 |  | Peerless
Peerless | CC-08 | 1342 | 1087 | 3398 | 72 | 3144.52 |  | Peerless
Peerless | CC-09 | 1559 | 1262 | 3947 | 80 | 3482.8 |  | Peerless
Peerless | CC-10 | 1761 | 1424 | 4506 | 88 | 3821.08 |  | Peerless
Peerless | CC-11 | 1963 | 1587 | 5071 | 96 | 4159.36 |  | Peerless
Peerless | CC-12 | 2165 | 1750 | 5635 | 104 | 4498.64 |  | Peerless
Peerless | 211A-04 | 630 | 486 | 1521 | 15.1 | 2523 |  | Peerless
Peerless | 211A-05 | 840 | 664 | 2075 | 18.2 | 2900 |  | Peerless
Peerless | 211A-06 | 1050 | 830 | 2596 | 21.3 | 3450 |  | Peerless
Peerless | 211A-07 | 1260 | 995 | 3108 | 24.4 | 3900 |  | Peerless
Peerless | 211A-08 | 1470 | 1161 | 3629 | 27.5 | 4390 |  | Peerless
Peerless | 211A-09 | 1680 | 1327 | 4146 | 30.6 | 4875 |  | Peerless
Peerless | 211A-10 | 1890 | 1493 | 4667 | 33.7 | 5320 |  | Peerless
Peerless | 211A-11 | 2100 | 1659 | 5183 | 36.8 | 5900 |  | Peerless
Peerless | 211A-12 | 2310 | 1825 | 5704 | 39.9 | 6370 |  | Peerless
Peerless | 211A-13 | 2520 | 1958 | 6333 | 43 | 7150 |  | Peerless
Peerless | 211A-14 | 2730 | 2124 | 6871 | 46.1 | 7700 |  | Peerless
Peerless | 211A-15 | 2940 | 2290 | 7408 | 49.2 | 8250 |  | Peerless
Peerless | 211A-16 | 3150 | 2454 | 7938 | 52.3 | 8800 |  | Peerless
Peerless | 211A-17 | 3360 | 2621 | 8479 | 55.4 | 9350 |  | Peerless
Peerless | 211A-18 | 3570 | 2785 | 9008 | 58.5 | 9900 |  | Peerless
Peerless | 211A-19 | 3780 | 2952 | 9550 | 61.75 | 10450 |  | Peerless
Peerless | 211A-20 | 3990 | 3116 | 10079 | 65 | 11000 |  | Peerless
Peerless | 211A-21 | 4200 | 3280 | 10613 | 68.25 | 11550 |  | Peerless
Peerless | 211A-22 | 4410 | 3449 | 11158 | 71.5 | 12100 |  | Peerless
Peerless | 211A-23 | 4620 | 3599 | 11642 | 74.75 | 12650 |  | Peerless
Peerless | 211A-24 | 4830 | 3763 | 12175 | 78 | 13200 |  | Peerless
Peerless | 211A-25 | 5040 | 3931 | 12717 | 81.25 | 13750 |  | Peerless
Peerless | 211A-26 | 5250 | 4095 | 13246 | 84.5 | 14300 |  | Peerless
Peerless | 211A-27 | 5460 | 4259 | 13779 | 87.75 | 14850 |  | Peerless
Peerless | 211A-28 | 5670 | 4428 | 14325 | 91 | 15400 |  | Peerless
Peerless | 211A-29 | 5880 | 4592 | 14854 | 94.25 | 15950 |  | Peerless
Peerless | 211A-30 | 6090 | 4756 | 15388 | 97.5 | 16500 |  | Peerless
Peerless | 211A-31 | 6300 | 4920 | 15917 | 100.75 | 17050 |  | Peerless
Peerless | 211A-32 | 6510 | 5084 | 16446 | 104 | 17600 |  | Peerless
Peerless | 211A-33 | 6720 | 5255 | 17000 | 107.25 | 18150 |  | Peerless
Peerless | 211A-34 | 6930 | 5419 | 17529 | 110.5 | 18700 |  | Peerless
Peerless | 211A-35 | 7140 | 5583 | 18063 | 113.75 | 19250 |  | Peerless
Peerless | 211A-36 | 7350 | 5748 | 18596 | 117 | 19800 |  | Peerless
Peerless | 211A-37 | 7560 | 5904 | 19100 | 120.25 | 20350 |  | Peerless
Peerless | EC(T)-e-03 | 105 | 92 | 288 | 14.16 | 570 |  | Peerless
Peerless | EC(T)-e-03 | 140 | 121 | 379 | 14.16 | 570 |  | Peerless
Peerless | EC(T)-e-04 | 175 | 152 | 475 | 17.28 | 710 |  | Peerless
Peerless | EC(T)-e-04 | 210 | 181 | 567 | 17.28 | 710 |  | Peerless
Peerless | EC(T)-e-05 | 245 | 213 | 667 | 20.4 | 840 |  | Peerless
Peerless | EC(T)-e-05 | 280 | 242 | 758 | 20.4 | 840 |  | Peerless
Peerless | EC(T)-05† | 336 | 279 | 874 | 20.4 | 840 |  | Peerless
Peerless | EC(T)-e-06† | 308 | 259 | 811 | 23.52 | 990 |  | Peerless
Peerless | EC(T)-e-06† | 336 | 282 | 883 | 23.52 | 990 |  | Peerless
Peerless | EC(T)-06† | 385 | 321 | 1006 | 23.52 | 990 |  | Peerless
Peerless | EC(T)-06† | 420 | 347 | 1087 | 23.52 | 990 |  | Peerless
Peerless | WBV-e-03-085-S | 119 | 104 | 325 | 12 | 584 |  | Peerless
Peerless | WBV-e-03-105-S | 147 | 127 | 396 | 12 | 584 |  | Peerless
Peerless | WBV-e-04-125-S | 175 | 152 | 475 | 14.87 | 685 |  | Peerless
Peerless | WBV-e-04-150-S | 210 | 180 | 563 | 14.87 | 685 |  | Peerless
Peerless | 63-03L | 88.5 | 74 | 233 | 9.3 | 465 |  | Peerless
Peerless | 63-03 | 118 | 98 | 308 | 9.3 | 465 |  | Peerless
Peerless | 63-04L | 147.5 | 123 | 383 | 10.8 | 576 |  | Peerless
Peerless | 63-04 | 177 | 147 | 458 | 10.8 | 576 |  | Peerless
Peerless | 63-05L | 206.5 | 171 | 533 | 12.4 | 700 |  | Peerless
Peerless | 63-05 | 236 | 196 | 613 | 12.4 | 700 |  | Peerless
Peerless | 63-06 | 287.5 | 238 | 746 | 13.9 | 812 |  | Peerless
Peerless | 63-x-03 | 100 | 82 | 258 | 7 | 480 |  | Peerless
Peerless | 63-x-04 | 150 | 124 | 388 | 9 | 595 |  | Peerless
Peerless | 63-x-05 | 200 | 165 | 517 | 11 | 725 |  | Peerless
Peerless | 63-x-06 | 250 | 206 | 646 | 13 | 840 |  | Peerless
Green Mountain | GMGS-75 | 75 | 62 | 195 | 1.8 | 297 |  | Green Mountain
Green Mountain | GMGS-112 | 112.5 | 91 | 283 | 2.7 | 368 |  | Green Mountain
Green Mountain | GMGS-150 | 150 | 122 | 383 | 3.7 | 440 |  | Green Mountain
Green Mountain | GMGS-187 | 187.5 | 153 | 479 | 4.7 | 512 |  | Green Mountain
Green Mountain | GMGS-225 | 225 | 183 | 570 | 5.7 | 584 |  | Green Mountain
Green Mountain | GMGS-262 | 262.5 | 214 | 670 | 6.7 | 659 |  | Green Mountain
Green Mountain | GMGS-299 | 299 | 245 | 766 | 7.7 | 736 |  | Green Mountain
Williamson | GSA-075 | 75000 | 62000 | 196 | 8.4 | 430 |  | Williamson
Williamson | GSA-100 | 100000 | 82000 | 258 | 8.4 | 430 |  | Williamson
Williamson | GSA-125 | 125000 | 103000 | 321 | 9.8 | 505 |  | Williamson
Williamson | GSA-150 | 150000 | 124000 | 388 | 9.8 | 505 |  | Williamson
Williamson | GSA-175 | 175000 | 145000 | 454 | 11.2 | 585 |  | Williamson
Williamson | GSA-200 | 200000 | 166000 | 521 | 11.2 | 585 |  | Williamson
Williamson | GSA-238 | 238000 | 198000 | 621 | 12.6 | 660 |  | Williamson
Williamson | GSA-282 | 282000 | 234000 | 733 | 14 | 735 |  | Williamson

## Calculations (hidden)
Schd 40 Pipe stats
| ID(in) | Area(ft2) | BTU/ft @ 210°F | linear ft3/ft | Lb/ft | Supply BTU Horizontal Runout | Return BTU Return Riser | Dry Return BTU |  | List generator | Trap Status | Louver Type | Free Area ratio | Opening Setup | in/btu
1/2 | 0.662 | 0.0023903 | 82 | 0.0013657 | 0.851 | 0 | 0 | 0 |  |  | Failed-Closed | Metal | 0.75 | Horizontal | 0.0005
3/4 | 0.824 | 0.0037032 | 100 | 0.0030671 | 1.131 | 6720 | 46080 | 98880 | 3/4 | 1 | Failed-Open | Wood | 0.25 | Vertical | 0.00025
1 | 1.049 | 0.0060018 | 123 | 0.0054572 | 1.679 | 13440 | 108480 | 208320 | 1 | 2 | Operational
1 1/4 | 1.38 | 0.010387 | 152 | 0.0085069 | 2.273 | 25920 | 238080 | 326400 | 1 1/4 | 3
1 1/2 | 1.61 | 0.014138 | 173 | 0.012269 | 2.718 | 40320 | 360000 | 710400 | 1 1/2 | 4
2 | 2.067 | 0.023303 | 212 | 0.021817 | 3.653 | 86880 | 720000 | 1180800 | 2 | 5
2 1/2 | 2.469 | 0.033248 | 252 | 0.034086 | 5.793 | 126720 |  | 2160000 | 2 1/2 | 6
3 | 3.068 | 0.051338 | 303 | 0.049074 | 7.576 | 192000 |  | 3100800 | 3 | 7
3 1/2 | 3.548 | 0.068659 | 342 | 0.068171 | 9.183 | 276480 |  | 4636800 | 3 1/2 | 8
4 | 4.026 | 0.088405 | 381 | 0.087269 | 10.79 | 408800 |  |  | 4 | 9
5 | 5.047 | 0.13893 | 464 | 0.13634 | 14.882 | 756480 |  |  | 5 | 10
6 | 6.065 | 0.20063 | 546 | 0.19635 | 18.974 |  |  |  | 6
6 | 6.065 | 0.20063 | 546 | 0.19635 | 18.974 |  |  |  | 6
5 | 5.047 | 0.13893 | 464 | 0.13634 | 14.882 | 756480 |  |  | 5
4 | 4.026 | 0.088405 | 381 | 0.087269 | 10.79 | 408800 |  |  | 4
3 1/2 | 3.548 | 0.068659 | 342 | 0.068171 | 9.183 | 276480 |  | 4636800 | 3 1/2
3 | 3.068 | 0.051338 | 303 | 0.049074 | 7.576 | 192000 |  | 3100800 | 3
2 1/2 | 2.469 | 0.033248 | 252 | 0.034086 | 5.793 | 126720 |  | 2160000 | 2 1/2
2 | 2.067 | 0.023303 | 212 | 0.021817 | 3.653 | 86880 | 720000 | 1180800 | 2
1 1/2 | 1.61 | 0.014138 | 173 | 0.012269 | 2.718 | 40320 | 360000 | 710400 | 1 1/2
1 1/4 | 1.38 | 0.010387 | 152 | 0.0085069 | 2.273 | 25920 | 238080 | 326400 | 1 1/4
1 | 1.049 | 0.0060018 | 123 | 0.0054572 | 1.679 | 13440 | 108480 | 208320 | 1
3/4 | 0.824 | 0.0037032 | 100 | 0.0030671 | 1.131 | 6720 | 46080 | 98880 | 3/4
1/2 | 0.662 | 0.0023903 | 82 | 0.0013657 | 0.851 | 0
| None | 1/2" | 1" | 1-1/2" | 2"
1/2 | 0 | 3.1 | 6.8 | 12.4 | 18
3/4 | 0 | 2.9 | 5.4 | 10.4 | 15.5
1 | 0 | 2.8 | 6.7 | 11.1 | 16.3
1 1/4 | 0 | 2.7 | 5.2 | 11.3 | 13.8
1 1/2 | 0 | 2.6 | 5.8 | 9.8 | 17
2 | 0 | 2.6 | 5.9 | 9.8 | 14.2
2 1/2 | 0 | 2.5 | 5.6 | 11.5 | 15.6
3 | 0 | 2.5 | 5.2 | 8.7 | 12.4
4 | 0 | 2.4 | 5.2 | 8.3 | 11.7
5 | 0 | 0 | 4.8 | 7.8 | 11
6 | 0 | 0 | 4.6 | 7.4 | 10.9

## SteamProperties (hidden)
Gauge Pressure | Temperature | Specific Volume Saturated Vapor | Enthalpy
(psig) | (oF) | (ft3/lb) | Saturated Liquid | Evaporated | Saturated Vapor
PSI | F | ft3/lb | (Btu/lb) | (Btu/lb) | (Btu/lb)
-2.456 | 203 | 31.8 | 171 | 976 | 1147 |  | 0.039683 | 1 | 0.92016
0 | 212 | 26.8 | 180 | 970 | 1150 |  | 0.042553 | 2 | 2.0884
1 | 215 | 25.2 | 183 | 968 | 1151
2 | 219 | 23.5 | 187 | 966 | 1153
3 | 222 | 22.3 | 190 | 964 | 1154
4 | 224 | 21.4 | 192 | 962 | 1154
5 | 227 | 20.1 | 195 | 960 | 1155
6 | 230 | 19.4 | 198 | 959 | 1157
Pipe Size | BTU/linear ft | [7 empty] | Branch Supply List | Supply Line List
| 100°F | 120°F | 150°F | 180°F | 210°F | 240°F | in3/ft | ID(in)
1/2 | 13 | 22 | 40 | 60 | 82 | 106 | 2.36 | 0.622 | AA | A
3/4 | 15 | 27 | 50 | 74 | 100 | 131 | 5.3 | 0.824 | BB | B
1 | 19 | 34 | 61 | 90 | 123 | 160 | 9.43 | 1.049 | CC | C
1 1/4 | 23 | 42 | 75 | 111 | 152 | 198 | 14.7 | 1.38 | DD | D
1 1/2 | 27 | 48 | 85 | 126 | 173 | 224 | 21.2 | 1.61 | EE | E
2 | 33 | 59 | 104 | 154 | 212 | 275 | 37.7 | 2.067 | FF | F
2 1/2 | 39 | 70 | 123 | 184 | 252 | 327 | 58.9 | 2.469 | GG | G
3 | 46 | 84 | 148 | 221 | 303 | 393 | 84.8 | 3.068 | HH | H
3 1/2 | 52 | 95 | 168 | 250 | 342 | 444 | 117.8 | 3.548 | II | I
4 | 59 | 106 | 187 | 278 | 381 | 496 | 150.8 | 4.026 | JJ
5 | 71 | 129 | 227 | 339 | 464 | 603 | 235.6 | 5.047 | KK
6 | 84 | 151 | 267 | 398 | 546 | 709 | 339.3 | 6.065 | LL
8 | 107 | 194 | 341 | 509 | 697 | 906
10 | 132 | 238 | 420 | 626 | 857 | 1114
12 | 154 | 279 | 491 | 732 | 1003 | 1305
14 | 181 | 326 | 575 | 856 | 1173 | 1527
16 | 203 | 366 | 644 | 960 | 1314 | 1711
18 | 214 | 385 | 678 | 1011 | 1385 | 1802
20 | 236 | 426 | 748 | 1115 | 1529 | 1990
Pressur Drop