## Cv Calcs
To Find Cv |  |  | To Find Flow |  | To Find PSI Drop
Known values |  |  | Known values |  | Known values
Delta P (PSI) | 1 |  | Delta P (PSI) | 15 | Cv | 1.15
Flow (GPM) | 1 |  | Cv | 0.23 | Flow | 5
Calculated Value |  |  | Calculated Value |  | Calculated Value
Cv >>>>>>>>>> | 1 |  | Flow (GPM) >>>>>>> | 0.89079 | Delta P (PSI) >>>>>>>> | 18.9036
[5 empty] | Feet of head >>>>>>>> | 43.6673
2 Cv in series |  |  |  |  | 3 Cv in series |  |  |  | 4 Cv in series
| Enter Cv Values | Squared | Inversed |  |  | Enter Cv Values | Squared | Inversed |  | Enter Cv Values | Squared | Inversed
Cv #1 = | 2.1 | 4.41 | 0.22676 |  | Cv #1 = | 3 | 9 | 0.11111 | Cv #1 = | 10 | 100 | 0.01
Cv #2 = | 3.5 | 12.25 | 0.081633 |  | Cv #2 = | 2.1 | 4.41 | 0.22676 | Cv #2 = | 10 | 100 | 0.01
[5 empty] | Cv #3 = | 2.1 | 4.41 | 0.22676 | Cv #3 = | 5 | 25 | 0.04
|  |  | 0.30839 |  |  |  |  | 0.56463 | Cv #4 = | 10 | 100 | 0.01
0.07
|  | Total Cv >> | 1.8007 |  |  |  | Total Cv >> | 1.3308 |  |  | Total Cv >> | 3.7796
663 Manifold Total Cv >>>>>>>>> |  | 2.3
668 Manifold Total Cv >>>>>>>>> |  | 1.2
IPEX manifold with flowmeter Cv >> |  | 1.04

## curves
To Find Cv |  |  | To Find Flow |  |  | To Find PSI Drop
Known values |  |  | Known values |  |  | Known values
Delta P (PSI) | 2.6 |  | Delta P (PSI) | 1 |  | Cv | 3.5
Flow (GPM) | 7 |  | Cv | 5 |  | Flow | 1
Calculated Value |  |  | Calculated Value |  |  | Calculated Value
Cv >>>>>>>>>> | 4.3412 |  | Flow (GPM) >>>>>>> | 5 |  | Delta P (PSI) >>>>>>>> | 0.081633
| Enter Cv Value below | Enter Cv Value below |  |  | Head loss
Flow | 1967 | 1967 |  | GPM | Ft/100 ft | PSID of pipe | Eq Ft of Pipe
0 | 0 | 0 |  | 0 | 0 | 0 | 0.01
250 | 0.016154 | 0.016154 |  | 1 | 0.44 | 0.1892 | 8.5379
500 | 0.064615 | 0.064615 |  | 2 | 1.44 | 0.6192 | 10.4352
750 | 0.14538 | 0.14538 |  | 3 | 2.91 | 1.2513 | 11.6186
1000 | 0.25846 | 0.25846 |  | 4 | 4.81 | 2.0683 | 12.4962
1250 | 0.40384 | 0.40384 |  | 5 | 7.11 | 3.0573 | 13.2091
1500 | 0.58153 | 0.58153 |  | 6 | 9.8 | 4.214 | 13.8
1750 | 0.79153 | 0.79153 |  | 7 | 12.86 | 5.5298 | 14.3139
2000 | 1.0338 | 1.0338 |  | 8 | 16.28 | 7.0004 | 14.7682
2250 | 1.3084 | 1.3084 |  | 9 | 20.06 | 8.6258 | 15.169
2500 | 1.6154 | 1.6154 |  | 10 | 24.19 | 10.4017 | 15.5298
2750 | 1.9546 | 1.9546 |  | 11 | 28.66 | 12.3238 | 15.8603
3000 | 2.3261 | 2.3261 |  | 12 | 33.47 | 14.3921 | 16.1625
3250 | 2.73 | 2.73 |  | 13 | 38.61 | 16.6023 | 16.4433
3500 | 3.1661 | 3.1661 |  | 14 | 44.07 | 18.9501 | 16.7077
3750 | 3.6346 | 3.6346 |  | 15 | 49.86 | 21.4398 | 16.9525
4000 | 4.1353 | 4.1353 |  | 16 | 55.97 | 24.0671 | 17.1825
4250 | 4.6684 | 4.6684 |  | 17 | 62.39 | 26.8277 | 17.4015
4500 | 5.2338 | 5.2338 |  | 18 | 69.13 | 29.7259 | 17.6068
4750 | 5.8315 | 5.8315
5000 | 6.4615 | 6.4615
5250 | 7.1238 | 7.1238
To Find Cv
Known values
[5 empty] | Delta P (PSI) | 2.91
[5 empty] | Flow (GPM) | 3
Calculated Value
[5 empty] | Cv >>>>>>>>>> | 1.7586

## velocity calc
Nominal Pipe Diameter (reference) >>>>> | 2 | 2.5 | 3 | 4 | 5 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 18 | 22
Inside pipe diameter (schedule 40) | 2 | 2.469 | 3.068 | 4.026 | 5.047 | 6.023 | 7.981 | 10.02 | 12 | 14 | 15.25 | 15.25 | 15.25 | 17.5 | 21.5
Area of pipe (sq in) | 3.1416 | 4.7878 | 7.3927 | 12.7303 | 20.0058 | 28.4915 | 50.027 | 78.8543 | 113.0973 | 153.938 | 182.6542 | 182.6542 | 182.6542 | 240.5282 | 363.0503
Flow rate (GPM) | 40 | 80 | 124 | 247 | 300 | 484 | 792 | 1330 | 1850 | 2500 | 3000 | 3000 | 3000 | 6800 | 6000
Calculated velocity (ft/sec) | 4.0846 | 5.3603 | 5.3809 | 6.2243 | 4.8106 | 5.4496 | 5.0787 | 5.4108 | 5.2475 | 5.2099 | 5.269 | 5.269 | 5.269 | 9.0694 | 5.3017
http://www.1728.com/flowrate.htm | <<< reference web page to check calculations